## BoQ1
Government eProcurement System Created By: VETRISELVI JAGADEESAN Created Date/Time: 21-Mar-2022 06:03 PM Tender Title: REPLACEMENT OF OLD PACKAGE AC AT SHA WITH VRF SYSTEM AT IMPHAL AIRPORT Tender ID: 2022_AAI_105794_1
Tender Inviting Authority: Asst. General Manager (Engg.-Elect.), AAI, Imphal Airport.
Name of Work: Replacement of Old Package Acs at SHA with VRF System at Imphal Airport, Imphal.
Contract No: 2022_AAI_105794_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Sagar Traders(GSTN-18AALPH4922R1Z2) |  | RS COOLING APPLIANCES(GSTN-18AALFR2502H3Z8) |  | CAC ENGINEERS PVT LTD(GSTN-33AAECC2301D2ZK) |  | COOL TECH ENGINEERS(GSTN-08AAFFC7397B1ZD)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply, Installation, Testing and Commissioning of Modular Type Variable Refrigerant Flow Outdoor Units with hermatically sealed inverter type Scroll Compressor(s) with BLDC motor suitable to operate on 415 V ± 10%, 50 Hz, 3 Phase AC Supply, heat exchanger/condenser coil, heating & cooling, microprocessor based controller, low noise condenser fan, auto check function for connection error, auto address setting and minimum capacity as mentioned below. All outdoor unit should have stepless modulation, Top discharge type condensing units with R410 A refrigerant including full charge of refrigerant gas and oil for commissioning the entire system, vibration isolators with fixing in the existing angle iron frame work, capable of delivering 100% capacity at 40 Deg C ambient and COP not less than 3.8 & 6.0 at 100% & 50% load condition respectively for cooling conforming to AHRI Standards and Conditions, etc., as required.
1.01 | 28.0 HP (Comprising of Minimum Two Compressors) | 7.00 | Jobs |  | 449639.00 | 3147473.00 | 650000.00 | 4550000.00 | 502500.00 | 3517500.00 | 541121.00 | 3787847.00 | 3147473.00 | Sagar Traders
2.00 | Supply, Installation, Testing and Commissioning of DX double skin Air Handling Unit of Floor Mounted Vertical type with 0.6 mm pre coated GI outer skin and 0.6 mm GI inner skin with 48 ± 2 mm thick PUF insulation of density of 40 ± 2 kg/m3 vertical Floor complete with DIDW centrifugal Forward curved fan,fan motort with V-belt & Motor (IE-3) suitable to operate on 415 V ± 10%, 50 Hz, 3 Phase AC Supply, 6 row deep DX cooling coil, MERV-10 filter section, with fire retardant canvass connection between AHU and supply Air duct, thermal break profile, vibration isolator pad, AHU Kit for connecting the Outdoor unit as per the VRF OEM Standard, Expansion Kit, communication Kit suitable for individually remote controllable and compatible for centralised contol, providing and fixing of suitable Starter Panel with indicating lights and auto selector switch for the AHU along with Neccessary power and control cabling upto 15 M (Power Cable capacity of 2 times of power rating of AHU), earthing, termination of Power and Control Cable etc., as required.
2.10 | Minimum 8800 CFM | 7.00 | Jobs |  | 339211.00 | 2374477.00 | 335000.00 | 2345000.00 | 257250.00 | 1800750.00 | 521521.00 | 3650647.00 | 1800750.00 | CAC ENGINEERS PVT LTD
3.00 | Supply, Installation, Testing and Commissioning of following nominal sizes of soft/hard drawn copper refrigerant piping for VRF System with necessary jointng/brazing including, insulated with nitrile rubber, tubular sleeve sections of specified thickness as below for Suction and Liquid lines i/c providing and fixing of all accessories, vaccumization and Nitrogen testing etc., complete i/c fixing arrangements of all sizes of CU tubes on the existing GI tray.
3.10 | 1/2" dia (OD) (soft drawn) with tube thickness 1.2 mm with 19mm thick insulation or as per OEM standard. | 74.00 | Meter |  | 479.00 | 35446.00 | 1050.00 | 77700.00 | 320.00 | 23680.00 | 325.00 | 24050.00 | 23680.00 | CAC ENGINEERS PVT LTD
3.20 | 3/4" dia (OD) (Hard drawn) with tube thickness 1.2 mm with 19mm thick insulation or as per OEM standard. | 103.00 | Meter | 10.00 | 596.00 | 61388.00 | 1100.00 | 113300.00 | 592.00 | 60976.00 | 580.00 | 59740.00 | 59740.00 | COOL TECH ENGINEERS
3.30 | 1 1/8" dia (OD) (Hard drawn) with tube thickness 1.2 mm with 19mm thick insulation or as per OEM standard. | 74.00 | Meter | 10.00 | 849.00 | 62826.00 | 1100.00 | 81400.00 | 920.00 | 68080.00 | 890.00 | 65860.00 | 62826.00 | Sagar Traders
3.40 | 1 3/8" dia (OD) (Hard drawn) with tube thickness 1.2 mm with 19mm thick insulation or as per OEM standard. | 103.00 | Meter | 10.00 | 869.00 | 89507.00 | 1200.00 | 123600.00 | 1292.00 | 133076.00 | 1700.00 | 175100.00 | 89507.00 | Sagar Traders
4.00 | Supply, Installation, Testing and Commissioning of following nominal sizes of soft/hard drawn copper refrigerant piping for VRF System with necessary jointng/brazing including, insulated with nitrile rubber, tubular sleeve sections of specified thickness as below for Suction and Liquid lines i/c providing and fixing of all accessories, vaccumization and Nitrogen testing etc.,including fixing Arragements for the following copper tubes in the Ceiling/Wall including providing and fixing necessary suspenders/supports etc., complete as required.
4.10 | 1/2" dia (OD) (soft drawn) with tube thickness 1.2 mm with 19mm thick insulation or as per OEM standard. | 44.00 | Meter |  | 349.00 | 15356.00 | 1050.00 | 46200.00 | 320.00 | 14080.00 | 375.00 | 16500.00 | 14080.00 | CAC ENGINEERS PVT LTD
4.20 | 3/4" dia (OD) (Hard drawn) with tube thickness 1.2 mm with 19mm thick insulation or as per OEM standard. | 44.00 | Meter |  | 369.00 | 16236.00 | 1100.00 | 48400.00 | 592.00 | 26048.00 | 630.00 | 27720.00 | 16236.00 | Sagar Traders
4.30 | 1 1/8" dia (OD) (Hard drawn) with tube thickness 1.2 mm with 19mm thick insulation or as per OEM standard. | 44.00 | Meter |  | 659.00 | 28996.00 | 1100.00 | 48400.00 | 920.00 | 40480.00 | 950.00 | 41800.00 | 28996.00 | Sagar Traders
4.40 | 1 3/8" dia (OD) (Hard drawn) with tube thickness 1.2 mm with 19mm thick insulation or as per OEM standard. | 44.00 | Meter |  | 769.00 | 33836.00 | 1200.00 | 52800.00 | 1292.00 | 56848.00 | 1800.00 | 79200.00 | 33836.00 | Sagar Traders
5.00 | Supply, Installation, balancing and Commissioning of fabricated at site GSS sheet metal rectangular/round ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes,hangers, supports etc., as per approved drawings and specifications of following sheet thickness including alignment, matching and fixing with existing ducting arragements etc., complete as required.
5.10 | 18 SWG | 10.00 | Sqm |  | 959.00 | 9590.00 | 1450.00 | 14500.00 | 625.00 | 6250.00 | 1600.00 | 16000.00 | 6250.00 | CAC ENGINEERS PVT LTD
5.20 | 22 SWG | 10.00 | Sqm |  | 759.00 | 7590.00 | 1400.00 | 14000.00 | 600.00 | 6000.00 | 1200.00 | 12000.00 | 6000.00 | CAC ENGINEERS PVT LTD
5.30 | 24 SWG | 10.00 | Sqm |  | 696.00 | 6960.00 | 1200.00 | 12000.00 | 550.00 | 5500.00 | 1050.00 | 10500.00 | 5500.00 | CAC ENGINEERS PVT LTD
6.00 | Supply and fixing of acoustic lining of supply air duct and plenum with 25 mm thick resin bonded glass wool having density of 32 kg/m³, with 25 mm X 25 mm GI section of 1.25 mm thick, at 600 mm centre to centre covered with Reinforced Plastic tissue paper and 0.5 mm thick perforated aluminum sheet fixed to inside surface of ducts with cadmium plated nuts, bolts, stick pins, CPRX compound etc. complete as required. | 10.00 | Sqm |  | 1049.00 | 10490.00 | 800.00 | 8000.00 | 250.00 | 2500.00 | 1200.00 | 12000.00 | 2500.00 | CAC ENGINEERS PVT LTD
7.00 | Supplying and fixing of 19mm thickness duly laminated aluminum foil of mat finish closed cell Nitrile rubber (Class "O") insulation on existing duct after applying suitable adhesive for Nitrile rubber. The joints shall be sealed with 50 mm wide and 3 mm thick self adhesive nitrile rubber tape insulation complete as per specifications and as required. | 20.00 | Sqm |  | 559.00 | 11180.00 | 650.00 | 13000.00 | 275.00 | 5500.00 | 750.00 | 15000.00 | 5500.00 | CAC ENGINEERS PVT LTD
8.00 | Supplying, Fixing, Testing and Commissioning of Fire Dampers made of 16 SWG GSS in supply air duct/main branch and return air path as and where required of required sizes i/c control wiring,the damper shall be motorized and spring return so as to close the damper in the event of power failure automatically and open the same in case of power being restored. The spring return action shall be inbuilt mechanism and not externally mounted. The damper shall also be closed in the event of fire signal complete as required and as per specifications.
8.10 | Fire Dampers | 7.00 | Sqm |  | 11449.00 | 80143.00 | 22000.00 | 154000.00 | 4500.00 | 31500.00 | 9000.00 | 63000.00 | 31500.00 | CAC ENGINEERS PVT LTD
8.20 | Actuator | 7.00 | Nos |  | 19099.00 | 133693.00 | 5000.00 | 35000.00 | 5000.00 | 35000.00 | 11000.00 | 77000.00 | 35000.00 | RS COOLING APPLIANCES, CAC ENGINEERS PVT LTD
9.00 | Supply and Fixing of 40 mm dia rigid UPVC pipe conforming to IS 4985-2000 with 6 mm nitrile rubber Insulation complete with fittings, supports etc., for drain piping as required . | 100.00 | Meter |  | 89.00 | 8900.00 | 300.00 | 30000.00 | 110.00 | 11000.00 | 225.00 | 22500.00 | 8900.00 | Sagar Traders
10.00 | Dismantling of existing 22 TR indoor and out door AC units i/c demolishing of the foundation and its accessories, dismantling of associated items like starter panel/copper pipes/power and control cables / trays / dampers / supports etc., i/c shifting and hand over to AAI Store as required. | 7.00 | Jobs | 10.00 | 2890.00 | 20230.00 | 30000.00 | 210000.00 | 500.00 | 3500.00 | 10000.00 | 70000.00 | 3500.00 | CAC ENGINEERS PVT LTD
11.00 | Supplying and installing 300 mm X 62.5 mm X 2 mm perforated hot dip Galvanised cable trays with perforation not more than 17.5%, in convenient sections, joined with connectors, fixed on wall/floor/surface with necessary fixing accessories for running refrigerant piping and cable alongwith control wiring etc., complete as required. | 104.00 | Meter | 10.00 | 649.00 | 67496.00 | 800.00 | 83200.00 | 550.00 | 57200.00 | 550.00 | 57200.00 | 57200.00 | CAC ENGINEERS PVT LTD, COOL TECH ENGINEERS
12.00 | Supply and fixing of 25 mm dia UPVC pipe along with accessories in surface / recess for laying of control cable as required. | 132.00 | Meter | 10.00 | 89.00 | 11748.00 | 150.00 | 19800.00 | 100.00 | 13200.00 | 70.00 | 9240.00 | 9240.00 | COOL TECH ENGINEERS
13.00 | Supply and drawing of 2 core x 1.5 sqmm armoured copper conductor FRLS Cable as per IS7098(Part 1)1988 in the existing Conduits as required. | 146.00 | Meter |  | 489.00 | 71394.00 | 300.00 | 43800.00 | 100.00 | 14600.00 | 100.00 | 14600.00 | 14600.00 | CAC ENGINEERS PVT LTD, COOL TECH ENGINEERS
14.00 | Supply and laying of of 4 C x 16 sqmm XLPE insulated and PVC sheathed armoured copper conductor Cable as per IS7098 (Part 1)1988 cable of 1.1 KV grade in the existing cable tray etc., complete as required. | 210.00 | Meter |  | 79.00 | 16590.00 | 390.00 | 81900.00 | 450.00 | 94500.00 | 1100.00 | 231000.00 | 16590.00 | Sagar Traders
15.00 | Supplying and making end termination with brass compression gland and Copper lugs for 4 C x 16 sqmm XLPE insulated and PVC sheathed copper conductor armoured cable of 1.1 KV grade etc., complete as required. | 28.00 | Each |  | 2190.00 | 61320.00 | 900.00 | 25200.00 | 500.00 | 14000.00 | 550.00 | 15400.00 | 14000.00 | CAC ENGINEERS PVT LTD
16.00 | Providing and fixing 6 SWG dia GI wire on surface or in recess for loop earthing for conductor earth electrode, including connection/ termination with GI thimble etc. as required. | 731.00 | Meter |  | 249.00 | 182019.00 | 90.00 | 65790.00 | 25.00 | 18275.00 | 91.00 | 66521.00 | 18275.00 | CAC ENGINEERS PVT LTD
17.00 | Earthing with GI earth pipe 4.5 meter long,40 mm dia including accessories and providing masonry enclosure with cover plate having locking arrangement and water pipe etc.(with charcoal/coke and salt) as required. | 2.00 | Jobs |  | 1490.00 | 2980.00 | 55000.00 | 110000.00 | 5428.50 | 10857.00 | 5498.00 | 10996.00 | 2980.00 | Sagar Traders
18.00 | Providing, fabricating and fixing of 50 mm X 50 mm x 5 mm M.S. angle support for positioning O/D units i/c grouting , necessary foundation, welding, fixing clamps, bolts, nuts and washers and painting with primer and finish paint etc. Complete as required. | 350.00 | Kg |  | 796.00 | 278600.00 | 180.00 | 63000.00 | 60.00 | 21000.00 | 120.00 | 42000.00 | 21000.00 | CAC ENGINEERS PVT LTD
19.00 | Providing and fixing of 14 SWG GSS sheet cover for existing perforated refrigeant pipe / cable tray i/c welding, fixing clamps, bolts, nuts and washers etc., Complete as per site requirement. | 18.00 | Sqm |  | 649.00 | 11682.00 | 1250.00 | 22500.00 | 450.00 | 8100.00 | 1800.00 | 32400.00 | 8100.00 | CAC ENGINEERS PVT LTD
| Total in Figures |  |  |  |  | 6858146.00 |  | 8492490.00 |  | 6100000.00 |  | 8705821.00
Lowest Amount Quoted BY: CAC ENGINEERS PVT LTD(6100000.00)

## BOQ Summary
BOQ Summary Details Tender Title: REPLACEMENT OF OLD PACKAGE AC AT SHA WITH VRF SYSTEM AT IMPHAL AIRPORT Tender ID: 2022_AAI_105794_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | CAC ENGINEERS PVT LTD | 6100000.00 | L1
| 2 | Sagar Traders | 6858146.00 | L2
| 3 | RS COOLING APPLIANCES | 8492490.00 | L3
| 4 | COOL TECH ENGINEERS | 8705821.00 | L4