## BoQ1
Government eProcurement System Created By: PRADIP KUMAR B Created Date/Time: 28-Mar-2022 03:25 PM Tender Title: Provision of illuminated Taxiway guidance signages at Isolation Bay at Kushinagar Airport Tender ID: 2022_AAI_106929_1
Tender Inviting Authority: AGM(Engg-E), AAI, Kushinagar Airport
Name of Work: Provision of illuminated Taxiway guidance signages at Isolation Bay at Kushinagar Airport.
Contract No: 2022_AAI_106929
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | REWINDER TECHNO ELECTRICALS(GSTN-18AAFFR7457K1ZL) |  | POSHDECOR(GSTN-27AAAPL7043G1ZV) |  | DElite System Engineering (India) Pvt. Ltd.(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Fabrication, Supply, Installation,Testing & commissioning of internally illuminated LED based Mandatory Taxiway guidance signage of various size made out of 4mm thick glare free poly carbonate sheet at front and body made out of 2 mm thick powder coated aluminum profile having minimum width of 150mm and supported at back by 50mm dia (Nominal size),3mm thick, die cast aluminum pipe at a separation and frangible coupling as required.Light Source shall be highly luminious, long life typical 50,000 Hrs. type, 0.5 watts LED's assembled on aluminum PCB of size 700mm X 20mmX2mm having 11 LED's per PCB for boards having height 800mm or more & 500mmX20mmX2mm PCB having 8 LED's per PCB for board having height 600mm respectively.These aluminium PCB should be places not more than 160mm apart across the length of the board in order to ensure uniform distribution of light across the board.Efficiency of LED shall have delivered minimum output 95 lumens per watt and colour temperature should be more then 5000 Kelvin with proper heat dissipation. The signage boards with length varying from 800 mm to 3000mm shall be suitable for operation on series circuit at variable current from 2.8 amp - 6.6 amp (brightness of the signage should be constant with current variation) including supply and installation of suitable single capacity/ wattage electronic converters and isolating transformers for entire length of sign boards. All the signage shall have letters and symbols made by computerized cutting of vinyl and pasting on the polycarbonate sheet from inside/outside of the sign face of required color as per ICAO Annex 14 Vol1(legends as approved by EIC).Scope of work shall included for Installation of mounting each legs with grouting accessories i.e anchor bolts,washer, frame,base plate etc. complete as required but excluded civil concrete works. | 7.00 | Sq.mtr |  | 50000.00 | 350000.00 | 54000.00 | 378000.00 | 65000.00 | 455000.00 | 350000.00 | REWINDER TECHNO ELECTRICALS
2.00 | Supply of Electronic Converters for LED based airfield signages boards having height 800mm and length varying from 800mm to 3000mm & suitable for operation on series circuit, input current varying from 2.8A to 6.6A and provide constant brightness for all current variation etc as required as directed by EIC. | 4.00 | Each |  | 11000.00 | 44000.00 | 8100.00 | 32400.00 | 4500.00 | 18000.00 | 18000.00 | DElite System Engineering (India) Pvt. Ltd.
3.00 | Supply of following Capacities,Series type, 5KV Grade,50Hz Isolating Transformer, made of super enameled copper wire,Two EPR Primary Cables of 5KV Grade with moulded plug and one EPR secondary twin-core cable of 1.1KV grade with molded two - pin receptacle, epoxy encapsulated and moulded with compounded moisture resistant neoprene rubber. (i) 200 watts, 6.6/6.6 amp | 4.00 | Each |  | 5500.00 | 22000.00 | 6300.00 | 25200.00 | 6000.00 | 24000.00 | 22000.00 | REWINDER TECHNO ELECTRICALS
4.00 | Supply of following size of stranded annealed copper conductor, 5 KV grade, PVC insulated , PVC sheathed ,unscreened,unarmoured,antitermite and antirodent treated Air Field cable generally confirming to ISI 554/ PT-II as ammended uptodate and as per specification. (i) 1x6 Sqmm | 250.00 | Mtr |  | 150.00 | 37500.00 | 150.00 | 37500.00 | 138.00 | 34500.00 | 34500.00 | DElite System Engineering (India) Pvt. Ltd.
5.00 | Supply of 50 mm outer dia. HDPE pipe as per IS:4984:1995,Material Grade:PE 80, PN 10 and as per specified in particular specification. | 250.00 | Mtr |  | 100.00 | 25000.00 | 120.00 | 30000.00 | 250.00 | 62500.00 | 25000.00 | REWINDER TECHNO ELECTRICALS
6.00 | Supply of 2core X 4 sq.mm AFL secondary lead made out of annealed tinned copper conductor, EPR insulalted PCP sheathed,unarmoured,anti termite & anti rodent treated 600V/1100V grade cable for connection between isolating transformer and airfield light fixtures as specified in particular specification etc complete as required. | 30.00 | Mtr |  | 200.00 | 6000.00 | 1500.00 | 45000.00 | 275.00 | 8250.00 | 6000.00 | REWINDER TECHNO ELECTRICALS
7.00 | Supply of following size , 5 KV grade plug and receptacle of type 1 class B connector and suitable field attachment with 5 KV grade PVC insulated PVC sheathed single core following size copper conductor cable confirming to the specified specification etc complete as required. (i) 6 sqmm | 10.00 | Each |  | 700.00 | 7000.00 | 660.00 | 6600.00 | 400.00 | 4000.00 | 4000.00 | DElite System Engineering (India) Pvt. Ltd.
8.00 | Supply of CI dummy plate of 8 mm thickness suitable for installation on the existing transformer housing boxes of 330 mm dia with 6 Nos hole suitable for M10 bolts and one no. hole at centre suitable to receive secondary cable etc as required. | 4.00 | Each |  | 1300.00 | 5200.00 | 600.00 | 2400.00 | 500.00 | 2000.00 | 2000.00 | DElite System Engineering (India) Pvt. Ltd.
9.00 | Supply of C.I. Transformer housing box water tight round type metal container of out side dia of 330 mm, height 450 mm made of 10 mm thick cast iron moulding all round except on top surface which is 15 mm thick suitable to receive a light fitting base plate at the top and underground housing associated with transformer power cable and having a clear hole/s center at one side surface center 75 mm above bottom surface & check nut having two earth bolts & four nuts with washer of M 10x30mm welded inside near the hole (4" away from the hole center) and having following nos. hole suitable to receive 50mm dia GI/HDPE pipe and an other one a drain hole at the bottom suitably tapped to received 15 mm dia 'B" class G.I. pipe & having clear opening of 220 mm at top surface and 6 nos. M 10 tapped hole at the centere of 260 mm to receive light fitting base plate and bolts and as required. | 4.00 | Each |  | 5500.00 | 22000.00 | 5700.00 | 22800.00 | 6000.00 | 24000.00 | 22000.00 | REWINDER TECHNO ELECTRICALS
10.00 | Installation of transformer housing boxes with a base concrete of 1:3:6 of size 630x630x100mm thick all round concrete of 1:2:4, 150mm thick top sloped with 1:2:4 cement including providing and fixing 300mm long 15mm dia "B" class GI pipe with check nut for drainage of water including excavation of soil and refilling, adjustment of CI boxes etc. complete as required. | 4.00 | Job |  | 2000.00 | 8000.00 | 3000.00 | 12000.00 | 2500.00 | 10000.00 | 8000.00 | REWINDER TECHNO ELECTRICALS
11.00 | Laying of 50 mm outer dia HDPE pipe including coupling,splicing of pipe direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc. , complete as required. | 250.00 | Mtr |  | 200.00 | 50000.00 | 360.00 | 90000.00 | 500.00 | 125000.00 | 50000.00 | REWINDER TECHNO ELECTRICALS
12.00 | Laying of size 2x4 Sqmm secondary lead and making interconnection between isolating transformer and Sign board etc in existing pipe/masonary open duct wherever reqd etc complete as reqd. | 30.00 | Mtr |  | 100.00 | 3000.00 | 45.00 | 1350.00 | 150.00 | 4500.00 | 1350.00 | POSHDECOR
13.00 | Making field connections by crimping 6/16 sq.mm. plug & receptable with existing 6/16 sq.mm. single core PVC copper conductor cable including filling the gap with water sealent material applying HT insulation tape over which again applying PVC insulation tape complete etc as required. | 10.00 | Each |  | 100.00 | 1000.00 | 120.00 | 1200.00 | 100.00 | 1000.00 | 1000.00 | DElite System Engineering (India) Pvt. Ltd., REWINDER TECHNO ELECTRICALS
14.00 | Supply of Plug and receptacles suitable for secondary lead of 2 x 4 sqmm EPR insulalted PCP sheathed copper conductor of secondary airfield lighting cables. | 5.00 | Each |  | 700.00 | 3500.00 | 660.00 | 3300.00 | 550.00 | 2750.00 | 2750.00 | DElite System Engineering (India) Pvt. Ltd.
15.00 | Making field connections by Plug or receptacles for existing secondary 2 x 4 sqmm cu cable from isolating transformer to Sign board including applying PVC insulation tape etc complete as required . | 5.00 | Each |  | 100.00 | 500.00 | 45.00 | 225.00 | 1500.00 | 7500.00 | 225.00 | POSHDECOR
16.00 | Laying of one number PVC insulated and PVC sheathed power cable of grade exceeding 1.1 KV but not exceeding 5KV of size not exceeding 16 sqmm. in the existing RCC / Hume / HDPE/Stoneware / GI pipe complete as required. | 250.00 | Mtr |  | 100.00 | 25000.00 | 45.00 | 11250.00 | 30.00 | 7500.00 | 7500.00 | DElite System Engineering (India) Pvt. Ltd.
17.00 | Excavation for cable trench/foundation of signboard in soft soil depth upto 1.5 mtr including refilling, dressing of sides and ramming of bottoms including getting out and disposal of surplus excavated soil as directed by EIC. | 6.00 | Cum |  | 200.00 | 1200.00 | 450.00 | 2700.00 | 1500.00 | 9000.00 | 1200.00 | REWINDER TECHNO ELECTRICALS
18.00 | Providing and laying in position specified grade of reinforced cement concrete, excluding the cost of centering, shuttering, finishing and reinforcement - All work up to plinth level :1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size). | 5.00 | Cum |  | 6000.00 | 30000.00 | 9000.00 | 45000.00 | 20000.00 | 100000.00 | 30000.00 | REWINDER TECHNO ELECTRICALS
19.00 | Providing and laying in position cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 20 mm nominal size) in the foundation etc including form work etc as required. | 3.00 | Cum |  | 5500.00 | 16500.00 | 7200.00 | 21600.00 | 15000.00 | 45000.00 | 16500.00 | REWINDER TECHNO ELECTRICALS
20.00 | Earthing with G.I pipe 4.5mm long x 40 mm dia including accessoires, and providing masonary enclosure with cover plate having locking arrangement and watering pipe etc with charcoal/coke and salt complete as required . | 4.00 | Set |  | 9000.00 | 36000.00 | 7200.00 | 28800.00 | 7000.00 | 28000.00 | 28000.00 | DElite System Engineering (India) Pvt. Ltd.
21.00 | Providing and fixing 6 SWG dia G.I. wire along with UG cable in existing HDPE/GI Pipe etc complete as required. | 250.00 | Mtr |  | 25.00 | 6250.00 | 36.00 | 9000.00 | 30.00 | 7500.00 | 6250.00 | REWINDER TECHNO ELECTRICALS
| Total in Figures |  |  |  |  | 699650.00 |  | 806325.00 |  | 980000.00
Lowest Amount Quoted BY: REWINDER TECHNO ELECTRICALS(699650.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of illuminated Taxiway guidance signages at Isolation Bay at Kushinagar Airport Tender ID: 2022_AAI_106929_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | REWINDER TECHNO ELECTRICALS | 699650.00 | L1
| 2 | POSHDECOR | 806325.00 | L2
| 3 | DElite System Engineering (India) Pvt. Ltd. | 980000.00 | L3