## BoQ1
Government eProcurement System Created By: Keishing Honpam Created Date/Time: 25-Apr-2022 04:08 PM Tender Title: Distribution of Power Supply from substation to AAI Residential Colony. Tender ID: 2022_AAI_107168_1
Tender Inviting Authority:
Name of Work: Distribution of Power Supply from substation to AAI Residential colony.
Contract No: 2022_AAI_107168_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | SHAKTI TECHNO FAB PRODUCTS(GSTN-09AAGPB2824D1Z8) |  | BOSE ENGINEERING AND MARKETING COMPANY(GSTN-19AHMPB0264G1ZJ) |  | M/s J H Associates(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply of following size of 1.1 KV grade, Armoured XLPE insulated PVC sheathed Aluminium conductor cable confirming to IS: 7098 part -I amended upto date.
2.00 | 3.5C x 50 sqmm (For B Block ) | 70.00 | Meter | 0.00 | 450.00 | 31500.00 | 360.00 | 25200.00 | 430.00 | 30100.00 | 25200.00 | BOSE ENGINEERING AND MARKETING COMPANY
3.00 | 3.5C x 95 sqmm (For B Block ) | 130.00 | Meter | 0.00 | 750.00 | 97500.00 | 580.00 | 75400.00 | 720.00 | 93600.00 | 75400.00 | BOSE ENGINEERING AND MARKETING COMPANY
4.00 | 3.5C x 185 sqmm (For old Residential colony) | 800.00 | Meter | 0.00 | 1350.00 | 1080000.00 | 1060.00 | 848000.00 | 1250.00 | 1000000.00 | 848000.00 | BOSE ENGINEERING AND MARKETING COMPANY
5.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required
6.00 | Above 35 sq. mm and upto 95 sq. mm | 200.00 | Meter | 0.00 | 300.00 | 60000.00 | 270.00 | 54000.00 | 400.00 | 80000.00 | 54000.00 | BOSE ENGINEERING AND MARKETING COMPANY
7.00 | Above 95 sq. mm and upto 185 sq. mm | 800.00 | Meter | 0.00 | 350.00 | 280000.00 | 270.00 | 216000.00 | 400.00 | 320000.00 | 216000.00 | BOSE ENGINEERING AND MARKETING COMPANY
8.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL pipe as required
9.00 | Above 35 sq. mm and upto 95 sq. mm | 5.00 | Meter | 0.00 | 100.00 | 500.00 | 30.00 | 150.00 | 30.00 | 150.00 | 150.00 | M/s J H Associates, BOSE ENGINEERING AND MARKETING COMPANY
10.00 | Above 95 sq. mm and upto 185 sq. mm | 31.00 | Meter | 0.00 | 120.00 | 3720.00 | 30.00 | 930.00 | 50.00 | 1550.00 | 930.00 | BOSE ENGINEERING AND MARKETING COMPANY
11.00 | Excavation of the cable trenches in hard rock not exceeding 1.5 metres in width, and lift upto 1.5 metres, including getting out the excavated soil and disposal of excavated soil as directed within a lead of 50 metres. | 8.00 | Cum | 0.00 | 2000.00 | 16000.00 | 800.00 | 6400.00 | 1000.00 | 8000.00 | 6400.00 | BOSE ENGINEERING AND MARKETING COMPANY
12.00 | Supplying and making end termination with heavy duty type brass single compression gland and aluminium lugs for following size of XLPE insulated aluminium conductor cable of 1.1 kV grade as required.
13.00 | 3.5 x 50 sqmm | 8.00 | Set | 0.00 | 450.00 | 3600.00 | 1400.00 | 11200.00 | 700.00 | 5600.00 | 3600.00 | SHAKTI TECHNO FAB PRODUCTS
14.00 | 3.5 x 95 sqmm | 4.00 | Set | 0.00 | 550.00 | 2200.00 | 1600.00 | 6400.00 | 1500.00 | 6000.00 | 2200.00 | SHAKTI TECHNO FAB PRODUCTS
15.00 | 3.5 x 185 sqmm | 10.00 | Set | 0.00 | 800.00 | 8000.00 | 2600.00 | 26000.00 | 2500.00 | 25000.00 | 8000.00 | SHAKTI TECHNO FAB PRODUCTS
16.00 | Design, Fabrication, Supply, Installation, Testing & Commissioning of outdoor type, totally enclosed, dust and vermin proof cubicle type LT Panel, made out of 2 mm thick CRCA sheet with 100 x 50 mm channel base frame in the bottom, totally enclosed, IP 55 or higher, free standing dust and vermin proof, compartmentalized with front lockable double doors, suitable for operation on 3 phase, 415 V, 50Hz AC system with TPN bus bars and internal control wiring of minimum 2.5 sqmm copper FRLS PVC insulated wires, interconnection, duly powder coated of approved shade as per specifications having following switchgears and accessories, and as approved by EIC, complete as required. INCOMMER: a) MCCB, 4P, 250A-320 A , 36 KA Breaking Capacity , with Ics= Icu*100% & Adjustable over load setting (0.8-1.0 In) with spreader terminals and rotary handle with castell type lock - 2 Nos. BUSBARS: b) 500 A TPN bus bars of high conductivity electrolytic quality Aluminium alloy- 1 Set each OUTGOING: c) MCCB, 4P, 250 A , 36 KA Breaking Capacity , with Ics= Icu*100 % & Adjustable over load setting (0.8- 1.0 In) with spreader terminals and rotary handle- 2 Nos. d) MCCB, 4P, 125 A , 25 KA Breaking Capacity , with Ics= Icu*100 % & Adjustable over load setting (0.8- 1.0 In) with spreader terminals and rotary handle- 1 No. e). 3 Phase Multifunction Digital Meters ( Volt, Amp, Energy, Freq, KVA, KW, PF) with inbuilt selector switch along with 3 nos. CT's - 100/5 Amp, RYB indicators, Breaker ON/OFF indicator-1 set each for Incomers. f) 3 Phase Multifunction Digital Meters ( Volt, Amp, Energy, Freq, KVA, KW, PF) , Breaker ON/OFF indicator-1 set each for Outgoings. Location:-Old Residential colony (Jagaran pump area,Ess panel ) | 1.00 | Each | 0.00 | 210000.00 | 210000.00 | 180000.00 | 180000.00 | 300000.00 | 300000.00 | 180000.00 | BOSE ENGINEERING AND MARKETING COMPANY
17.00 | Design, Fabrication, Supply, Installation, Testing & Commissioning of outdoor type, totally enclosed, dust and vermin proof cubicle type LT Panel, made out of 2 mm thick CRCA sheet with 100 x 50 mm channel base frame in the bottom, totally enclosed, IP 55 or higher, free standing dust and vermin proof, compartmentalized with front lockable double doors, suitable for operation on 3 phase, 415 V, 50Hz AC system with TPN bus bars and internal control wiring of minimum 2.5 sqmm copper FRLS PVC insulated wires, interconnection, duly powder coated of approved shade as per specifications having following switchgears and accessories, and as approved by EIC, complete as required. INCOMMER: a) MCCB, 4P, 250 A , 36 KA Breaking Capacity , with Ics= Icu*100% & Adjustable over load setting (0.8-1.0 In) with spreader terminals and rotary handle with castell type lock - 2 Nos. BUSBARS: b) 400 A TPN bus bars of high conductivity electrolytic quality Aluminium alloy- 1 Set each OUTGOING: c) MCCB, 4P, 160 A , 25 KA Breaking Capacity , with Ics= Icu*100 % & Adjustable over load setting (0.8- 1.0 In) with spreader terminals and rotary handle- 2 Nos. d) MCCB, 4P, 100 A , 25 KA Breaking Capacity , with Ics= Icu*100 % & Adjustable over load setting (0.8- 1.0 In) with spreader terminals and rotary handle- 4 Nos. e). 3 Phase Multifunction Digital Meters ( Volt, Amp, Energy, Freq, KVA, KW, PF) with inbuilt selector switch along with 3 nos. CT's - 100/5 Amp, RYB indicators, Breaker ON/OFF indicator-1 set each for Incomers. f) 3 Phase Multifunction Digital Meters ( Volt, Amp, Energy, Freq, KVA, KW, PF), Breaker ON/OFF indicator-1 set each for Outgoings. Location:-Old Residential colony (Jagaran pump area)-01 no.(Ess) & B Block area -01 no.(Ess) | 2.00 | Each | 0.00 | 225000.00 | 450000.00 | 200000.00 | 400000.00 | 280000.00 | 560000.00 | 400000.00 | BOSE ENGINEERING AND MARKETING COMPANY
18.00 | SITC of wall mounted, indoor type , Double door , 4 way, 4 pole 250A, LOAD BANK, MCCB Based Distribution Panel, complete with Cable Alley, pre-wired meter module with VAF meter, inbuilt selector switch, CT Control fuse, MCCB-Terminals, LED Phase indication lamp for Incomer, tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. a. 250A 4P, 35/36kA, Ics=100%Icu MCCB-1 nos (incomer) b. 100A 4P, 35/36kA, Ics=100%Icu MCCB-2 nos (Outgoing ) c. 63A 4P, 35/36kA, Ics=100%Icu MCCB-1 nos (Outgoing ) (For B Block-Non-Ess panel ) | 1.00 | Each | 0.00 | 100000.00 | 100000.00 | 107000.00 | 107000.00 | 100000.00 | 100000.00 | 100000.00 | M/s J H Associates, SHAKTI TECHNO FAB PRODUCTS
19.00 | SITC of wall mounted, indoor type , Double door , 4 way, 4 pole 400A, LOAD BANK, MCCB Based Distribution Panel, complete with Cable Alley, pre-wired meter module with VAF meter, inbuilt selector switch, CT Control fuse, MCCB-Terminals, LED Phase indication lamp for Incomer, tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. a. 400A 4P, 35/36kA, Ics=100%Icu MCCB-1 nos (incomer) b. 100A 4P, 35/36kA, Ics=100%Icu MCCB-2 nos (Outgoing ) c. 63A 4P, 35/36kA, Ics=100%Icu MCCB-1 nos (Outgoing ) (For old Residential colony,Non -Ess panel ) | 1.00 | Each | 0.00 | 115000.00 | 115000.00 | 107000.00 | 107000.00 | 110000.00 | 110000.00 | 107000.00 | BOSE ENGINEERING AND MARKETING COMPANY
20.00 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for the following size of PVC insulated and PVC sheathed / XLPE conductor cable of 1.1 KV grade as required.
21.00 | 3.5 x 50 sqmm | 2.00 | set | 0.00 | 3000.00 | 6000.00 | 2500.00 | 5000.00 | 4000.00 | 8000.00 | 5000.00 | BOSE ENGINEERING AND MARKETING COMPANY
22.00 | 3.5 x 95 sqmm | 2.00 | set | 0.00 | 4000.00 | 8000.00 | 3000.00 | 6000.00 | 6000.00 | 12000.00 | 6000.00 | BOSE ENGINEERING AND MARKETING COMPANY
23.00 | 3.5 x 185 sq. mm. | 4.00 | set | 0.00 | 5500.00 | 22000.00 | 4000.00 | 16000.00 | 8000.00 | 32000.00 | 16000.00 | BOSE ENGINEERING AND MARKETING COMPANY
24.00 | Supplying and making cable route marker with cement concrete 1:2:4 (1 cement: 2 coarse: 4 graded stone aggregate 20 mm niminal size) of size 60 cm X 60 cm at the bottom and 50 cm X 50 cm at the top with a thickness of 10 cm including inscription duly engraved as required. | 20.00 | Each | 0.00 | 500.00 | 10000.00 | 800.00 | 16000.00 | 450.00 | 9000.00 | 9000.00 | M/s J H Associates
25.00 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia medium duty approved ISI Mark including accessories, andproviding masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 9.00 | Set | 0.00 | 9000.00 | 81000.00 | 7000.00 | 63000.00 | 5000.00 | 45000.00 | 45000.00 | M/s J H Associates
26.00 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing along with existing surface/ recessed conduit/ submain wiring/ cable as required. | 100.00 | Meter | 0.00 | 20.00 | 2000.00 | 30.00 | 3000.00 | 30.00 | 3000.00 | 2000.00 | SHAKTI TECHNO FAB PRODUCTS
27.00 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia. GI pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 36.00 | Meter | 0.00 | 700.00 | 25200.00 | 500.00 | 18000.00 | 500.00 | 18000.00 | 18000.00 | M/s J H Associates, BOSE ENGINEERING AND MARKETING COMPANY
28.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | 36.00 | Meter | 0.00 | 250.00 | 9000.00 | 70.00 | 2520.00 | 180.00 | 6480.00 | 2520.00 | BOSE ENGINEERING AND MARKETING COMPANY
29.00 | Providing , fixing and laying of 100 mm dia G.I. Pipe (medium class) in existing trench i/c threading and coupling etc as required. | 30.00 | Meter | 0.00 | 1200.00 | 36000.00 | 1500.00 | 45000.00 | 1700.00 | 51000.00 | 36000.00 | SHAKTI TECHNO FAB PRODUCTS
| Total in Figures |  |  |  |  | 2657220.00 |  | 2238200.00 |  | 2824480.00
Lowest Amount Quoted BY: BOSE ENGINEERING AND MARKETING COMPANY(2238200.00)

## BOQ Summary
BOQ Summary Details Tender Title: Distribution of Power Supply from substation to AAI Residential Colony. Tender ID: 2022_AAI_107168_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | BOSE ENGINEERING AND MARKETING COMPANY | 2238200.00 | L1
| 2 | SHAKTI TECHNO FAB PRODUCTS | 2657220.00 | L2
| 3 | M/s J H Associates | 2824480.00 | L3