## BoQ1
Government eProcurement System Created By: Vivek Katara Created Date/Time: 18-Apr-2022 01:07 PM Tender Title: Extension of Runway 36 Towards 18 side by 1300 feet and allied works at Civil Airport Jammu. SH SITC of 2x160 KVA UPS System for Ground Lighting Facilities Tender ID: 2022_AAI_108062_1
Tender Inviting Authority: Airports Authority of India, Jammu Airport, Jammu
Name of Work: Extension of Runway 36 (towards 18 side) by 1300 feet and allied works at Civil Airport Jammu. (SH: SITC of 2 x 160 KVA UPS System for Ground Lighting Facilities).
Contract No: AAI/Jammu/Elect/RW05
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | GREWAL ELECTRIC CORPORATION(GSTN-03ABNPG6269P1Z2) |  | Saar Technologies(GSTN-04ABIFS3089A1ZD) |  | Anil Kumar Sharma(GSTN-01AIWPS0647K1ZU) |  | VENTURE INDIA(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SH(I): SITC of UPS and LT panels
1.01 | Design, Fabrication, Supply, Installation, Testing and Commisioning of 3 Phase, 50 Hz Online UPS system of 2x160 KVA capacity, 3-phase input, 3 phase output online UPS with double conversion IGBT technology with suitable rated isolation transformer to drive constant current regulators, Suitable for 100% unbalanced load, built in automatic static by pass, active input power factor correction, phase sequence corrector, pure sine wave output, input/ output isolation, compatibility with generator supply, cold start capability, EMI/RFI noise filter, advanced communication- RS232 port and user friendly LCD display, suitable to operate at 415V, 50Hz, 3 phase AC supply and capable to load 2 phase & single phase loads on 3phase output with 100% unbalanced and necessary safety protections, to be operated in parallel rudundancy configuration in dust and vermin proof cubicle panel duly painted and with ventillation ducts, forced air cooling, floor mounted comprising of supply and connecting required/suitable size & number of 12 V SMF batteries shall have backup time of minimum 30 minutes at rated full load for individual UPS along with battery rack, arranged in racks with terminals, intercell connectors, DC cables with insulated copper conductor of required size with sutaible capacity battery MCCB of interface with UPS as per site condition and all accessories and capable of giving desired output suitable to operate Airport runway Airfield lighting systems through Constant Current regulators with all contorls and protective circuits and conforming to IEC-62040-1/ IEC-62040-2/ IEC-62040-3/ IS 16242-1etc. complete as per technical specifications and approved make. | 1.00 | Set | 3847140.00 | 4600000.00 | 4600000.00 | 4600000.00 | 4600000.00 | 4200000.00 | 4200000.00 | 4300000.00 | 4300000.00 | 4200000.00 | Anil Kumar Sharma
1.02 | Outgoing LT panel for UPS: Design, fabrication, assembling, supply, installation, testing and commissioning of cubicle type - UPS Output LT panel floor mounted, free standing suitable for 415 V 3 phase, 4 wire 50 Hz AC supply system fabricated in compartmentalised design from CRCA sheet steel of 2 mm thick for frame work IP 42 and covers,3 mm thick for gland plates i/c cleaning and finishing complete 7 tank process for powder coating in approved shade, both sides extendable type TPN aluminium alloy busbars of high conductivity, extended rotary handles, DMC/SMC busbar supports, with bottom base channel of MS section not less than 100mm X 50 mm X 5 mm thick, entire panel shall have a common copper earthbar of size 25mm X 5 mm at the rear with 2 Nos. earth studs, solid connection from main busbar to switchgears with require size of aluminium busbar & control wiring with FRLS insulated copper conductor cable, provision of cable entry from both top & bottom, cable alleys, cable gland plates i/c accessrories as per specification and providing switchgears, metering instruments etc. as per specifications. (A) INCOMER: a) 2 Nos. 350 Amp, 50KA, 4P Moulded Case Circuit Breaker with Thermal magnetic release with thermal adjustability with O/C and S/C protection. b) 2 Nos. digital multifunction meter, Class 1.0, LCD type including suitable rating CTs for 3 phase, 4 wire operation. c) 2 Set of RYB phase indicating lamps controlled by MCBs. (I/C & O/G) d) 2 Set of ON/OFF Indication lamps. (B) BUSBARS: 400 Amp TPN busbars of high conductivity electrolytic quality aluminium alloy. (C) BUS COUPLER: a) 1 Nos. 350 Amp, 50KA, 4P Moulded Case Circuit Breake. b) 1 Set of RYB phase indicating lamps controlled by MCBs. c) 1 Set of ON/OFF Indication lamps. (D) OUTGOING: a) 4 Nos. 150 Amp, 35KA, 4P Moulded Case Circuit Breaker with Thermal magnetic release with thermal adjustability with O/C and S/C protection. b) 3 Nos. 100 Amp, 35KA, 4P Moulded Case Circuit Breaker with Thermal magnetic release with thermal adjustability with O/C and S/C protection. c) 3 Nos. 50 Amp, 35KA, 4P Moulded Case Circuit Breaker with Thermal magnetic release with thermal adjustability with O/C and S/C protection. | 1.00 | Job | 358000.00 | 412500.00 | 412500.00 | 480000.00 | 480000.00 | 500000.00 | 500000.00 | 370000.00 | 370000.00 | 370000.00 | VENTURE INDIA
1.03 | Incoming LT panel for UPS: Design, fabrication, assembling, supply, installation, testing and commissioning of cubicle type - UPS Input LT panel floor mounted, free standing suitable for 415 V 3 phase, 4 wire 50 Hz AC supply system fabricated in compartmentalised design from CRCA sheet steel of 2 mm thick for frame work IP 42 and covers, 3 mm thick for gland plates i/c cleaning and finishing complete 7 tank process for powder coating in approved shade, both sides extendable type TPN aluminium alloy busbars of high conductivity, extended rotary handles, DMC/SMC busbar supports, with bottom base channel of MS section not less than 100mm X 50 mm X 5 mm thick, entire panel shall have a common copper earthbar of size 25mm X 5 mm at the rear with 2 Nos. earth studs, solid connection from main busbar to switchgears with require size of aluminium busbar & control wiring with FRLS insulated copper conductor cable, provision of cable entry from both top & bottom, cable alleys, cable gland plates i/c accessrories as per specification and providing switchgears, metering instruments etc. as per specifications. (A) INCOMER: a) 2 Nos. 630 Amp, 50kA, 4P Moulded Case Circuit Breaker with Thermal magnetic release with thermal adjustability with O/C and S/C protection. b) 2 Nos. digital multifunction meter, Class 1.0, LCD type including suitable rating CTs for 3 phase, 4 wire operation. c) 2 Set of RYB phase indicating lamps controlled by MCBs. (I/C & O/G) d) 2 Set of ON/OFF Indication lamps. (B) BUSBARS: 800 Amp TPN busbars of high conductivity electrolytic quality aluminium alloy. (C) BUS COUPLER: a) 1 Nos. 630 Amp, 50KA, 4P Moulded Case Circuit Breake. b) 1 Set of RYB phase indicating lamps controlled by MCBs. c) 1 Set of ON/OFF Indication lamps. (D) OUTGOING: a) 2 Nos. 400 Amp, 35kA, 4P Moulded Case Circuit Breaker with Thermal magnetic release with thermal adjustability with O/C and S/C protection. b) 4 Nos. 250 Amp, 35kA, 4P Moulded Case Circuit Breaker with Thermal magnetic release with thermal adjustability with O/C and S/C protection. c) 2 Nos. 200 Amp, 35kA, 4P Moulded Case Circuit Breaker with Thermal magnetic release with thermal adjustability with O/C and S/C protection. d) 2 Nos. 150 Amp, 35kA, 4P Moulded Case Circuit Breaker with Thermal magnetic release with thermal adjustability with O/C and S/C protection. e) 12 Nos. 100 Amp, 35kA, 4P Moulded Case Circuit Breaker with Thermal magnetic release with thermal adjustability with O/C and S/C protection. f) 4 Nos. 63 Amp, 10kA, 4P Miniature Circuit Breaker, C-series. g) 4 Nos. 40 Amp, 10kA, DP Miniature Circuit Breaker. C-series. h) 4 Nos. 32 Amp, 10kA, SP Miniature Circuit Breaker. C-series. i) 4 Nos. 16 Amp, 10kA, SP Miniature Circuit Breaker. C-series. j) ON/OFF Indication lamps with all outgoing MCCBs. | 1.00 | Job | 719000.00 | 812500.00 | 812500.00 | 1070000.00 | 1070000.00 | 800000.00 | 800000.00 | 850000.00 | 850000.00 | 800000.00 | Anil Kumar Sharma
2.00 | SH(II): Suppy of cable
2.01 | Supply of following size FR PVC insulated single core unsheathed wire flexible bright anealed multi stranded care copper conductor 650/1100 volts grade as per IS: 694-1990 in 100 mtr. coil packing. a) 1Cx 50 Sq. mm | 200.00 | Mtr | 553.00 | 890.00 | 178000.00 | 550.00 | 110000.00 | 500.00 | 100000.00 | 480.00 | 96000.00 | 96000.00 | VENTURE INDIA
3.00 | SH(III): Laying and end termination of cables
3.01 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL pipe as required. a) Above 35 sq. mm and upto 95 sq. mm | 40.00 | Mtr | 55.00 | 50.00 | 2000.00 | 370.00 | 14800.00 | 100.00 | 4000.00 | 30.00 | 1200.00 | 1200.00 | VENTURE INDIA
3.02 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required. a) Above 35 sq. mm and upto 95 sq. mm | 50.00 | Mtr | 44.00 | 50.00 | 2500.00 | 370.00 | 18500.00 | 100.00 | 5000.00 | 30.00 | 1500.00 | 1500.00 | VENTURE INDIA
3.03 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required. a) Above 35 sq. mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp) | 40.00 | Mtr | 121.00 | 50.00 | 2000.00 | 370.00 | 14800.00 | 100.00 | 4000.00 | 50.00 | 2000.00 | 2000.00 | VENTURE INDIA, GREWAL ELECTRIC CORPORATION
3.04 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required. a) Above 35 sq. mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp) | 70.00 | Mtr | 86.00 | 60.00 | 4200.00 | 370.00 | 25900.00 | 100.00 | 7000.00 | 45.00 | 3150.00 | 3150.00 | VENTURE INDIA
3.05 | Supplying and making end termination with brass single compression gland and aluminium lugs for following sizes of PVC/XLPE insulated PVC sheathed aluminium conductor cable of 1.1 KV grade as required. a) 3.5 x 25 sq.mm (28 mm) | 4.00 | Set | 290.00 | 500.00 | 2000.00 | 90.00 | 360.00 | 800.00 | 3200.00 | 125.00 | 500.00 | 360.00 | Saar Technologies
3.06 | b) 3.5 x 35 sq.mm (32 mm) | 6.00 | Set | 348.00 | 500.00 | 3000.00 | 100.00 | 600.00 | 800.00 | 4800.00 | 170.00 | 1020.00 | 600.00 | Saar Technologies
3.07 | c) 3.5 x 50 sq.mm (35 mm) | 4.00 | Set | 382.00 | 550.00 | 2200.00 | 125.00 | 500.00 | 1000.00 | 4000.00 | 200.00 | 800.00 | 500.00 | Saar Technologies
3.08 | d) 3.5 x 95 sq.mm (45 mm) | 4.00 | Set | 549.00 | 850.00 | 3400.00 | 200.00 | 800.00 | 1200.00 | 4800.00 | 350.00 | 1400.00 | 800.00 | Saar Technologies
3.09 | e) 3.5 x 120 sq.mm (45 mm) | 3.00 | Set | 568.00 | 850.00 | 2550.00 | 220.00 | 660.00 | 800.00 | 2400.00 | 350.00 | 1050.00 | 660.00 | Saar Technologies
3.10 | f) 3.5 x 150 sq.mm (50 mm) | 3.00 | Set | 644.00 | 875.00 | 2625.00 | 240.00 | 720.00 | 800.00 | 2400.00 | 300.00 | 900.00 | 720.00 | Saar Technologies
3.11 | g) 3.5 x 185 sq.mm (57 mm) | 4.00 | Set | 815.00 | 890.00 | 3560.00 | 310.00 | 1240.00 | 800.00 | 3200.00 | 325.00 | 1300.00 | 1240.00 | Saar Technologies
3.12 | h) 3.5 x 240 sq.mm (62 mm) | 3.00 | Set | 939.00 | 1275.00 | 3825.00 | 400.00 | 1200.00 | 800.00 | 2400.00 | 350.00 | 1050.00 | 1050.00 | VENTURE INDIA
3.13 | Supplying and making end termination with PVC single compression gland and copper lugs for following sizes of FR PVC insulated single core unsheathed wire flexible bright anealed multi stranded care copper conductor 650/1100 volts grade as required. a) 1Cx 50 Sq. mm | 40.00 | Set | 154.00 | 250.00 | 10000.00 | 350.00 | 14000.00 | 200.00 | 8000.00 | 90.00 | 3600.00 | 3600.00 | VENTURE INDIA
4.00 | SH(IV): Supplying and installing of cable trays
4.01 | Supplying and installing following size of perforated painted with powder coating M.S. cable trays with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with M.S. suspenders or fixed from the floor with M.S. angles including bolts & nuts, painting suspenders/ angle etc. as required. a) 200 mm width X 50 mm depth X 1.6 mm thickness | 150.00 | Mtr | 693.00 | 950.00 | 142500.00 | 585.00 | 87750.00 | 500.00 | 75000.00 | 425.00 | 63750.00 | 63750.00 | VENTURE INDIA
4.02 | Supplying and installing following size of perforated painted with powder coating M.S. cable trays bends with perforation not more than 17.5%,, joined with connectors, suspended from the ceiling with M.S. suspenders or fixed from the floor with M.S. angles including bolts & nuts, painting suspenders/ angle including bolts & nuts, painting suspenders etc as required. a) 200 mm width X 50 mm depth X 1.6 mm thickness | 5.00 | Each | 1327.00 | 750.00 | 3750.00 | 1000.00 | 5000.00 | 650.00 | 3250.00 | 400.00 | 2000.00 | 2000.00 | VENTURE INDIA
4.03 | Supplying and installing following size of perforated painted with powder coating M.S. cable trays Tee with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders or fixed from the floor with M.S. angles including bolts & nuts, painting suspenders/ angle including bolts & nuts, painting suspenders etc as required. a) 225 mm width X 50 mm depth X 1.6 mm thickness | 4.00 | Each | 1521.00 | 1000.00 | 4000.00 | 1000.00 | 4000.00 | 1275.00 | 5100.00 | 800.00 | 3200.00 | 3200.00 | VENTURE INDIA
4.04 | Supplying and installing following size of perforated painted with powder coating M.S. cable trays Cross Member with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspendersor fixed from the floor with M.S. angles including bolts & nuts, painting suspenders/ angle including bolts & nuts, painting suspenders etc as required. a) 225 mm width X 50 mm depth X 1.6 mm thickness | 3.00 | Each | 1521.00 | 1000.00 | 3000.00 | 1000.00 | 3000.00 | 1800.00 | 5400.00 | 800.00 | 2400.00 | 2400.00 | VENTURE INDIA
4.05 | Supplying and installing following size of perforated painted with powder coating M.S. cable trays Reducer with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders or fixed from the floor with M.S. angles including bolts & nuts, painting suspenders/ angle including bolts & nuts, painting suspenders etc as required. a) 225 mm width X 50 mm depth X 1.6 mm thickness | 4.00 | Each | 1472.00 | 1500.00 | 6000.00 | 1000.00 | 4000.00 | 1800.00 | 7200.00 | 100.00 | 400.00 | 400.00 | VENTURE INDIA
5.00 | SH(V): Earthing works
5.01 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 2.00 | Set | 7218.00 | 14000.00 | 28000.00 | 2200.00 | 4400.00 | 5000.00 | 10000.00 | 10000.00 | 20000.00 | 4400.00 | Saar Technologies
5.02 | Providing and fixing 25 mm x 5 mm GI strip on surface or in recess for connections with clamping etc as required. | 60.00 | Mtr | 239.00 | 160.00 | 9600.00 | 120.00 | 7200.00 | 180.00 | 10800.00 | 170.00 | 10200.00 | 7200.00 | Saar Technologies
5.03 | Providing and fixing 25 mm X 5 mm GI strip in 40 mm dia GI pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 30.00 | Mtr | 561.00 | 500.00 | 15000.00 | 160.00 | 4800.00 | 500.30 | 15009.00 | 350.00 | 10500.00 | 4800.00 | Saar Technologies
5.04 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 2.00 | Set | 13694.00 | 20000.00 | 40000.00 | 9400.00 | 18800.00 | 10000.00 | 20000.00 | 12500.00 | 25000.00 | 18800.00 | Saar Technologies
5.05 | Providing and fixing 25 mm x 5 mm Copper strip on surface or in recess for connections with clamping etc as required. | 60.00 | Mtr | 1172.00 | 1400.00 | 84000.00 | 1300.00 | 78000.00 | 1200.00 | 72000.00 | 1200.00 | 72000.00 | 72000.00 | VENTURE INDIA, Anil Kumar Sharma
5.06 | Providing and fixing 25 mm X 5 mm Copper strip in 40 mm dia GI pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 30.00 | Mtr | 1421.00 | 1850.00 | 55500.00 | 160.00 | 4800.00 | 1600.00 | 48000.00 | 1400.00 | 42000.00 | 4800.00 | Saar Technologies
5.07 | Providing and fixing 6 SWG dia G.I. earth wire along the cable length or on surface or in recess for loop earthing as required. | 120.00 | Mtr | 66.00 | 40.00 | 4800.00 | 13.00 | 1560.00 | 30.00 | 3600.00 | 25.00 | 3000.00 | 1560.00 | Saar Technologies
6.00 | SH(VI): Miscellaneous work
6.01 | Disconnection of end termination of following size of PVC insulated and PVC sheathed/ XLPE aluminium conductor cable of 1.1 kV grade from the existing panel complete as required. a) 3.5 x 25 sq.mm (28 mm) | 4.00 | Set | 59.00 | 250.00 | 1000.00 | 500.00 | 2000.00 | 100.00 | 400.00 | 40.00 | 160.00 | 160.00 | VENTURE INDIA
6.02 | b) 3.5 x 35 sq.mm (32 mm) | 6.00 | Set | 59.00 | 250.00 | 1500.00 | 500.00 | 3000.00 | 100.00 | 600.00 | 40.00 | 240.00 | 240.00 | VENTURE INDIA
6.03 | c) 3.5 x 50 sq.mm (35 mm) | 4.00 | Set | 74.00 | 300.00 | 1200.00 | 500.00 | 2000.00 | 100.00 | 400.00 | 40.00 | 160.00 | 160.00 | VENTURE INDIA
6.04 | d) 3.5 x 95 sq.mm (45 mm) | 4.00 | Set | 74.00 | 500.00 | 2000.00 | 500.00 | 2000.00 | 100.00 | 400.00 | 40.00 | 160.00 | 160.00 | VENTURE INDIA
6.05 | e) 3.5 x 120 sq.mm (45 mm) | 3.00 | Set | 89.00 | 600.00 | 1800.00 | 500.00 | 1500.00 | 100.00 | 300.00 | 40.00 | 120.00 | 120.00 | VENTURE INDIA
6.06 | f) 3.5 x 150 sq.mm (50 mm) | 3.00 | Set | 89.00 | 650.00 | 1950.00 | 500.00 | 1500.00 | 100.00 | 300.00 | 50.00 | 150.00 | 150.00 | VENTURE INDIA
6.07 | g) 3.5 x 185 sq.mm (57 mm) | 4.00 | Set | 119.00 | 700.00 | 2800.00 | 500.00 | 2000.00 | 100.00 | 400.00 | 50.00 | 200.00 | 200.00 | VENTURE INDIA
6.08 | h) 3.5 x 240 sq.mm (62 mm) | 3.00 | Set | 134.00 | 850.00 | 2550.00 | 500.00 | 1500.00 | 100.00 | 300.00 | 70.00 | 210.00 | 210.00 | VENTURE INDIA
7.00 | SH(VII): CMC of UPS
7.01 | Comprehensive annual maintenance contract for 160 KVA UPS (for item No.1) inclusive of all spare parts to maintain the system healthy on all days inclusive of periodic maintenance as per schedule as well as breakdown maintenance as and when called or needed. [Note: AMC will start after Two years of completion of work as for Two years same are covered under defect liability period.] a) For First year (Start after sucessfully completion of 2 year defect liability period) [Remark: 3% of item no.1 of SH(I) | 2.00 | Per set per year | 57707.10 | 69000.00 | 138000.00 | 69000.00 | 138000.00 | 63000.00 | 126000.00 | 64500.00 | 129000.00 | 126000.00 | Anil Kumar Sharma
7.02 | b) For Second year [Remark: 3% commulative enhancement on first year cost] | 2.00 | Per set per year | 59438.00 | 71070.00 | 142140.00 | 71070.00 | 142140.00 | 64890.00 | 129780.00 | 66435.00 | 132870.00 | 129780.00 | Anil Kumar Sharma
7.03 | c) For Third year [Remark: 3% commulative enhancement on second year cost] | 2.00 | Per set per year | 61221.00 | 73202.00 | 146404.00 | 73202.00 | 146404.00 | 66837.00 | 133674.00 | 68428.00 | 136856.00 | 133674.00 | Anil Kumar Sharma
7.04 | d) For Forth year [Remark: 3% commulative enhancement on third year cost] | 2.00 | Per set per year | 63058.00 | 75398.00 | 150796.00 | 75398.00 | 150796.00 | 68842.00 | 137684.00 | 70481.00 | 140962.00 | 137684.00 | Anil Kumar Sharma
7.05 | d) For Firth year [Remark: 3% commulative enhancement on forth year cost] | 2.00 | Per set per year | 64950.00 | 77660.00 | 155320.00 | 77660.00 | 155320.00 | 70907.00 | 141814.00 | 72595.00 | 145190.00 | 141814.00 | Anil Kumar Sharma
| Total in Figures |  |  |  |  | 7190470.00 |  | 7325550.00 |  | 6602611.00 |  | 6576198.00
Lowest Amount Quoted BY: VENTURE INDIA(6576198.00)

## BOQ Summary
BOQ Summary Details Tender Title: Extension of Runway 36 Towards 18 side by 1300 feet and allied works at Civil Airport Jammu. SH SITC of 2x160 KVA UPS System for Ground Lighting Facilities Tender ID: 2022_AAI_108062_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | VENTURE INDIA | 6576198.00 | L1
| 2 | Anil Kumar Sharma | 6602611.00 | L2
| 3 | GREWAL ELECTRIC CORPORATION | 7190470.00 | L3
| 4 | Saar Technologies | 7325550.00 | L4