## BoQ1
Government eProcurement System Created By: Manoj Kumar Sahoo Created Date/Time: 03-Aug-2022 03:17 PM Tender Title: Replacement of Fire alarm detectors and FAS panel and Replacement of AC Units and Air curtains at MSSR Building, Yarada hills AAI Visakhapatnam Tender ID: 2022_AAI_110655_1
Tender Inviting Authority:SENIOR MANAGER (ENGG-ELECT), AIRPORTS AUTHORITY OF INDIA, VISAKHAPATNAM AIRPORT, VISAKHAPATNAM.
Name of Work: Replacement of Fire alarm detectors and FAS panel and AC units & Air curtains at MSSR building, Yarada hills AAI Visakhapatna.
Contract No: 2022_AAI_110655_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | GRID2CHIP(GSTN-36AAKFG3006E1ZT) |  | QUALITY ENGINEERING SERVICES(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SITC of UL/EN listed (latest version) intelligent addressable multisensor detector {Smoke + heat } with inbuilt fault isolator / isolator base and with unique optical sensing chamber, visible LED, fully coated circuit board, superior RF / Transient protection suitable for 2 wires loop connection, complete with plug into common separate base & housing constructed of polycarbonate complete with connections etc. as required and to be installed under/ above false ceiling roof and concealed space including dismantling of existing smoke and heat detectors and submission to AAI store complete as required as per technical specifications. (Cost of plug in common base shall deemed to be included in cost of detectors) | 55.00 | No's |  | 3019.00 | 166045.00 | 2950.00 | 162250.00 | 162250.00 | QUALITY ENGINEERING SERVICES
2.00 | SITC of UL/EN listed (Latest Version) intelligent Addressable type Heat Detector (Fixed cum-rate of rise type) with inbuilt fault isolator / isolator base with range upto 60° C complete with all fixing accessories like base, base box, self adhesive sticker indicating loop number and address etc. to be installed under/above false ceiling, roof and concealed space,interconnecting to loop cable including dismantling of existing smoke and heat detectors and submission to AAI store complete as required as per technical specifications. | 2.00 | No's |  | 2809.00 | 5618.00 | 3000.00 | 6000.00 | 5618.00 | GRID2CHIP
3.00 | SITC of UL/EN listed (latest version) intelligent addressable Manual Pull station (not break glass type) suitable for semi flush mounting with inbuilt fault isolator / isolator module with double gang outlet box, equipment for key operated test-reset lock, electronic or rotary switches for address setting. Manual pull station shall be connected with two wire to SLC loop of Fire Control Panel. Cover shall be made out of poly carbonate equivalent with clear operating instruction complete with connections including dismantling of existing mannual call station and submission to AAI store etc. as required as per technical specifications. | 5.00 | No's |  | 3805.00 | 19025.00 | 2600.00 | 13000.00 | 13000.00 | QUALITY ENGINEERING SERVICES
4.00 | SITC of UL/EN listed (latest version) loop powered addressable Hooter-cum- strobe with inbuilt fault isolator / isolator module with minimum 90dB output at a distance of 1 mtr. including dismantling of existing hooters and submission to AAI store etc. as required and as per technical specifications. | 5.00 | No's |  | 10033.00 | 50165.00 | 3700.00 | 18500.00 | 18500.00 | QUALITY ENGINEERING SERVICES
5.00 | SITC of UL/EN listed (Latest Version) Addressable type fault isolator for isolating shorted, de-linked and loose circuits between two successive fault isolators with automatic resetting arrangement to be interconnecting to loop cable including dismantling of existing fault Isolator and submission to AAI store etc. complete as required and as per technical specifications. | 2.00 | No's |  | 100.00 | 200.00 | 2800.00 | 5600.00 | 200.00 | GRID2CHIP
6.00 | SITC of UL/EN listed Microprocessor based Intelligent Analogue Addressable type Fire alarm control panel of two loop, each loop having capacity of connecting minimum 99 +99 intellegent addressable detectors and device in any combination, with minimum 80 character LCD display, zone creatable, event historical logging, flash EPROM, CPU Main Board, 24 volts sealed lead acid batteries sufficient for 24 hours running in normal condition and 30 minutes in alarm condition,sufficient serial ports, programmable at site,including supply of autodialer and connecting with fire control panel, dismantling of existing panel and submission to AAI store etc. complete as required as per technical specifications. etc complete as required. | 1.00 | No |  | 93188.00 | 93188.00 | 130000.00 | 130000.00 | 93188.00 | GRID2CHIP
7.00 | Supply, Laying, Fixing, Testing and Commissioning of XLPE insulated, PVC sheathed 2c x 1.5 sq.mm FRLS , stranded copper conductor, armoured cable,600/1100V conforming to IS 7098 (Part-I) with upto date amendments including both end terminations with copper lugs & glands etc. on existing cable tray / surface suitably clamped as per site requirement complete as required. | 662.00 | Mts |  | 113.00 | 74806.00 | 82.00 | 54284.00 | 54284.00 | QUALITY ENGINEERING SERVICES
8.00 | Supply installation testing and commisioning of 24V dc power supply system , it shall provide supplies to hooter/conventional sounder/strobers . It shall have LED indications for power supply ON, batter fail, battery charging etc ,shall have inbuilt battery charging circuit with 2 no of 12 V, 7 AH batteries. | 5.00 | No's |  | 9750.00 | 48750.00 | 2800.00 | 14000.00 | 14000.00 | QUALITY ENGINEERING SERVICES
9.00 | SITC of UL/EN listed (latest version) Intelligent addressable Control Module/ Relay Module (output module) with inbuilt fault isolator / isolator module for activate hooter/conventional sounders/strobers etc complete with termination etc. complete as required and as per technical specifications. | 10.00 | No's |  | 3170.00 | 31700.00 | 2800.00 | 28000.00 | 28000.00 | QUALITY ENGINEERING SERVICES
10.00 | Supply, installation, testing and commissioning of Response Indicators (metal plate) for getting fire indications of detectors installed above false ceiling area interconnecting to loop cable complete as required. | 24.00 | each |  | 225.00 | 5400.00 | 155.00 | 3720.00 | 3720.00 | QUALITY ENGINEERING SERVICES
11.00 | SITC of 2.0 TR Split Inverter Cool Type air conditioner unit fitted with copper tube condensor, hermatically sealed rotary compressors operating on refrigerant R-32 / Non CFC, 5 Star Rating, suitable for wall mounting with cordless remote and operation on 230V, 50Hz single phase A.C supply including fixing the outdoor unit with fabricated MS Stand etc complete as required and as per enclosed technical specification including supply of suitable size of Copper tube with nitrile insulation and suitable size PVC insulated FR type cu wire of 3 mtr length.( Noter: Cost of gas charging as per site requirement is also included in this item.) | 3.00 | each |  | 44844.00 | 134532.00 | 50000.00 | 150000.00 | 134532.00 | GRID2CHIP
12.00 | SITC of 3.0 TR vertical split type air conditioner of floor mounting type fitted with copper tube condensor, rotary compressors operating on refrigerant R-32 /Non CFC, with cordless remote and operation on 415V, 50 Hz three phase A.C supply including fixing the outdoor unit with fabricated MS Stand or as per site specification including supply & interconnection of suitable size of Copper tube with nitrile insulation and suitable size PVC insulated FR type copper wire of 3 mtr length. ( Note: Cost of gas charging as per site requirement is also included in this item.) | 5.00 | each |  | 124890.00 | 624450.00 | 101000.00 | 505000.00 | 505000.00 | QUALITY ENGINEERING SERVICES
13.00 | Supply and fixing of extra refregerant copper piping with nitrile insulation ( if required) and PVC insulated FR type copper wire suitable for 3.0 TR Vertical Split AC unit as mention In BOQ item No. -12 etc complete as required | 45.00 | mtr |  | 1125.00 | 50625.00 | 1350.00 | 60750.00 | 50625.00 | GRID2CHIP
14.00 | Supply and fixing of extra refrigerant copper piping with nitrile insulation ( if required) and PVC insulated FR type copper wire suitable for 2.0 TR Split AC unit as mention in BOQ Item No-11 etc complete as required. | 3.00 | mtr |  | 1563.00 | 4689.00 | 950.00 | 2850.00 | 2850.00 | QUALITY ENGINEERING SERVICES
15.00 | Supply and fixing of drain pipe connection from indoor to outside wall including all accessories etc complete as required. | 50.00 | mtr |  | 750.00 | 37500.00 | 250.00 | 12500.00 | 12500.00 | QUALITY ENGINEERING SERVICES
16.00 | SITC of RO + UV storage type water purifier with minimum storage capacity of 6ltr ,minimum flow rate 15 LPH, Filter Change Alarm,UV fail Alaram, including 20" external prefilter and fully automatic operated suitable for 230V , 50 Hz AC supply etc . (Simillar to Make:EUREKA FORBES/KENT/AQUA) | 3.00 | each |  | 20000.00 | 60000.00 | 21000.00 | 63000.00 | 60000.00 | GRID2CHIP
17.00 | Supply and fixing of dual AC Controller with protection of AC against under voltage,Over voltage,under load & over load,alarm for AC fail,power fail & high temprature and suitable for operating at 230V±10%, 50 Hz,Single Phase A.C.Supply. (Simillar to make Minilec,Model:-PROTOCOM4) | 9.00 | each |  | 10000.00 | 90000.00 | 7200.00 | 64800.00 | 64800.00 | QUALITY ENGINEERING SERVICES
| Total in Figures |  |  |  |  | 1496693.00 |  | 1294254.00
Lowest Amount Quoted BY: QUALITY ENGINEERING SERVICES(1294254.00)

## BOQ Summary
BOQ Summary Details Tender Title: Replacement of Fire alarm detectors and FAS panel and Replacement of AC Units and Air curtains at MSSR Building, Yarada hills AAI Visakhapatnam Tender ID: 2022_AAI_110655_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | QUALITY ENGINEERING SERVICES | 1294254.00 | L1
| 2 | GRID2CHIP | 1496693.00 | L2