## BoQ1
Government eProcurement System Created By: PRAKASH WAKPAIJAN Created Date/Time: 17-May-2022 11:18 AM Tender Title: Providing Street Light and High mast at Chennai Airport Tender ID: 2022_AAI_110733_1
Tender Inviting Authority: Asst.General Manager (Engg-Elect) - II, Project Electrical Division, Chennai Airport Project, Chennai.
Name of Work: Modernization of Chennai Airport Phase - II, Chenai SH: Construction of Road in front of Terminal Building – Providing Street lights and Highmast at Chennai Airport.(Electrical works)
Contract No: 2022_AAI_110733
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | vk sam engineering(GSTN-33AMZPS4037L1ZA) |  | R.K.M. ELECTRICALS(GSTN-33ACAPM4207B2ZE) |  | VISHAL ELECTRICALS(GSTN-09ACYPB4483E1Z9) |  | DElite System Engineering (India) Pvt. Ltd.(GSTN-NA) |  | C R ELECTRICALS(GSTN-NA) |  | Surya Roshni Limited(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply of following size of 1.1 KV grade multicore aluminium conductor XLPE insulated and PVC sheathed armoured cable as per IS : 7098:1988 Part 1 with upto date amendments.
2.00 | 4 Core X 16 Sqmm Al.Armoured cable | 4500.00 | Mtrs |  | 151.00 | 679500.00 | 195.00 | 877500.00 | 173.42 | 780390.00 | 159.00 | 715500.00 | 155.00 | 697500.00 | 138.82 | 624690.00 | 624690.00 | Surya Roshni Limited
3.00 | 4 Core X 25 Sqmm Al.Armoured cable | 2000.00 | Mtrs |  | 198.00 | 396000.00 | 257.00 | 514000.00 | 226.78 | 453560.00 | 209.00 | 418000.00 | 209.00 | 418000.00 | 195.23 | 390460.00 | 390460.00 | Surya Roshni Limited
4.00 | 3.5 Core X 95 Sqmm Al.Armoured cable | 1400.00 | Mtrs |  | 507.00 | 709800.00 | 680.00 | 952000.00 | 583.74 | 817236.00 | 609.00 | 852600.00 | 537.00 | 751800.00 | 488.22 | 683508.00 | 683508.00 | Surya Roshni Limited
5.00 | 3.5 Core X 185 Sqmm Al.Armoured cable | 1000.00 | Mtrs |  | 928.00 | 928000.00 | 1210.00 | 1210000.00 | 1069.50 | 1069500.00 | 999.00 | 999000.00 | 978.00 | 978000.00 | 921.17 | 921170.00 | 921170.00 | Surya Roshni Limited
6.00 | Supply of street light luminarie 60-65W LED IP 66 protection made of single High pressure Die- cast aluminium / Standard alloy, high power LED light source, PDC housing with finless design and poly corbanet cover IK08 and the luminaire comes with dedicated street optices making it suitable for wide verity road application. The luminaire shall be able to deliver a system lumen of >7000 lumens. The CCT shall be 6500K, , operating voltage 140 V-270 V, Lumen efficacy of LED >110 lm/W and viewing angle of 120° Not less than 50000 burning hours. The electronic Powered by an integral, isolated electronic LED driver (SMPS based constant current supply) with lower THD, Output Open / Short Circuit protection, Over Voltage protection, Surge Voltage Protection & other safety test Philips Make of Cat No. BRP062 LED 65CW SLA S1 PSU including driver or equivalent etc, as required. | 71.00 | Nos |  | 2508.00 | 178068.00 | 3300.00 | 234300.00 | 2300.00 | 163300.00 | 3899.00 | 276829.00 | 3508.00 | 249068.00 | 1687.00 | 119777.00 | 119777.00 | Surya Roshni Limited
7.00 | Supply of street light luminarie 45W LED IP 66 protection made of single High pressure Die- cast aluminium / Standard alloy, high power LED light source, PDC housing with finless design and poly corbanet cover IK08 and the luminaire comes with dedicated street optices making it suitable for wide verity road application. The luminaire shall be able to deliver a system lumen of >7000 lumens. The CCT shall be 6500K, , operating voltage 140 V-270 V, Lumen efficacy of LED >110 lm/W and viewing angle of 120° Not less than 50000 burning hours. The electronic Powered by an integral, isolated electronic LED driver (SMPS based constant current supply) with lower THD, Output Open / Short Circuit protection, Over Voltage protection, Surge Voltage Protection & other safety test Philips Make of Cat No. BRP052 LED 045CW SLMR FG S1 PSU GR including driver or equivalent etc, as required. | 97.00 | Nos |  | 1795.00 | 174115.00 | 2500.00 | 242500.00 | 1725.00 | 167325.00 | 2999.00 | 290903.00 | 2852.00 | 276644.00 | 1870.00 | 181390.00 | 167325.00 | VISHAL ELECTRICALS
8.00 | Supplying,assembly,erection,connecting,testing and commisioning of Standard of 7.0 mtrs long street light pole(above ground)GRP pole(Pressure as per IS 878 part 3 or as per relevant standard) with stiffeners,chain,Allen bolt,1 m to 1.5m long arm bracket 48mm x 3 mm thick,foundation bolts,pre-fabricated plate,template accessories,nut and washers,factory finish,Base Plate.The column shall be provided with flush door at the bottom with proper strengthenening to the Cut-out of the door opening,an outdoor IP 66 rated junction/looping box with heavy duty 3 phase and neutral ,32 amp connector with 10 A DP MCB,Lightning Finial,including all accessories complete as required as per specification and as approved by Engineer-In Charge.The pole design ,foundation bolt design shall be supported by necessary strcutural Calculation.as per the pole strcutural design and soil bearing capacity,the pole shall have proper door with rubber gasket for installing electrical components for connetions.The pole shall be including necessary electrical components like MCBs,Din Rail etc.The pole shoud be Elegant and Decorative type Airport Infrastructure developing , individual GI earthing system & connection etc with accessories complete.( Including civil work foundation ) Model: Bajaj: BAJAJ 7m GRP Flanged Conical Pole, Teknihan: A1070 or equalant . The necessary Test Certificate to be produced
9.00 | Single Arm Bracket | 52.00 | Nos |  | 42330.00 | 2201160.00 | 43000.00 | 2236000.00 | 41183.50 | 2141542.00 | 33999.00 | 1767948.00 | 45068.00 | 2343536.00 | 41914.00 | 2179528.00 | 1767948.00 | DElite System Engineering (India) Pvt. Ltd.
10.00 | Double Arm Bracket | 6.00 | Nos |  | 43413.00 | 260478.00 | 44000.00 | 264000.00 | 42046.00 | 252276.00 | 33999.00 | 203994.00 | 46108.00 | 276648.00 | 43497.00 | 260982.00 | 203994.00 | DElite System Engineering (India) Pvt. Ltd.
11.00 | Supplying,assembly,erection,connecting,testing and commisioning of Standard of 9.0 mtrs long street light pole(above ground)GRP pole(Pressure as per IS 878 part 3 or as per relevant standard) with stiffeners,chain,Allen bolt,1 m to 1.5m long arm bracket 48mm x 3 mm thick,foundation bolts,pre-fabricated plate,template accessories,nut and washers,factory finish,Base Plate.The column shall be provided with flush door at the bottom with proper strengthenening to the Cut-out of the door opening,an outdoor IP 66 rated junction/looping box with heavy duty 3 phase and neutral ,32 amp connector with 10 A DP MCB,Lightning Finial,including all accessories complete as required as per specification and as approved by Engineer-In Charge.The pole design ,foundation bolt design shall be supported by necessary strcutural Calculation.as per the pole strcutural design and soil bearing capacity,the pole shall have proper door with rubber gasket for installing electrical components for connetions.The pole shall be including necessary electrical components like MCBs,Din Rail etc.The pole shoud be Elegant and Decorative type Airport Infrastructure developing , individual GI earthing system & connection etc with accessories complete.( Including civil work foundation ). Model: Bajaj: BAJAJ 9m GRP Flanged Conical Pole, Teknihan: A1090 or equalant . The necessary Test Certificate to be produced .
12.00 | Single Arm Bracket | 68.00 | Nos |  | 47403.00 | 3223404.00 | 49000.00 | 3332000.00 | 48416.00 | 3292288.00 | 37999.00 | 2583932.00 | 49664.00 | 3377152.00 | 47979.00 | 3262572.00 | 2583932.00 | DElite System Engineering (India) Pvt. Ltd.
13.00 | Double Arm Bracket | 10.00 | Nos |  | 48429.00 | 484290.00 | 51000.00 | 510000.00 | 49278.50 | 492785.00 | 37999.00 | 379990.00 | 50705.00 | 507050.00 | 49750.00 | 497500.00 | 379990.00 | DElite System Engineering (India) Pvt. Ltd.
14.00 | Supply, Installation, Testing & commissioning of outdoor type, double door, street light service / Sub feeder pillar, fabricated out of 3.15 mm steel sheet duly powder coated, dust and Vermin proof with one no. 100A Incomer MCCB 25KA, bus bar as required, 32A FP MCB 10KA- 5 Nos , Astro type digital timer- 1 No., 100A 3P power contactor,daylight sensor, Timer, Voltmeter, Ameter, CT, Indication lamps, danger notice plate etc as required including connection of cables i/c supply and installation of brick foundation with plaster for the feeder pillar including providing and fixing of MS support for panel base size of 75 x 40 x 6 MM 'C' Channel including Cutting, Grinding, welding etc. as required. Details of cost for One Panel | 4.00 | Set |  | 65233.00 | 260932.00 | 150000.00 | 600000.00 | 98150.00 | 392600.00 | 81999.00 | 327996.00 | 115050.00 | 460200.00 | 97729.00 | 390916.00 | 260932.00 | vk sam engineering
15.00 | Design, Supply, Installation , testing and commissioning of Outdoor type duly wired 415Volts, 50Hz, 3phase, 4wire electrical MAIN OUTDOOR FEEDER PILLER having I/C& O/G feeders, instrumentation metering, protection system, aluminium busbars & other components power contactor, Voltmeter, Ameter, CT, Indication lamps, danger notice plate etc as required including connection of cables i/c supply completely as per single line diagram and as per detailed technical specifications. The panel shall be of modular type, floor mounting, free standing, vermin proof, IP-65 grade, made out of CRCA sheet steel of 1.6mm thickness for body & 2mm for load bearing points, powder coated painting, fuseless type confirming to relevent IS standards. The panel shall have microprocessor based MCCB with shunt tripp for incomer and thermal magnetic based MCCBs for out going feeders with rotory handle. The work includes providing required fixing accessories such as grouting bolt-nuts, welding, coupling of laid conduits/ cables and associated civil works complete as directed.Providing and fixing 200A, 35kA, FP MCCB with thermo magnetic release and terminal spreaders. O/G feeder 100A rating, TPN MCCB with thermo Magnetic Release 6Nos, 415 V, 35 kA,suitable for inductive load, including providing and fixing of MS support for panel base size of 75 x 40 x 6 MM 'C' Channel including Cutting, Grinding, welding etc. as required. Details of cost for One Panel | 1.00 | Set |  | 149809.00 | 149809.00 | 250000.00 | 250000.00 | 219300.00 | 219300.00 | 189999.00 | 189999.00 | 216250.00 | 216250.00 | 180636.00 | 180636.00 | 149809.00 | vk sam engineering
16.00 | Supplying and laying of following size of DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc., complete as required. Direct in ground (75 cm below ground level)
17.00 | 63 mm dia (OD-63 mm & ID-51 mm nominal) | 350.00 | Mtrs |  | 180.00 | 63000.00 | 200.00 | 70000.00 | 145.20 | 50820.00 | 120.00 | 42000.00 | 215.00 | 75250.00 | 206.40 | 72240.00 | 42000.00 | DElite System Engineering (India) Pvt. Ltd.
18.00 | 200 mm dia (OD-200 mm & ID-175 mm nominal) | 3000.00 | Mtrs |  | 531.00 | 1593000.00 | 480.00 | 1440000.00 | 427.50 | 1282500.00 | 399.00 | 1197000.00 | 488.00 | 1464000.00 | 521.73 | 1565190.00 | 1197000.00 | DElite System Engineering (India) Pvt. Ltd.
19.00 | Supplying and laying of 125 mm dia (OD-125 mm & ID-76 mm nominal) size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc. complete as required. In the existing trench | 4500.00 | Mtrs |  | 182.00 | 819000.00 | 270.00 | 1215000.00 | 199.50 | 897750.00 | 229.00 | 1030500.00 | 200.00 | 900000.00 | 301.88 | 1358460.00 | 819000.00 | vk sam engineering
20.00 | Laying of following size of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size etc as required. Direct in ground including excavation, sand cushioning, protective covering and refilling the trench.
21.00 | Upto 35 sq. mm | 500.00 | Mtrs |  | 365.00 | 182500.00 | 150.00 | 75000.00 | 205.90 | 102950.00 | 199.00 | 99500.00 | 345.00 | 172500.00 | 339.00 | 169500.00 | 75000.00 | R.K.M. ELECTRICALS
22.00 | Above 35 sq. mm and upto 95 sq. mm | 400.00 | Mtrs |  | 376.00 | 150400.00 | 180.00 | 72000.00 | 230.90 | 92360.00 | 199.00 | 79600.00 | 345.00 | 138000.00 | 418.00 | 167200.00 | 72000.00 | R.K.M. ELECTRICALS
23.00 | Above 95 sq. mm and upto 185 sq. mm | 100.00 | Mtrs |  | 399.00 | 39900.00 | 250.00 | 25000.00 | 255.90 | 25590.00 | 199.00 | 19900.00 | 345.00 | 34500.00 | 452.00 | 45200.00 | 19900.00 | DElite System Engineering (India) Pvt. Ltd.
24.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of size Above 95 sq. mm and upto 185 sq. mm etc as required. On cable tray. | 800.00 | Mtrs |  | 68.00 | 54400.00 | 150.00 | 120000.00 | 80.00 | 64000.00 | 29.00 | 23200.00 | 75.00 | 60000.00 | 126.00 | 100800.00 | 23200.00 | DElite System Engineering (India) Pvt. Ltd.
25.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size etc. as required (In the existing RCC / HUME / METAL pipe.
26.00 | Upto 35 sq. mm | 6000.00 | Mtrs |  | 46.00 | 276000.00 | 135.00 | 810000.00 | 40.00 | 240000.00 | 15.00 | 90000.00 | 58.00 | 348000.00 | 79.00 | 474000.00 | 90000.00 | DElite System Engineering (India) Pvt. Ltd.
27.00 | Above 35 sq.mm and upto 95 sq.mm | 1000.00 | Mtrs |  | 55.00 | 55000.00 | 150.00 | 150000.00 | 60.00 | 60000.00 | 29.00 | 29000.00 | 58.00 | 58000.00 | 106.00 | 106000.00 | 29000.00 | DElite System Engineering (India) Pvt. Ltd.
28.00 | Above 95 sq.mm and upto 185 sq.mm | 100.00 | Mtrs |  | 68.00 | 6800.00 | 200.00 | 20000.00 | 80.00 | 8000.00 | 39.00 | 3900.00 | 58.00 | 5800.00 | 226.00 | 22600.00 | 3900.00 | DElite System Engineering (India) Pvt. Ltd.
29.00 | Cable termination for above cables including the cost of crimping heavy duty tinned aluminum lugs, nickel plated brass double compression glands,ring type earth tags,insulation tape, cable tag & all requisite material for completion of termination as per specification & requirement.
30.00 | End termination (4 Core 16 Sq.mm.) - 1 set | 185.00 | Set |  | 400.00 | 74000.00 | 75.00 | 13875.00 | 399.00 | 73815.00 | 399.00 | 73815.00 | 460.00 | 85100.00 | 668.00 | 123580.00 | 13875.00 | R.K.M. ELECTRICALS
31.00 | End termination (4 Core 25 Sq.mm.) - 1 set | 35.00 | Set |  | 460.00 | 16100.00 | 80.00 | 2800.00 | 449.00 | 15715.00 | 400.00 | 14000.00 | 460.00 | 16100.00 | 811.00 | 28385.00 | 2800.00 | R.K.M. ELECTRICALS
32.00 | End termination (3.5 Core 95 Sq.mm.) - 1 set | 8.00 | Set |  | 1110.00 | 8880.00 | 100.00 | 800.00 | 890.00 | 7120.00 | 700.00 | 5600.00 | 690.00 | 5520.00 | 1713.00 | 13704.00 | 800.00 | R.K.M. ELECTRICALS
33.00 | End termination (3.5 Core 185 Sq.mm) - 1 set | 2.00 | Set |  | 1890.00 | 3780.00 | 150.00 | 300.00 | 2190.00 | 4380.00 | 900.00 | 1800.00 | 920.00 | 1840.00 | 2582.00 | 5164.00 | 300.00 | R.K.M. ELECTRICALS
34.00 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 10.00 | Set |  | 7700.00 | 77000.00 | 11000.00 | 110000.00 | 7175.00 | 71750.00 | 4999.00 | 49990.00 | 11500.00 | 115000.00 | 10050.00 | 100500.00 | 49990.00 | DElite System Engineering (India) Pvt. Ltd.
35.00 | Supplying and laying 25 mm X 5 mm G.I strip at 0.50 metre below ground as strip earth electrode, including connection / terminating with G.I. nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of G.I. nut bolt & spring washer spaced at 50mm) | 100.00 | Mtrs |  | 270.00 | 27000.00 | 200.00 | 20000.00 | 152.01 | 15201.00 | 300.00 | 30000.00 | 259.00 | 25900.00 | 262.00 | 26200.00 | 15201.00 | VISHAL ELECTRICALS
36.00 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing along with existing surface / recessed conduit / submain wiring / cable as required. | 2116.00 | Mtrs |  | 23.00 | 48668.00 | 50.00 | 105800.00 | 22.70 | 48033.20 | 29.00 | 61364.00 | 29.00 | 61364.00 | 41.00 | 86756.00 | 48033.20 | VISHAL ELECTRICALS
37.00 | Constructing masonry Chamber 60x60x75 cm inside, in brick work in cement mortar 1:4 (1 cement : 4 coarse sand) for sluice valve, with C.I. surface box 100mm top diameter, 160 mm bottom diameter and 180 mm deep ( inside) with chained lid and RCC top slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size ) , i/c necessary excavation, foundation concrete 1:5:10 (1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominal size) and inside plastering with cement mortar 1:3 (1 cement : 3 coarse sand) 12 mm thick, finished with a floating coat of neat cement complete as per standard design : 18.33.1 With common burnt clay F.P.S.(non modular) bricks of class designation 7.5 With common burnt clay F.P.S.(non modular) bricks of class designation 7.5 | 26.00 | Nos |  | 7980.00 | 207480.00 | 12000.00 | 312000.00 | 6500.00 | 169000.00 | 9999.00 | 259974.00 | 11500.00 | 299000.00 | 5025.00 | 130650.00 | 130650.00 | Surya Roshni Limited
38.00 | Design and Supply of lowering and raising type high mast tower 25 mtrs, fabricated in two sections, hot dip galvnised, inside & outside in single dip, suitable for wind velocity as per IS 875 part 3, complete in all respects including electrically operated raising and lowering gears, double drum winch, 6 mm dia stainless steel wire rope, lantern carriage, three suspension head frame complete with integral power tool for maintenance, required length of multi core trailing cable between top carriage and base board etc., including supply of foundation bolts manufactured from special steel along with nuts, washers, anchor plates and templates, complete as required and as specified in the particular specifications and of following height. | 5.00 | Nos |  | 364230.00 | 1821150.00 | 470000.00 | 2350000.00 | 310500.00 | 1552500.00 | 469999.00 | 2349995.00 | 332988.00 | 1664940.00 | 316520.00 | 1582600.00 | 1552500.00 | VISHAL ELECTRICALS
39.00 | Supply of 400W LED Flood light luminaires with complete accessories as per latest IS/IEC | 50.00 | Nos |  | 17100.00 | 855000.00 | 19500.00 | 975000.00 | 14375.00 | 718750.00 | 21099.00 | 1054950.00 | 18975.00 | 948750.00 | 11560.00 | 578000.00 | 578000.00 | Surya Roshni Limited
40.00 | Supply of twin dome aviation obstruction lights using LED with other accessories suitable for operation on 230 V single phase supply 50 Hz. | 5.00 | Nos |  | 6954.00 | 34770.00 | 4000.00 | 20000.00 | 6325.00 | 31625.00 | 3000.00 | 15000.00 | 5750.00 | 28750.00 | 3706.00 | 18530.00 | 15000.00 | DElite System Engineering (India) Pvt. Ltd.
41.00 | Erection, testing and commissioning of the above high masts, flood light luminaires, obstruction light luminaires, etc. with the help of suitable equipments and wiring of all luminaires with all wiring materials including all necessary connections and interconnections to achieve required illumination of 30 lux average on , etc. as required including construction of shallow foundation with M25 grade concrete for the high mast considering the safe soil bearing capacity at site as 10 T/sqm at 2 metre depth, etc. as required. | 5.00 | Jobs |  | 143640.00 | 718200.00 | 240000.00 | 1200000.00 | 165000.00 | 825000.00 | 99999.00 | 499995.00 | 201250.00 | 1006250.00 | 157035.00 | 785175.00 | 499995.00 | DElite System Engineering (India) Pvt. Ltd.
42.00 | Supply, installation, testing and commissioning of feeder pillars fabricated from 14 swg CRCA sheet steel including providing and fixing of 63 A TPN MCB as incomer having MCBs, relays, contactors, 24 hrs timers for automatic On/OFF arrangements and control for power tool, etc. as required. | 5.00 | Jobs |  | 29640.00 | 148200.00 | 25000.00 | 125000.00 | 39875.00 | 199375.00 | 21000.00 | 105000.00 | 30791.00 | 153955.00 | 33919.00 | 169595.00 | 105000.00 | DElite System Engineering (India) Pvt. Ltd.
43.00 | Provision of GI pipe earthing for high mast with 2.5 m long 40 mm dia GI pipe inlcuding connection of high mast earth terminal with 25 x 3 mm GI flats, etc. as required. | 5.00 | Jobs |  | 8000.00 | 40000.00 | 6500.00 | 32500.00 | 6525.00 | 32625.00 | 2999.00 | 14995.00 | 4025.00 | 20125.00 | 7538.00 | 37690.00 | 14995.00 | DElite System Engineering (India) Pvt. Ltd.
44.00 | Fabricating, supply, installation of MS barricading in twin rows in horizontal length with 125 mm x 65 xx MS channel including cutting to size as required. The channel shall be grouted in ground with cement concrete of 1:2:4 with suitable plate at the bottom complete as required, as per direction of Engineer-in-Charge including cutting, welding, pinting, etc. | 5.00 | Jobs |  | 37677.00 | 188385.00 | 35000.00 | 175000.00 | 85000.00 | 425000.00 | 26999.00 | 134995.00 | 39000.00 | 195000.00 | 46122.00 | 230610.00 | 134995.00 | DElite System Engineering (India) Pvt. Ltd.
| Total in Figures |  |  |  |  | 17154169.00 |  | 20662375.00 |  | 17255961.20 |  | 16292764.00 |  | 18435492.00 |  | 17691458.00
Lowest Amount Quoted BY: DElite System Engineering (India) Pvt. Ltd.(16292764.00)

## BOQ Summary
BOQ Summary Details Tender Title: Providing Street Light and High mast at Chennai Airport Tender ID: 2022_AAI_110733_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | DElite System Engineering (India) Pvt. Ltd. | 16292764.00 | L1
| 2 | vk sam engineering | 17154169.00 | L2
| 3 | VISHAL ELECTRICALS | 17255961.20 | L3
| 4 | Surya Roshni Limited | 17691458.00 | L4
| 5 | C R ELECTRICALS | 18435492.00 | L5
| 6 | R.K.M. ELECTRICALS | 20662375.00 | L6