## BoQ1
Government eProcurement System Created By: Rahul S Mankar Created Date/Time: 22-Apr-2022 02:47 PM Tender Title: Construction of ASR-MSSR Building at DBAI Airport, Nagpur. SH- Power Supply Work Tender ID: 2022_AAI_110786_1
Tender Inviting Authority: Asstt. Gen. Manager (Engg-Elect), AAI, Nagpur
Name of Work :- Construction of ASR-MSSR Building at DBAI Airport, Nagpur. SH: Power Supply Work.
Contract No: Ref:- AAI/NGP/E-E/2021-22/10/MSSR/NIT-03 Date: 23.03.2022
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Techno Electricals(GSTN-24AAGFT9086M1ZG) |  | Manish Electricals(GSTN-22ABLPM9012E1ZY) |  | M/s V.R. Associates(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply of following solid / stranded Aluminium conductor, XLPE insulated, PVC inner sheathed, armoured power cable of 1.1 kV grade as per IS-7098 (Part 1)-1988 with up to date amendments of approved make & as per technical specifications etc. complete as required.
1.01 | 3.5 core X 240 sq.mm. | 1100.00 | Metre | 1358.00 | 1250.00 | 1375000.00 | 1050.00 | 1155000.00 | 1225.00 | 1347500.00 | 1155000.00 | Manish Electricals
1.02 | 3.5 core X 150 sq.mm. | 260.00 | Metre | 802.00 | 797.00 | 207220.00 | 650.00 | 169000.00 | 750.00 | 195000.00 | 169000.00 | Manish Electricals
2.00 | Supplying and laying of 120 mm size (OD-120 mm & ID-103 mm nominal) DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers, end caps etc. conforming to IS-16205, Part 24 complete with fitting and cutting, jointing etc. direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required. | 1010.00 | Metre | 345.00 | 250.00 | 252500.00 | 250.00 | 252500.00 | 200.00 | 202000.00 | 202000.00 | M/s V.R. Associates
3.00 | Supply and laying 140 mm, PN 6, HDPE PE 63 grade size HDPE pipe using Horizontal Directional Drilling (HDD) method for cable diversion including jointing of HDPE pipe, arrangement & mobilization of all machinery, tools & pit excavation etc. as required. | 80.00 | Metre | 2338.00 | 4000.00 | 320000.00 | 2100.00 | 168000.00 | 3000.00 | 240000.00 | 168000.00 | Manish Electricals
4.00 | Providing, laying and fixing 150 dia G.I. pipe (medium class) in ground complete with G.I. fittings including trenching (75 cm deep) and re-filling etc as required. | 42.00 | Metre | 2542.00 | 1400.00 | 58800.00 | 2100.00 | 88200.00 | 2000.00 | 84000.00 | 58800.00 | Techno Electricals
5.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of Above 185 sq. mm and up to 400 sq. mm size in the existing RCC/ HUME/ METAL/DWC pipe as required. | 1100.00 | Metre | 117.00 | 80.00 | 88000.00 | 40.00 | 44000.00 | 50.00 | 55000.00 | 44000.00 | Manish Electricals
6.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of above 185 sq. mm and up to 400 sq. mm size in the existing masonry open duct as required. | 95.00 | Metre | 334.00 | 80.00 | 7600.00 | 140.00 | 13300.00 | 50.00 | 4750.00 | 4750.00 | M/s V.R. Associates
7.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of above 95 sq. mm and up to 185 sq. mm size in the existing masonry open duct as required. | 200.00 | Metre | 289.00 | 80.00 | 16000.00 | 140.00 | 28000.00 | 50.00 | 10000.00 | 10000.00 | M/s V.R. Associates
8.00 | Supplying and making end termination with brass compression gland and Aluminium lugs for 3.5 core X 240 sq.mm. size of PVC insulated and PVC sheathed / XLPE Aluminium conductor cable of 1.1 KV grade as required. | 8.00 | Nos. | 1125.00 | 1000.00 | 8000.00 | 1200.00 | 9600.00 | 500.00 | 4000.00 | 4000.00 | M/s V.R. Associates
9.00 | Supplying and making end termination with brass compression gland and Aluminium lugs for 3.5 core X 150 sq.mm. size of PVC insulated and PVC sheathed / XLPE Aluminium conductor cable of 1.1 KV grade as required. | 24.00 | Nos. | 696.00 | 850.00 | 20400.00 | 700.00 | 16800.00 | 250.00 | 6000.00 | 6000.00 | M/s V.R. Associates
10.00 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal / coke and salt as required. | 4.00 | Nos. | 6460.00 | 8000.00 | 32000.00 | 7500.00 | 30000.00 | 5000.00 | 20000.00 | 20000.00 | M/s V.R. Associates
11.00 | Earthing with Copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal / coke and salt as required. | 4.00 | Nos. | 18249.00 | 17000.00 | 68000.00 | 19000.00 | 76000.00 | 12500.00 | 50000.00 | 50000.00 | M/s V.R. Associates
12.00 | Providing and fixing 25 mm X 5 mm Copper strip in 40 mm dia G.I. pipe from earth electrode including connection with brass nut, bolt, spring, washer excavation and re-filling etc. as required. | 89.00 | Metre | 2059.00 | 1750.00 | 155750.00 | 1450.00 | 129050.00 | 1500.00 | 133500.00 | 129050.00 | Manish Electricals
13.00 | Providing and fixing 25 mm X 5 mm GI strip in 40 mm dia G.I. pipe from earth electrode including connection with brass nut, bolt, spring, washer excavation and re-filling etc. as required. | 89.00 | Metre | 675.00 | 600.00 | 53400.00 | 750.00 | 66750.00 | 500.00 | 44500.00 | 44500.00 | M/s V.R. Associates
14.00 | Providing and fixing 25 mm X 5 mm Copper strip on surface or in recess for connections etc. as required. | 30.00 | Metre | 1671.00 | 1100.00 | 33000.00 | 1200.00 | 36000.00 | 1000.00 | 30000.00 | 30000.00 | M/s V.R. Associates
15.00 | Providing and fixing 25 mm X 5 mm GI strip on surface or in recess for connections etc. as required. | 35.00 | Metre | 231.00 | 200.00 | 7000.00 | 300.00 | 10500.00 | 100.00 | 3500.00 | 3500.00 | M/s V.R. Associates
16.00 | Extra for excavation of the cable trenches in hard rock / PCC / Bituminous not exceeding 1.5 metres in width, and lift up to 1.5 metres, including getting out the excavated soil and disposal of excavated soil as directed within a lead of 50 metres. | 24.00 | Cum | 705.00 | 800.00 | 19200.00 | 1000.00 | 24000.00 | 500.00 | 12000.00 | 12000.00 | M/s V.R. Associates
17.00 | Providing and laying in position cement concrete of specified grade excluding the cost of centering, shuttering - All work up to plinth level : 1:2:4 (1 cement : 2 coarse sand(zone-III) : 4 graded stone aggregate 20 mm nominal size) | 5.00 | Cum | 5641.00 | 5500.00 | 27500.00 | 7000.00 | 35000.00 | 4906.00 | 24530.00 | 24530.00 | M/s V.R. Associates
18.01 | Supply, Installation, Testing & Commissioning of Silent Type Diesel Generating set along with prime power rating of 180 KVA, 415 Volts at 1500 RPM, 0.8 lagging power factor at 415 V suitable for 50 Hz., 3-Phase system and consisting of the followings: a) Diesel Engine: Radiator cooled Diesel Engine of suitable BHP (not less than 234 BHP) at 1500 RPM after considering derating factors as applicable, 4 Stroke, turbo charged - after / inter cooled with charged air cooling, vacuum indicator, electronic / mechanical governor, electric start, suitable for above output of alternator at 47.7 Deg.C, 30-80% RH & at 306 Metres MSL and conforming to ISO 3046 / IS 10000, capable of taking 10% over loading for one hour after 12 hours of continuous operation. The engine shall be fitted completed with all the required accessories & shall be provided with 1st fill of lube oil and coolant.
18.02 | b) Engine Mounted Control Panel - Fitted with Microprocessor based Genset Controller having digital display & control devices for safety and monitoring along with indicators as below: Start-Stop switch with key, coolant temperature high/low indication, lubrication oil pressure indication, battery charging indication, RPM indication, over speed indication, low lube oil pressure trip indication, engine run hours indication etc. c) Alternator: Synchronous alternator rated at 180 KVA (Minimum), 415 Volts at 1500 RPM, 3-Phase 50 Hz., AC Supply with 0.8 lagging power factor at 47.7 Deg.C, 30-80% RH & at 306 Metres MSL. The alternator shall be having SPDP enclosure, brushless, continuous duty, self-excited and self-regulated through AVR/DVR conforming to IS 4722 / BS 2613 suitable for tropical conditions, with adapter box and with class-H insulation.
18.03 | d) Base Frame: Both the engine and alternator shall be mounted on suitable base frame made of MS channel with necessary reinforcement which shall be installed on cement concrete foundation (Will be provided by AAI) and AVM pads / vibration isolation arrangement to be provided as per recommendations of manufacturer. e) Fuel Tank: Calibrated Day Storage fuel tank of 990 Litres capacity fabricated out of 3 mm thick M. S. sheet complete with suitable MS stand, flanged inlet & outlet, overflow, drain, vent, high & low level indicator, 450 mm dia access hole on top with cover & all standard accessories, fuel piping between fuel tank and diesel engine with MS class 'C' pipes of suitable dia. as required as per specifications. (This tank shall be separate from in-built fuel tank of Genset).
18.04 | f) Exhaust System: Dry exhaust manifold with residential / hospital grade exhaust silencer and catalytic convertor with MS support structure for exhaust piping including rope wrapping insulation and aluminium cladding as required. g) Starting System: 12V/24V DC starting system comprising of starter motors: Voltage regulator and arrangement for initial excitation complete with suitable nos. of batteries complete with leads, charger and battery stand etc. as per the OEM standard and as required as per specifications. h) Acoustic Enclosure: Acoustic and weather proof enclosure complying with CPCB-II norms, with arrangement for fresh air intake for cooling of the engine and alternator, extraction, discharging hot air into the atmosphere as per specifications.
18.05 | Diesel Generator Set - 180 KVA as Above. (18.01 to 18.05) | 1.00 | Set | 1757052.00 | 1450000.00 | 1450000.00 | 1650000.00 | 1650000.00 | 1110000.00 | 1110000.00 | 1110000.00 | M/s V.R. Associates
19.01 | Fabrication, Supply, Installation, Testing and Commissioning of cubicle type, IP-42 indoor AMF LT panel - type tested assembly (TTA) as per IEC 61439-1&2, floor mounting, free standing, suitable for 415V+/-10%, 3 Phase, 4 wire, 50 Hz AC supply system, fabricated in compartmentalized modular design (Form-4B) from CRCA sheet steel of 1.6 mm thick for frame work and covers, 3 mm thick for gland plates i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having 400 A capacity TPN Aluminium alloy bus bars of high conductivity, SMC / DMC bus bar supports, with short circuit withstand capacity of 50 KA for 1 sec, bottom base channel of MS section not less than 100 mm x 50 mm x 5 mm thick, fabrication shall be done in transportable sections, entire panel shall have a common Al. earth bus bar of suitable size at the rear end with 2 Nos. earth stud,
19.02 | solid / flexible connections from main bus bar to switchgears and from switchgear output to cable termination in cable alley with required size of Copper conductors / Aluminium bus bars and control wiring with 2.5 sqmm PVC insulated copper conductor cable (FRLS), cable alleys, cable gland plates in two half, complete with all accessories, interconnection, earthing i/c providing following switchgears / accessories as per specifications.: (AMF LT PANEL - SUITABLE FOR 180 KVA DG SET)
19.03 | a) 320 A, 36 KA, 4 Pole MCCB (Ics = 100% Icu), Microprocessor Based Release with O/C & S/C Protection - 2 Sets.
19.04 | b) 315 / 325 A, 4 Pole Power Contactor with Aux. Contacts - 2 Nos.
19.05 | c) 315 A, 4 Pole Bypass Changeover Switch to bypass Mains / DG supply - 01 No.
19.06 | e) Protection Relays - Over Current + Earth Fault, Over Voltage, Under Voltage (Each - 2 Nos.), Reverse Power (1 No.) with CTs of suitable range - 15VA, CL-5P10 accuracy for protection as applicable.
19.07 | f) LED Indication lamps for RYB (3 Sets), Load on Mains, Load on DG, DC Control ON, Battery Charger ON etc. with 2 Amp MCB for protection.
19.08 | g) Intelligent Digital Multi Function Meter to read V, A, kVA, KW, kVAR, PF, Hz, THD and individual order harmonics up to 31st Order etc. with communication facility (RS-485 port), CL-1.0, LED display - 2 Nos. + Digital Ammeter, RS 485, CL-1.0, with in-built selector switch with 2 Amps MCBs for controlling and protection - 2 Nos. + 3 Nos. CTs, 300/5, 15 VA, Class 1.0 and control circuit wiring with 2 Amps MCBs for controlling and protection.
19.09 | h) Microprocessor Based Advanced AMF Control Logic Relay with Built-In DG Protection - 1 No.
19.10 | i) 12/24 V DC Control Circuit, Voltage Monitoring Relay (2 Nos), Cranking Relay, Engine Starting Relay, Aux. Relays, Timers, Aux. Contactors, Selector Switches, Push Buttons, Emergency Stop Push Button, 2 A Control MCBs as required for control / interlocking / protection & Accessories etc. as required. - 1 Set.
19.11 | j) 24 VDC Battery Charger, complete with transformer / rectifier, DC Voltmeter and DC Ammeter, Selector Switch for Trickle / Off / Boost with current adjustment - 1 Set
19.12 | k) 8 Window Annunciator with Push Button for Test/Accept/Reset + Hooter for indication of High Water Temperature, High/Low Lube Oil Pressure, Engine Overspeed, Engine Fails to Start, Over Current, Under / Over Voltage, Reverse Power & Earth Fault Etc. as required. - 1 Set
19.13 | l) Control Cabling with 10C x 2.5 Sqmm Cu. Arm. Cable between AMF Panel and DG Set Control Unit as required.
19.14 | NOTE: All MCCBs shall be provided with rotary operating handle and spreader terminals.
19.15 | AMF LT PANEL - (SUITABLE FOR 180 KVA DG SET) AS ABOVE - 19.01 to 19.15 | 1.00 | Set | 478105.00 | 350000.00 | 350000.00 | 550000.00 | 550000.00 | 600000.00 | 600000.00 | 350000.00 | Techno Electricals
20.01 | Fabrication, Supply, Installation, Testing and Commissioning of cubicle type, IP-42, indoor LT panel as per IS 8623-Part-1, floor mounting, free standing, suitable for 415V+/-10%, 3 Phase, 4 wire, 50 Hz AC supply system, fabricated in compartmentalized modular design from CRCA sheet steel of 1.6 mm thick for frame work and covers, 3 mm thick for gland plates i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, TPN Aluminium alloy bus bars of high conductivity, extensible on both sides, SMC / DMC bus bar supports, with short circuit withstand capacity of 50 KA for 1 sec, bottom base channel of MS section not less than 100 mm x 50 mm x 5 mm thick, fabrication done in transportable sections, entire panel shall have a common Al. earth bus bar of suitable size, at the rear end with 2 Nos. earth stud,
20.02 | solid / flexible connections from main bus bar to switchgears and from switchgear output to cable termination in cable alley with required size of Copper conductors / Aluminium bus bars and control wiring with 2.5 sqmm PVC insulated copper conductor cable (FRLS), cable alleys, cable gland plates in two half, complete with all accessories, interconnection, interlocking, earthing i/c providing following switchgears / accessories as per specifications.: (ESSENTIAL LT PANEL)
20.03 | A) Incomers & Bus coupler:
20.04 | (a) 250 A, 36 kA, 4 Pole MCCB (Ics = 100% Icu), Microprocessor Based Release with O/C & S/C Protection - 3 Sets (Incomer - 2 Nos. & Bus-Coupler - 1 No.)
20.05 | b) Intelligent Digital Multi Function Meter to read V, A, kVA, KW, kVAR, PF, Hz, THD and individual order harmonics up to 31st Order etc. with communication facility (RS-485 port), CL-1.0, LED display with 03 Nos of CTs, 250/5, 15 VA, Class 1.0 and control circuit wiring with 2 Amps MCBs for controlling and protection. - 2 Sets.
20.06 | c) R, Y, B Phase indicating lamps, LED type, with 2 Amp MCB for protection. - 3 Sets. d) 1 Set of Indication Lamps, LED type for MCCB 'ON' , 'OFF', 'TRIP' with 02 Amps MCB for protection - 3 Sets.
20.07 | e) Auxiliary contacts / contactors, auxiliary relays, shunt trip etc. for positive interlocking of the incomer MCCBs and bus coupler MCCB as required. - 1 Set.
20.08 | B) Main Busbars: TPN, high conductivity Aluminium, both sides extensible type main bus bars of minimum of 300 Amps. capacity with heat shrinkable coloured sleeves and i/c DMC / SMC bus bars cross section supports & their spacing etc. For withstanding fault level of 50 kA capacity for 1 sec. - 1 Set
20.09 | C) Outgoings:
20.10 | (a) 125 A, 36 kA, Four Pole MCCB (Ics = 100% Icu) with O/L and S/C Fault Protection with Adjustable Thermal and Adjustable Magnetic Releases + Digital Ammeter with in-built selector switch, RS 485, CL-1 accuracy & suitable range of cast resin CTs (03 Nos) including connections etc as required. - 2 Sets.
20.11 | (b) 100 A, 36 kA, Four Pole MCCB (Ics = 100% Icu) with O/L and S/C Fault Protection with Adjustable Thermal and Adjustable Magnetic Releases + Digital Ammeter with in-built selector switch, RS 485, CL-1 accuracy & suitable range of cast resin CTs (03 Nos) including connections etc as required. - 6 Sets.
20.12 | (c) 63 A, 36 kA, Four Pole MCCB (Ics = 100% Icu) with O/L and S/C Fault Protection with Adjustable Thermal and Adjustable Magnetic Releases + Digital Ammeter with in-built selector switch, RS 485, CL-1 accuracy & suitable range of cast resin CTs (03 Nos) including connections etc as required. - 2 Sets.
20.13 | NOTE: a) All MCCBs shall be provided with ON, OFF & TRIP indication lamps (LED type) with 2 Amp SP MCB for protection. b) All MCCBs shall be provided with rotary operating handle and spreader terminals.
20.14 | ESSENTIAL LT PANEL AS ABOVE - 20.01 to 20.14 | 1.00 | Set | 330331.00 | 450000.00 | 450000.00 | 440000.00 | 440000.00 | 400000.00 | 400000.00 | 400000.00 | M/s V.R. Associates
21.01 | Fabrication, Supply, Installation, Testing and Commissioning of cubicle type, IP-42, indoor LT panel - type tested assembly (TTA) as per IEC 61439-1&2, floor mounting, free standing, suitable for 415V+/-10%, 3 Phase, 4 wire, 50 Hz AC supply system, fabricated in compartmentalized modular design (Form-4B) from CRCA sheet steel of 1.6 mm thick for frame work and covers, 3 mm thick for gland plates i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, TPN Aluminium alloy bus bars of high conductivity, extensible on both sides, SMC / DMC bus bar supports, with short circuit withstand capacity of 50 KA for 1 sec, bottom base channel of MS section not less than 100 mm x 50 mm x 5 mm thick, fabrication done in transportable sections, entire panel shall have a common Al. earth bus bar of suitable size, at the rear end with 2 Nos. earth stud,
21.02 | solid / flexible connections from main bus bar to switchgears and from switchgear output to cable termination in cable alley with required size of Copper conductors / Aluminium bus bars and control wiring with 2.5 sqmm PVC insulated copper conductor cable (FRLS), cable alleys, cable gland plates in two half, complete with all accessories, interconnection, interlocking, earthing i/c providing following switchgears / accessories as per specifications.: (NON-ESSENTIAL LT PANEL)
21.03 | A) Incomers & Bus coupler:
21.04 | (a) 400 A, 36 kA, Four Pole MCCB (Ics = 100% Icu), Microprocessor Based Release with O/L & S/C Protection - 3 Sets (Incomer - 2 Nos. & Bus-Coupler - 1 No.)
21.05 | b) Intelligent Digital Multi Function Meter to read V, A, kVA, KW, kVAR, PF, Hz, THD and individual order harmonics up to 31st Order etc. with communication facility (RS-485 port), CL-1.0, LED display with 03 Nos of CTs, 400/5, 15 VA, Class 1.0 and control circuit wiring with 2 Amps MCBs for controlling and protection. - 2 Sets.
21.06 | c) R, Y, B Phase indicating lamps, LED type, with 2 Amp MCB for protection. - 3 Sets. d) 1 Set of Indication Lamps, LED type for MCCB 'ON' , 'OFF', 'TRIP' with 02 Amps MCB for protection - 3 Sets.
21.07 | d) Auxiliary contacts / contactors, auxiliary relays, shunt trip etc. for positive interlocking of the incomer MCCBs and bus coupler MCCB as required. - 1 Set.
21.08 | (e) 3 Phase 4 Wire kWh Meter, CT op base mounting, Class accuracy 0.5s (Neptune or similar) with 03 Nos of CTs, 400/5, 15 VA, Class 1.0 - 2 Sets.
21.09 | f) Surge Protection Device - Type 1+2, 3 Pole + NPE, Imax = 50 kA, Modular Type, conforming to EN/IEC 61643-11 with 32A, FP C-Series MCB including complete connection with copper flexible cable and as per technical specifications. (OBO - V50-3+NPE-320 / L&T AUSP123PN50 or similar) - 2 Sets
21.10 | B) Main Busbars: TPN, high conductivity Aluminium, both sides extensible type main bus bars of minimum of 400 Amps. capacity with heat shrinkable coloured sleeves and i/c DMC / SMC bus bars cross section supports & their spacing etc. For withstanding fault level of 50 kA capacity for 1 sec. - 1 Set
21.11 | C) Outgoings:
21.12 | (a) 250 A, 36 kA, 4 Pole MCCB (Ics = 100% Icu), Microprocessor Based Release with O/C & S/C Protection + Digital Ammeter with in-built selector switch, RS 485, CL-1 accuracy & suitable range of cast resin CTs (03 Nos) including connections etc as required. - 2 Sets.
21.13 | (b) 100 A, 36 kA, Four Pole MCCB (Ics = 100% Icu) with O/L and S/C Fault Protection with Adjustable Thermal and Adjustable Magnetic Releases + Digital Ammeter with in-built selector switch, RS 485, CL-1 accuracy & suitable range of cast resin CTs (03 Nos) including connections etc as required. - 2 Sets.
21.14 | NOTE: a) All MCCBs shall be provided with ON, OFF & TRIP indication lamps (LED type) with 2 Amp SP MCB for protection. b) All MCCBs shall be provided with rotary operating handle and spreader terminals.
21.15 | NON-ESSENTIAL LT PANEL AS ABOVE - 21.01 to 21.15 | 1.00 | Set | 392856.00 | 500000.00 | 500000.00 | 475000.00 | 475000.00 | 475000.00 | 475000.00 | 475000.00 | M/s V.R. Associates, Manish Electricals
22.00 | Supply & Installation of 8 mm dia Aluminium Alloy Round Conductor for air termination network & down conductor system meeting the requirements of IS/IEC 62305 and IEC 62561 complete as per technical specifications as required. (OBO Type No. RD 8/ALU-I (5450 08 6) / CAPE Type SRC 8-AL (400 008) or Similar) | 210.00 | Metre | 206.00 | 500.00 | 105000.00 | 180.00 | 37800.00 | 115.00 | 24150.00 | 24150.00 | M/s V.R. Associates
23.00 | Providing & fixing cross connector for T and cross connection, to route vertical down conductor / mesh formation, made of hot dipped Galvanised Iron / Stainless Steel with necessary bolts and nuts etc. meeting the requirements of IS/IEC 62305 and IEC 62561 complete as per technical specifications as required. (OBO Type No.251 8-10 (5312 03 5) / CAPE Type: CCSS 8-10 (400 206) or Similar) | 13.00 | Nos. | 405.00 | 650.00 | 8450.00 | 400.00 | 5200.00 | 235.00 | 3055.00 | 3055.00 | M/s V.R. Associates
24.00 | Providing & fixing of roof conductor holder for tiled / slated / corrugated roof sheet, suitable for 8 mm dia round conductor, made up of UV resistant Nylon / PU / Polyamide complete as per technical specifications as required. (OBO Type No. 159 K-VA (5216 81 8) / or Similar) | 40.00 | Nos. | 268.00 | 750.00 | 30000.00 | 300.00 | 12000.00 | 150.00 | 6000.00 | 6000.00 | M/s V.R. Associates
25.00 | Providing & fixing of roof conductor holder for parapet wall, suitable for 8 mm dia round conductor, made up of UV resistant Nylon / PU / Polyamide complete as per technical specifications as required. (OBO Type No. 177 30 M8 (5207 46 0) / CAPE Type PCH 8 (400 202) or Similar) | 167.00 | Nos. | 71.00 | 400.00 | 66800.00 | 80.00 | 13360.00 | 45.00 | 7515.00 | 7515.00 | M/s V.R. Associates
26.00 | Providing & fixing of roof conductor holder for flat roof, suitable for 8 mm dia round conductor, made up of UV resistant Nylon / PU / Polyamide with concrete block / filling complete as per technical specifications as required. (OBO Type No. 165 MBG-8 (5218 70 0) / CAPE Type MBPCH 8 (403 201)or Similar) | 3.00 | Nos. | 277.00 | 300.00 | 900.00 | 250.00 | 750.00 | 175.00 | 525.00 | 525.00 | M/s V.R. Associates
27.00 | Providing & fixing of expansion piece including connectors (2 nos / expansion piece) for equalising temperature related length changes, suitable for 8 mm dia round conductor, meeting the requirements of IS/IEC 62305 and IEC 62561 complete as per technical specifications as required. (OBO Type No. 172 AR ( 5218 92 6 ) + 249 8-10 ST (5311 50 0) / CAPE Type EPC 8 (401 209) + CJ 8 (401 211) or Similar) | 3.00 | Set | 962.00 | 1000.00 | 3000.00 | 1000.00 | 3000.00 | 575.00 | 1725.00 | 1725.00 | M/s V.R. Associates
28.00 | Providing & fixing 16 Sqmm flexible bridging Copper cable with UV stabilized chlorinated natural rubber mixture coating, Aluminium lugs, suitable for indoor & outdoor application, installed to make continuity at air terminals including providing & fixing 8 mm clamping shoe (2 Nos.) complete as per technical specifications as required. (OBO Type No. 853 300 (5331 01 3) with 319 8 Clamping Shoe, 8 mm (5325 307) or similar) | 1.00 | Set | 2319.00 | 10000.00 | 10000.00 | 2500.00 | 2500.00 | 1500.00 | 1500.00 | 1500.00 | M/s V.R. Associates
29.00 | Supply & Installation of 1 metre long, 10 mm dia Aluminium vertical air termination rod along with mounting accessories to install on the flat surface, meeting the requirements of IS/IEC 62305 and IEC 62561 complete as per technical specifications as required. (OBO Type No. F-FIX-JUNIOR (5403 30 8) or / CAPE Type VAT 1 (400 410) or similar) | 1.00 | Nos. | 1615.00 | 2000.00 | 2000.00 | 1500.00 | 1500.00 | 1000.00 | 1000.00 | 1000.00 | M/s V.R. Associates
30.00 | Providing & fixing of Test Joint (Folding Clamp), suitable to connect 8 mm round conductor and 50 X 5 mm GI strip, made up of Cu. / Stainless steel / Galvanized Iron, meeting the requirements of IS/IEC 62305 and IEC 62561 complete as per technical specifications as required. (OBO Type No. 271 8-10 VA (5317 48 1) or Similar) | 6.00 | Nos. | 1539.00 | 3000.00 | 18000.00 | 1500.00 | 9000.00 | 1000.00 | 6000.00 | 6000.00 | M/s V.R. Associates
31.00 | Supply & Installation of hot dipped galvanised steel flat strip of 25 x 6 mm thickness with Zinc coating (500 Gms /Sqm or 70 microns) for ring equipotential bonding and connecting earthing system with down conductor system meeting the requirements of IS/IEC 62305 and IEC 62561 complete as per technical specifications as required. (OBO Type No. 5052 25x6 GI (5450 43 1) or Similar) | 140.00 | Metre | 534.00 | 300.00 | 42000.00 | 500.00 | 70000.00 | 290.00 | 40600.00 | 40600.00 | M/s V.R. Associates
32.00 | Providing & fixing of Cross connector for flat strip, suitable for 30 mm Galvanised steel strip, made up of Stainless steel / Galvanized Iron, with 4 Nos. of hexagonal bolts complete as per technical specifications as required. (OBO Type No. 255 FL30 FT (5314 53 4) or Similar) | 20.00 | Nos. | 366.00 | 1000.00 | 20000.00 | 400.00 | 8000.00 | 205.00 | 4100.00 | 4100.00 | M/s V.R. Associates
33.00 | Supply & Installation of UL Listed, maintenance free earthing, comprising: (1) 17.2 mm dia low carbon copper bonded steel earth electrode of 3 metre length with copper coating thickness of 250 microns (OBO Type No. 17 3000 CCER (5450 01 4) or Similar) (2) Universal clamp made up of stainless steel to connect earth rod with flat conductor (OBO Type No. 17 25 RTC (5450 06 8) or Similar) (3) Earth conductivity enhancing mineral compound tested for leaching & TCLP - 25 Kg (OBO Type No. OEC 2 25 (5450 05 8) or Similar) (4) Heavy duty earth chamber / inspection pit (OBO Type No. UFE (5450 03 0) or Similar) All materials as above meeting the requirements of IS/IEC 62305 and IEC 62561 complete as per technical specifications as required. | 6.00 | Set | 15057.00 | 45000.00 | 270000.00 | 14000.00 | 84000.00 | 8000.00 | 48000.00 | 48000.00 | M/s V.R. Associates
34.01 | Supply, installation, testing and commissioning outdoor feeder pillar box of minimum size 450 X 450 X 300 mm depth, suitable for operation on 415V, 3 phase, 4 wire 50Hz AC supply system, fabricated in totally enclosed, free standing, non-extensible, IP-65 rated design from CRCA sheet steel of 2 mm thick for frame work and covers, 3 mm thick for gland plates, complete with 50 kA for 1 Sec rated 200 Amps current capacity Aluminium Bus-bars, hinged front & back door opening & locking arrangement, painted/powder coated with one coat of red oxide & two coats of enamel paint, suitable openings at the bottom for cable entries, earthing bolts etc.
34.02 | The box shall be mounted on MS angle stand to be grouted in 1:2:4 concrete of 100 X 100 X 300 mm depth, providing & laying in position cement concrete (PCC) of specified grade around the feeder panel boxes (PCC Size 1Mtr X 1 Mtr X 0.25 Mtr) (1:2:4) (1 cement: 2 coarse sand: 4 graded stone aggregate 40mm nominal size) with Suitable HDPE pipe for cable in & out to the boxes, etc. as per technical specifications as required.
34.03 | FEEDER PILLAR AS ABOVE - 34.01 to 34.03 | 2.00 | Job | 8351.00 | 7000.00 | 14000.00 | 9000.00 | 18000.00 | 10000.00 | 20000.00 | 14000.00 | Techno Electricals
35.00 | Supply of nominal 2.0 mm +/- 10 % thick electrically insulated synthetic mat confirming to IS 15652:2006 & suitable for all voltages up to 3.3 KV etc. complete as required. | 30.00 | Sqm | 557.00 | 1250.00 | 37500.00 | 700.00 | 21000.00 | 475.00 | 14250.00 | 14250.00 | M/s V.R. Associates
36.00 | ITC of nominal 2.0 +/- 10 % thick electrically insulated synthetic mat along with suitable adhesive / chemibound / PU resin, sealing material etc. as required. | 30.00 | Sqm | 266.00 | 200.00 | 6000.00 | 150.00 | 4500.00 | 100.00 | 3000.00 | 3000.00 | M/s V.R. Associates
37.00 | SITC of 1.5 HP, 18 Stages, Borewell Submersible Pump Set with single phase starter, 25 mm HDPE pipe (53 Metres), 10 mm Nylon Rope (60 Metres), 25 mm SS Nipple (2 Nos), 25 mm SS Bolt (2 Nos), 25mm GI Bend, GI Socket, Hose Nipple, 32 mm x 25 mm Reducer, 3 Core X 2.5 Sq.mm. Cu. flat cable (70 Metres) and Bore Cap etc. complete as required. (KSB - Cora 50/18 ELX or Similar) | 1.00 | Job | 34977.00 | 12000.00 | 12000.00 | 28000.00 | 28000.00 | 40000.00 | 40000.00 | 12000.00 | Techno Electricals
38.00 | Supply & Installation of 12 V, 900 VA Pure Sine Wave Inverter, micro-controller based design, LED display indications, overload and short circuit protection, multi stage battery charger with battery state monitoring, suitable for input voltage range of 180 - 260 VAC etc. complete as required. (Microtek Model 900 (12) SW or similar) | 1.00 | Each | 4971.00 | 75000.00 | 75000.00 | 4500.00 | 4500.00 | 7500.00 | 7500.00 | 4500.00 | Manish Electricals
39.00 | Supply of 12 V, 150 AH Battery suitable for UPS etc. as required. (Make: Exide/ Model Inva King IK5000 or similar) | 1.00 | Each | 10540.00 | 18000.00 | 18000.00 | 12000.00 | 12000.00 | 15000.00 | 15000.00 | 12000.00 | Manish Electricals
| Total in Figures |  |  |  |  | 6238020.00 |  | 5801810.00 |  | 5295200.00
Lowest Amount Quoted BY: M/s V.R. Associates(5295200.00)

## BOQ Summary
BOQ Summary Details Tender Title: Construction of ASR-MSSR Building at DBAI Airport, Nagpur. SH- Power Supply Work Tender ID: 2022_AAI_110786_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | M/s V.R. Associates | 5295200.00 | L1
| 2 | Manish Electricals | 5801810.00 | L2
| 3 | Techno Electricals | 6238020.00 | L3