## BoQ1
Government eProcurement System Created By: VETRISELVI JAGADEESAN Created Date/Time: 27-Apr-2022 05:27 PM Tender Title: REPLACEMENT OF EXISTING 6X10TR PACKAGE AC WITH VRF SYSTEM IN DEPARTURE HALL AT IMPHAL AIRPORT Tender ID: 2022_AAI_111173_1
Tender Inviting Authority: Asst. General Manager (Engg.-Elect.), AAI, Imphal Airport.
Name of Work: REPLACEMENT OF EXISTING 6X10TR PACKAGE AC WITH VRF SYSTEM IN DEPARTURE HALL AT IMPHAL AIRPORT
Contract No: 2022_AAI_111173_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | CAC ENGINEERS PVT LTD(GSTN-33AAECC2301D2ZK) |  | VOLKS ENERGIE PVT LTD(GSTN-07AADCV9396C1ZZ) |  | RS COOLING APPLIANCES(GSTN-18AALFR2502H3Z8)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply, Installation, Testing and Commissioning of Modular Type Variable Refrigerant Flow Outdoor Units with hermatically sealed inverter type Scroll Compressor with BLDC motor suitable to operate on 415 V ± 10%, 50 Hz, 3 Phase AC Supply, heat exchanger/condenser coil, heating & cooling, microprocessor based controller, low noise condenser fan, auto check function for connection error, auto address setting and minimum capacity as mentioned below. All outdoor unit should have stepless modulation, Top discharge type condensing units with R410 A refrigerant including full charge of refrigerant gas and oil for commissioning the entire system, vibration isolators with fixing in the existing angle iron frame work, capable of delivering 100% capacity at 40 Deg C ambient and COP not less than 3.8 & 6.0 at 100% & 50% load condition respectively for cooling conforming to AHRI Standards and Conditions, etc., as required.
1.01 | 12.0 HP | 6.00 | Jobs |  | 262017.60 | 1572105.60 | 300000.00 | 1800000.00 | 365000.00 | 2190000.00 | 1572105.60 | CAC ENGINEERS PVT LTD
2.00 | Supply, Installation, Testing and Commissioning of DX double skin Air Handling Unit of Floor Mounted Vertical type with 0.6 mm pre coated GI outer skin and 0.6 mm GI inner skin with 48 ± 2 mm thick PUF insulation of density of 40 ± 2 kg/m3 complete with DIDW centrifugal Forward curved fan, fan motor with V-belt & Motor (IE-3) suitable to operate on 415 V ± 10%, 50 Hz, 3 Phase AC Supply, 6 row deep DX cooling coil, MERV-8 & MERV-10 filter section, with fire retardant canvass connection between AHU and supply Air duct, thermal break profile, vibration isolator pad, AHU Kit for connecting the Outdoor unit as per the VRF OEM Standard, Expansion Kit, communication Kit suitable for individually remote controllable and compatible for centralised contol, providing and fixing of suitable Starter Panel with indicating lights and auto selector switch for the AHU along with Neccessary power and control cabling upto 15M (Power and control cables shall be minimum 4 C x 10 sqmm copper conductor Cable & 2 core x 1.5 sqmm copper conductor Cable respectively) , earthing, termination of Power and Control Cable etc., as required.
2.10 | Minimum 4000 CFM | 6.00 | Jobs |  | 165000.00 | 990000.00 | 317400.00 | 1904400.00 | 325000.00 | 1950000.00 | 990000.00 | CAC ENGINEERS PVT LTD
3.00 | Supply, Installation, Testing and Commissioning of following nominal sizes of soft/hard drawn copper refrigerant piping for VRF System with necessary jointng/brazing including, insulated with nitrile rubber, tubular sleeve sections of specified thickness as below for Suction and Liquid lines i/c providing and fixing of all accessories, vaccumization and Nitrogen testing etc., complete i/c fixing arrangements of all sizes of copper tubes on the existing GI tray.
3.10 | 1/2" dia (OD) (soft drawn) with tube thickness 1.2 mm with 19mm thick insulation or as per OEM standard. | 54.00 | Meter |  | 400.00 | 21600.00 | 500.00 | 27000.00 | 325.00 | 17550.00 | 17550.00 | RS COOLING APPLIANCES
3.20 | 1 1/8" dia (OD) (Hard drawn) with tube thickness 1.2 mm with 19mm thick insulation or as per OEM standard. | 54.00 | Meter | 10.00 | 920.00 | 49680.00 | 1300.00 | 70200.00 | 1050.00 | 56700.00 | 49680.00 | CAC ENGINEERS PVT LTD
4.00 | Supply, Installation, Testing and Commissioning of following nominal sizes of soft/hard drawn copper refrigerant piping for VRF System with necessary jointng/brazing including, insulated with nitrile rubber, tubular sleeve sections of specified thickness as below for Suction and Liquid lines i/c providing and fixing of all accessories, vaccumization and Nitrogen testing etc.,including fixing Arragements for the following copper tubes on the Wall including providing and fixing necessary supports etc., complete as required.
4.10 | 1/2" dia (OD) (soft drawn) with tube thickness 1.2 mm with 19mm thick insulation or as per OEM standard. | 45.00 | Meter |  | 400.00 | 18000.00 | 500.00 | 22500.00 | 325.00 | 14625.00 | 14625.00 | RS COOLING APPLIANCES
4.20 | 1 1/8" dia (OD) (Hard drawn) with tube thickness 1.2 mm with 19mm thick insulation or as per OEM standard. | 45.00 | Meter |  | 920.00 | 41400.00 | 1300.00 | 58500.00 | 1050.00 | 47250.00 | 41400.00 | CAC ENGINEERS PVT LTD
5.00 | Supply, Installation, balancing and Commissioning of fabricated at site GSS sheet metal rectangular/round ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports etc., as per approved drawings and specifications of following sheet thickness including alignment, matching and fixing with existing ducting arragements etc., complete as required.
5.10 | 18 SWG | 6.00 | Sqm |  | 800.00 | 4800.00 | 1400.00 | 8400.00 | 650.00 | 3900.00 | 3900.00 | RS COOLING APPLIANCES
5.20 | 22 SWG | 6.00 | Sqm |  | 700.00 | 4200.00 | 1100.00 | 6600.00 | 620.00 | 3720.00 | 3720.00 | RS COOLING APPLIANCES
5.30 | 24 SWG | 6.00 | Sqm |  | 600.00 | 3600.00 | 950.00 | 5700.00 | 580.00 | 3480.00 | 3480.00 | RS COOLING APPLIANCES
6.00 | Supply, installation, testing and commissioning of duct mounted hand lever operated 18 Ga GI volume control damper, locking devices etc. complete as required as per specifications | 3.24 | Sqm |  | 5250.00 | 17010.00 | 10000.00 | 32400.00 | 5000.00 | 16200.00 | 16200.00 | RS COOLING APPLIANCES
7.00 | Supply and fixing of acoustic lining of supply air duct and plenum with 25 mm thick resin bonded glass wool having density of 32 kg/m³, with 25 mm X 25 mm GI section of 1.25 mm thick, at 600 mm centre to centre covered with Reinforced Plastic tissue paper and 0.5 mm thick perforated aluminum sheet fixed to inside surface of ducts with cadmium plated nuts, bolts, stick pins, CPRX compound etc. complete as required. | 12.00 | Sqm |  | 400.00 | 4800.00 | 900.00 | 10800.00 | 300.00 | 3600.00 | 3600.00 | RS COOLING APPLIANCES
8.00 | Supplying and fixing of 19mm thickness duly laminated aluminum foil of mat finish closed cell Nitrile rubber (Class "O") insulation on existing duct after applying suitable adhesive for Nitrile rubber. The joints shall be sealed with 50 mm wide and 3 mm thick self adhesive nitrile rubber tape insulation complete as per specifications and as required. | 12.00 | Sqm |  | 250.00 | 3000.00 | 800.00 | 9600.00 | 320.00 | 3840.00 | 3000.00 | CAC ENGINEERS PVT LTD
9.00 | Supplying, Fixing, Testing and Commissioning of Fire Dampers made of 16 SWG GSS in supply air duct/main branch and return air path as and where required of required sizes i/c control wiring,the damper shall be motorized and spring return so as to close the damper in the event of power failure automatically and open the same in case of power being restored. The spring return action shall be inbuilt mechanism and not externally mounted. The damper shall also be closed in the event of fire signal complete as required and as per specifications.
9.10 | Fire Dampers | 3.00 | Sqm |  | 6500.00 | 19500.00 | 10000.00 | 30000.00 | 5000.00 | 15000.00 | 15000.00 | RS COOLING APPLIANCES
9.20 | Actuator | 6.00 | Nos |  | 7500.00 | 45000.00 | 7500.00 | 45000.00 | 5000.00 | 30000.00 | 30000.00 | RS COOLING APPLIANCES
10.00 | Supply and Fixing of 40 mm dia rigid UPVC pipe conforming to IS 4985-2000 with 6 mm nitrile rubber Insulation complete with fittings, supports etc., for drain piping as required . | 66.00 | Meter |  | 100.00 | 6600.00 | 400.00 | 26400.00 | 105.00 | 6930.00 | 6600.00 | CAC ENGINEERS PVT LTD
11.00 | Dismantling of existing 10 TR indoor and out door AC units i/c partial dismantling of the existing MS Spport frame and its accessories, dismantling of associated items like MV Panel, starter panel/copper pipes/power and control cables / trays / dampers / supports etc. i/c shifting and hand over to AAI Store as required | 6.00 | Jobs | 10.00 | 100.00 | 600.00 | 5000.00 | 30000.00 | 5000.00 | 30000.00 | 600.00 | CAC ENGINEERS PVT LTD
12.00 | Supplying and installing 300 mm X 62.5 mm X 2 mm perforated hot dip Galvanised cable trays with perforation not more than 17.5 %, in convenient sections, joined with connectors, fixed on wall/floor/surface with necessary fixing accessories for running refrigerant piping and cable alongwith control wiring etc., complete as required. | 52.00 | Meter | 10.00 | 550.00 | 28600.00 | 800.00 | 41600.00 | 600.00 | 31200.00 | 28600.00 | CAC ENGINEERS PVT LTD
13.00 | Supply and fixing of 25 mm dia UPVC pipe along with accessories in surface / recess for laying of control cable as required.s required. | 66.00 | Meter | 10.00 | 100.00 | 6600.00 | 250.00 | 16500.00 | 115.00 | 7590.00 | 6600.00 | CAC ENGINEERS PVT LTD
14.00 | Supply and drawing Additional Quantity of (beyond 15m ) 2 core x 1.5 sqmm armoured copper conductor FRLS Cable as per IS7098(Part 1)1988 in the existing Conduits etc, complete as required. | 66.00 | Meter |  | 100.00 | 6600.00 | 100.00 | 6600.00 | 130.00 | 8580.00 | 6600.00 | CAC ENGINEERS PVT LTD, VOLKS ENERGIE PVT LTD
15.00 | Supply and laying Additional Quantity (beyond 15m ) 4 C x 10 sqmm XLPE insulated and PVC sheathed armoured copper conductor Cable as per IS7098(Part 1)1988 cable of 1.1 KV grade in the existing cable tray etc., complete as required. | 144.00 | Meter |  | 425.00 | 61200.00 | 550.00 | 79200.00 | 390.00 | 56160.00 | 56160.00 | RS COOLING APPLIANCES
16.00 | Supplying and making end termination with brass compression gland and Copper lugs for 4 C x 10 sqmm XLPE insulated and PVC sheathed copper conductor armoured cable of 1.1 KV grade etc., complete as required. | 24.00 | Set |  | 750.00 | 18000.00 | 400.00 | 9600.00 | 450.00 | 10800.00 | 9600.00 | VOLKS ENERGIE PVT LTD
17.00 | Providing and fixing 6 SWG dia GI wire on surface or in recess for loop earthing for conductor earth electrode, including connection/ termination with GI thimble etc. as required. | 402.00 | Meter |  | 50.00 | 20100.00 | 20.00 | 8040.00 | 35.00 | 14070.00 | 8040.00 | VOLKS ENERGIE PVT LTD
18.00 | Providing, fabricating and fixing of 50 mm X 50 mm x 5 mm M.S. angle support for positioning O/D units i/c grouting , welding, fixing clamps, bolts, nuts and washers and painting with primer and finish paint etc. Complete as required. | 180.00 | Kg |  | 95.00 | 17100.00 | 150.00 | 27000.00 | 60.00 | 10800.00 | 10800.00 | RS COOLING APPLIANCES
19.00 | Providing and fixing of 14SWG GSS sheet cover for existing perforated refrigeant pipe /cable tray i/c welding, fixing clamps, bolts, nuts and washers etc. Complete as per site requirement. | 12.60 | Sqm |  | 550.00 | 6930.00 | 1000.00 | 12600.00 | 440.00 | 5544.00 | 5544.00 | RS COOLING APPLIANCES
20.00 | Fabrication, S.I.T.C of Indoor MV Panel made out of 2mm thick CRCA sheet, dust tight, vermin proof, totally enclosed, cubicle type, floor mounting, free standing, suitable for operation at 433 V, 3 phase, 4 wire, 50 Hz, A.C. Power Supply System complete with all accessories, interconnection, connection, earthing, painting, grouting, providing pedastal UPTO THE HEIGHT OF 100 mm, Top side Cable Entry provision etc. as required and comprising of following: 1.1 One No. of 400 A, 50 KA, 4P MCCB with Microprocessor Based Release for OC/SC/EF Protection as INCOMER with CT operated MFM of Conserve Make Model EM6400 or equivalent, with ON/OFF/TRIP Indication Lamps and Phase Indication Lamps as required. 1.2 12 Nos. of 63 A, 36 KA, 4P MCCB with Thermal Magnetic Releases for Protection as Outgoing, ON/OFF/TRIP Indication Lamps as required. 1.3 One set of 600A Al. bus bars with at par neutral bus bar as required. 1.4 All accessories such as fuses, auxillary contactors, auxillary switches, etc. including providing Empty Cubicle Space (2 Nos.) suitable for 63A 4P MCCB as required. ALL AS ABOVE1.1 To 1.4 | 1.00 | Job |  | 295000.00 | 295000.00 | 250000.00 | 250000.00 | 460000.00 | 460000.00 | 250000.00 | VOLKS ENERGIE PVT LTD
| Total in Figures |  |  |  |  | 3262025.60 |  | 4538640.00 |  | 4997539.00
Lowest Amount Quoted BY: CAC ENGINEERS PVT LTD(3262025.60)

## BOQ Summary
BOQ Summary Details Tender Title: REPLACEMENT OF EXISTING 6X10TR PACKAGE AC WITH VRF SYSTEM IN DEPARTURE HALL AT IMPHAL AIRPORT Tender ID: 2022_AAI_111173_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | CAC ENGINEERS PVT LTD | 3262025.60 | L1
| 2 | VOLKS ENERGIE PVT LTD | 4538640.00 | L2
| 3 | RS COOLING APPLIANCES | 4997539.00 | L3