## BoQ1
Government eProcurement System Created By: UMESH CHAURASIA Created Date/Time: 09-May-2022 05:55 PM Tender Title: Construction of Domestic Air Cargo Terminal Building and associated works at Raja Bhoj Airport, Bhopal. SH - Provision of Power Supply, Fire Fighting and allied works. Tender ID: 2022_AAI_112216_1
Tender Inviting Authority: SM(E-E), AAI, R.B. Airport, Bhopal
Name of Work: Construction of Domestic Air Cargo Terminal Building and associated works at Raja Bhoj Airport, Bhopal. SH: Provision of Power Supply, Fire Fighting and allied works.
Contract No: AAI/BPL/ENGG(E)/NIT-02/2022-23
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Techno Electricals(GSTN-24AAGFT9086M1ZG) |  | surbhi association(GSTN-23AGKPD2522N1ZK)
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply of Following Size. XLPE insulated, PVC sheathed Al. conductor armoured power cable of 1.1 KV grade conforming to IS:7098 Part-I with upto date amendment etc. complete as required. 3.5 core x 240 sq.mm. | 750.00 | Mtr |  | 1200.00 | 900000.00 | 1390.00 | 1042500.00 | 900000.00 | Techno Electricals
2.00 | Supply and Laying of following size DWC HDPE pipe ISI marked along with all acessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc. in the existing trench, complete as required. 120 mm dia (OD-120 mm & ID-103 mm nominal) | 620.00 | Mtr |  | 240.00 | 148800.00 | 150.00 | 93000.00 | 93000.00 | surbhi association
3.00 | Providing and Fixing of 100 mm dia (medium class) G. I. pipes i/c digging work of 0.5 meter depth & 0.3 meter width for the road crossing & filling the surface with 1:3:6 PCC of 1 feet width and 4 inches deep complete as required. | 40.00 | Mtr |  | 1400.00 | 56000.00 | 1350.00 | 54000.00 | 54000.00 | surbhi association
4.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL/PVC pipe as required Above 185 sq. mm and upto 400 sq. mm | 660.00 | Mtr |  | 65.00 | 42900.00 | 50.00 | 33000.00 | 33000.00 | surbhi association
5.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required. Above 185 sq. mm and upto 400 sq. mm | 60.00 | Mtr |  | 65.00 | 3900.00 | 40.00 | 2400.00 | 2400.00 | surbhi association
6.00 | Laying and fixing of one number PVC insulated and PVC sheathed XLPE power cable of 1.1 kV grade of following size on cable tray/surface etc as required. Above 185 sq. mm and upto 400 sq. mm (clamped with 40x3mm MS flat clamp) | 30.00 | Mtr |  | 100.00 | 3000.00 | 60.00 | 1800.00 | 1800.00 | surbhi association
7.00 | Supplying and making end termination with brass compression gland and aluminum lugs for following size of XLPE insulated and PVC sheathed aluminum conductor cable of 1.1 KV grade as required 3.5 core x 240 Sq.mm (62 mm) | 4.00 | Set |  | 1000.00 | 4000.00 | 800.00 | 3200.00 | 3200.00 | surbhi association
8.00 | Construction of cable chamber of inner size 900mm(L) x900mm(W) x900mm(D) which includes excavation and disposal of excavated in all kinds of soil earth lead upto 50 m and providing & laying of 100 mm cement concrete of 1:4:8 (1 Cement : 4 coarse sand : 8 graded stone aggregate 40 mm nominal size) grade at the bottom of the chamber and Brick work with common burnt clay bricks at foundation and plinth in Cement mortar 1:4 (1 cement : 4 coarse sand) with 12 mm cement plaster finished with neat cement of mix 1:3 (1 cement: 3 fine sand). Chamber shall be provided with cover of chamber size chequer plate of 8mm thick with MS Angle frame made of 35x35x5mm and shall be provided with lifting hooks as required. | 4.00 | Job |  | 8500.00 | 34000.00 | 10000.00 | 40000.00 | 34000.00 | Techno Electricals
9.00 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required. 3 x 6 sq. mm | 150.00 | Mtr |  | 150.00 | 22500.00 | 230.00 | 34500.00 | 22500.00 | Techno Electricals
10.00 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required. 2 X 10 sq. mm + 1 X 6 sq. mm earth wire | 150.00 | Mtr |  | 300.00 | 45000.00 | 330.00 | 49500.00 | 45000.00 | Techno Electricals
11.00 | Supply, Installation, Testing and Commissioning of 3 KVA, single phase UPS system with input voltage 150 - 280 volt and output 230 volt + 1%, 50 Hz + 5 Hz., voltage regulation from no load to full load will be within + 1% in both the case. UPS will withstand 10% overload for 10 minutes and 50 % over load for 10 seconds. The UPS should have auto and manual bypass arrangements. The UPS should be provided to withstand 15 minutes battery backup on full load with suitable rating sealed maintenance free battery i/c interlinks complete etc. as required. | 1.00 | Job |  | 60000.00 | 60000.00 | 50000.00 | 50000.00 | 50000.00 | surbhi association
12.00 | Supply, Installation, Testing & Commissioning of Electrical LT Panel cubicle type, made out of 2 mm thick CRCA sheet and 3 mm thick gland plate, 100x100 x3 mm suitable MS channels frame in the bottom/ legs for grouting in foundation etc totally enclosed IP 42, free standing, floor mounting, dust and vermin proof, indoor, compartmentalised with consealed hinged lockable doors, suitable for operation on 3 phase, 415 V, 50Hz AC system with TPN busbars including internal control wiring with minimum 2.5 sqmm size FRLS PVC insulated flexible wires/cable, interconnection, duly powder coated painting etc. as per technical specifications including following switchgears,metering instruments and accessories in the Panel as per the approved drawing. INCOMER 2 No- 250A, 36KA, 4 pole MCCB (Ics = lcu= 100%) with thermal megnetic release Make- L&T Cat no: DU-250 or Equivalent approved make BUSCOUPLER 1 No- 250A, 36KA, 4 pole MCCB (Ics = lcu= 100%) having thermal megnetic release with electrical & mechanical interlocking with both incommers Make- L&T Cat no: DU-250 or Equivalent approved make Busbar 1 Set of 250 Amp(Minimum) TPN busbars of high conductivity electrolytic grade aluminium with heat shrinkable colour sleeves & DMC/SMC supports Outgoing 10 nos -63A,18KA, 4 pole MCCB with thermal magnatic release DU-100D (Make-L&T or Equivalent approved make) 10nos -100A,18 KA, 4 pole MCCB with thermal magnatic release DU-100D (Make-L&T Equivalent approved make) Other Accessories 2 nos:- Digital LED type VAF+PF meter of suitable range with suitable CTs for 3 phase 4 wire operation with selector switch 20 nos-LED type indicating lamps for 'ON' (Red) with 2 Amp control MCB 08 nos -ON , OFF and Trip LED type indicator for incommers & ON and OFF LED type indicator for buscoupler MCCB's with 2 Amp control MCB 06 nos: -LED type Indicating Lamp for phase indication with 2Amp control MCB 23 Sets: (1 set for each MCCB) -Extended Rotary operating mechanism as required Internal connections, industrial connectors , control circuit protections, electrical & mechanical interlocking between incommers & bus coupler, 40x6 mm AL common Earth & any other accessories etc as required | 1.00 | Job |  | 425000.00 | 425000.00 | 300000.00 | 300000.00 | 300000.00 | surbhi association
13.00 | Metering Panel SITC of cubical type compartmentalized meter board suitable for 10 nos of energy meters made of 1.6 mm thick sheet steel, duly powder coated,integrated loose wire box, complete with incommer 4-pole MCCB of 100 Amp, 18KA , Ics=Icu=100% with ON indicator,insulated copper busbars of 100 Amp capacity , each meter compartment (minimum size 300 x 300mm) having DP MCB of 40A, space for single phase energy meter, pre-wired from bus bar up to connector block with DP MCB of 40 A, 10KA in loose wire box, locking /sealing arrangement for each compartment with suitable size window covered with transperant sheet/glass,bus bar chamber etc as required. | 1.00 | Job |  | 100000.00 | 100000.00 | 50000.00 | 50000.00 | 50000.00 | surbhi association
14.00 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia (Drilling of 300 mm dia, 4.5 Mtr deep by using Borewell machine) including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. (with charcoal/ coke and salt ) as required. | 7.00 | Set |  | 7000.00 | 49000.00 | 5500.00 | 38500.00 | 38500.00 | surbhi association
15.00 | Supplying and laying 25 mm X 5 mm G.I strip at 0.50 meter below ground as strip earth electrode, including connection/ terminating with G.I. nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of G.I. nut bolt & spring washer spaced at 50 mm) | 70.00 | Mtr |  | 250.00 | 17500.00 | 180.00 | 12600.00 | 12600.00 | surbhi association
16.00 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 70.00 | Mtr |  | 750.00 | 52500.00 | 600.00 | 42000.00 | 42000.00 | surbhi association
17.00 | Providing and fixing of lightning conductor finial, made of 25 mm dia 300 mm long, copper tube, having single prong at top, with 85 mm dia 3 mm thick copper base plate including holes etc. complete as required. | 3.00 | Each |  | 2000.00 | 6000.00 | 1800.00 | 5400.00 | 5400.00 | surbhi association
18.00 | Fixing of lightning conductor finial (single prong) with base plate including holes etc. complete as required. | 3.00 | Each |  | 1500.00 | 4500.00 | 500.00 | 1500.00 | 1500.00 | surbhi association
19.00 | Jointing copper / G.I. tape (with another copper/ G I tape, base of the finial or any other metallic object) by riveting / nut bolting/ sweating and soldering etc as required. | 3.00 | Each |  | 500.00 | 1500.00 | 50.00 | 150.00 | 150.00 | surbhi association
20.00 | Fixing of copper tape 20 mm X 3 mm thick on parapet or surface of wall for lightning conductor complete as required.(For horizontal run) | 50.00 | Meter |  | 900.00 | 45000.00 | 850.00 | 42500.00 | 42500.00 | surbhi association
21.00 | Providing and fixing copper tape 20 mm X 3 mm thick on parapet or surface of wall for lightning conductor complete as required.(For vertical run) | 60.00 | Meter |  | 900.00 | 54000.00 | 850.00 | 51000.00 | 51000.00 | surbhi association
22.00 | Supply & installation single dome LED type Aviation Obstruction light suitable to operate on 1ph, 230 V, 50Hz power supply including suitable arrangement for installation on the highest location of the building Make/Model:- Bajaj/ BGAV 302 LED OR Equv. Approved | 2.00 | Each |  | 6500.00 | 13000.00 | 4000.00 | 8000.00 | 8000.00 | surbhi association
23.00 | Supply, Installation, testing and commissioning of 24 Feet sweep size energy efficient, noiseless high volume low speed fans (HVLS), suitable for operation on three phase,50 Hz AC supply along with fan motor with or without gear box, suitable down rod on proflex self supported profile roofing as per site requirements. , required number of rotating blades, operating control panel with VFD, control remote etc. and all other associated components, safety and mounting arrangements as per OEM including welding, drilling, providing staging , ladders, boom lift, scaffolding etc. complete as per actual site requirements.( Power supply cable upto the fan will be providedd by AAI). | 1.00 | Job |  | 225000.00 | 225000.00 | 250000.00 | 250000.00 | 225000.00 | Techno Electricals
24.00 | Supply & Laying of 4 x 2.5 sqmm size & 1.1 kv grade FR PVC round sheathed copper (flexible) conductor unarmoured cable conforming to IS:694with up to date ammendments in the existing conduite/pipe/raceway / on surface as required | 50.00 | Mtrs |  | 250.00 | 12500.00 | 150.00 | 7500.00 | 7500.00 | surbhi association
25.00 | Supply, Installation, Testing and Commissioning of 7- Stage Purification System with inbuilt Storage Type water cooler of storage capacity 80 Liter and cooling capacity 60 liter/Hr. with full stainless steel body & storage tank, ecofriendly refrigerant, 2 No. of Cold Purified Water Outlet, Thermostat to control temperature automatically, suitable for operation on 230 V, 50 Hz single phase AC supply. PF>0.85, along with Hermetic type compressor with over loaded protection, condenser fan, conform to IS:1475 ( latest), Cooler to be provide with the limit switch to control the level of water in storage tank and switches ON/OFF the purification unit consists of Pre Filter, Carbon Filter, Reverse Osmosis membrane, Post Carbon filter, UV lamp accordingly to provide cool water continually without over flow and inbuilt safety feature etc. as required. | 1.00 | Job |  | 80000.00 | 80000.00 | 98500.00 | 98500.00 | 80000.00 | Techno Electricals
26.00 | Supplying, installation, testing and commissioning of electric driven terrace pump suitable for automatic operation and consisting of following, complete in all respects, as required: (Terrace Pump) (a) Horizontal type, multistage, centrifugal, split casing pump of cast iron body & bronze impeller with stainless steel shaft, mechanical confirming to IS : 1520 b) Suitable HP squirell cage induction motor TEFC type suitable for operation on 415 volts, 3 phase, 50 Hz, AC supply with IP55 class of protection for enclosure, horiziontal foot mounted type with Class-'F' insulation, conforming to IS-325. (c) M.S.fabricated common base plate, coupling, coupling guard, foundation bolts etc.as required. (d) Suitable cement concrete foundation duly plastered and with anti vibration pads. 900 lpm at 35 m Head | 1.00 | Set |  | 15000.00 | 15000.00 | 84000.00 | 84000.00 | 15000.00 | Techno Electricals
27.00 | Providing, installation, testing and commissioning of stainless steel Y-strainer fabricated out of 1.6 mm thick stainless steel, Grade 304, sheet with 3 mm dia holes with stainless steel flange 200 mm | 1.00 | Each |  | 8000.00 | 8000.00 | 19500.00 | 19500.00 | 8000.00 | Techno Electricals
28.00 | Providing, installation, testing and commissioning of stainless steel Y-strainer fabricated out of 1.6 mm thick stainless steel, Grade 304, sheet with 3 mm dia holes with stainless steel flange 150 mm | 1.00 | Each |  | 7000.00 | 7000.00 | 16900.00 | 16900.00 | 7000.00 | Techno Electricals
29.00 | Providing, installation, testing and commissioning of stainless steel Y-strainer fabricated out of 1.6 mm thick stainless steel, Grade 304, sheet with 3 mm dia holes with stainless steel flange 80 mm | 1.00 | Each |  | 6000.00 | 6000.00 | 5000.00 | 5000.00 | 5000.00 | surbhi association
30.00 | Providing & fixing of pressure switch in M.S. pipe line including connection etc. as required. | 3.00 | Each |  | 5000.00 | 15000.00 | 3000.00 | 9000.00 | 9000.00 | surbhi association
31.00 | Supplying and fixing air vessel made of 250 mm dia, 8 mm thick MS sheet, 1200 mm in height with air release valve on top and flanged connection to riser, drain arrangement with 25 mm dia gun metal wheel valve with required accessories, pressure gauge and paintingwith synthetic enamel paint of approved shade as required. | 1.00 | Each |  | 25000.00 | 25000.00 | 25000.00 | 25000.00 | 25000.00 | Techno Electricals, surbhi association
32.00 | Supplying, fixing, testing & commissioning of double flanged sluice valve of rating PN 1.6 with non rising spindle, bronze/gun metal seat, ISI marked complete with nuts, bolts, washers, gaskets and conforming to IS 780 of following sizes as required. 200 mm Dia. | 1.00 | Each |  | 25000.00 | 25000.00 | 19800.00 | 19800.00 | 19800.00 | surbhi association
33.00 | Supplying, fixing, testing and commissioning of butterfly valve of PN 1.6 rating with bronze/gunmetal seat duly ISI marked complete with nuts, bolts, washers, gaskets conforming to IS 13095 of following sizes as required. 150 mm | 5.00 | Each |  | 5500.00 | 27500.00 | 5600.00 | 28000.00 | 27500.00 | Techno Electricals
34.00 | Supplying, fixing, testing and commissioning of butterfly valve of PN 1.6 rating with bronze/gunmetal seat duly ISI marked complete with nuts, bolts, washers, gaskets conforming to IS 13095 of following sizes as required. 80 mm | 2.00 | Each |  | 3000.00 | 6000.00 | 4100.00 | 8200.00 | 6000.00 | Techno Electricals
35.00 | Providing, installation, testing and commissioning of non-return valve of following sizes confirming to IS: 5312 complete with rubber gasket, GI bolts, nuts, washers etc.as required. 150 mm | 2.00 | Each |  | 5000.00 | 10000.00 | 3900.00 | 7800.00 | 7800.00 | surbhi association
36.00 | Providing, installation, testing and commissioning of non-return valve of following sizes confirming to IS: 5312 complete with rubber gasket, GI bolts, nuts, washers etc.as required. 80 mm | 1.00 | Each |  | 3000.00 | 3000.00 | 2900.00 | 2900.00 | 2900.00 | surbhi association
37.00 | Providing, laying, testing & commissioning of 'C' class heavy duty MS pipe conforming to IS 3589/IS 1239 including Welding, fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. and fixing the pipe on the wall/ceiling with suitable clamp/support frame and painting with two or more coats of synthetic enamel paint of required shade complete as required. 150 mm dia | 150.00 | RMT |  | 4000.00 | 600000.00 | 2200.00 | 330000.00 | 330000.00 | surbhi association
38.00 | Providing, laying, testing & commissioning of 'C' class heavy duty MS pipe conforming to IS 3589/IS 1239 including Welding, fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. and fixing the pipe on the wall/ceiling with suitable clamp/support frame and painting with two or more coats of synthetic enamel paint of required shade complete as required. 80 mm dia | 24.00 | RMT |  | 2000.00 | 48000.00 | 1450.00 | 34800.00 | 34800.00 | surbhi association
39.00 | Providing, laying, testing & commissioning of 'C' class heavy duty MS pipe conforming to IS 3589/IS 1239 including Welding, fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. and fixing the pipe on the wall/ceiling with suitable clamp/support frame and painting with two or more coats of synthetic enamel paint of required shade complete as required. 25 mm dia | 24.00 | RMT |  | 750.00 | 18000.00 | 480.00 | 11520.00 | 11520.00 | surbhi association
40.00 | Supplying and fixing Single headed external yard hydrant valve with 1 No. 63 mm dia instantaneous FM Gunmetal/Stainless Steel coupling and cast iron wheel, ISI marked, conforming to IS 5290 (type A) with blank Gunmetal/Stainless Steel cap and chain as required. Single headed Gunmetal | 6.00 | Set |  | 5500.00 | 33000.00 | 5500.00 | 33000.00 | 33000.00 | Techno Electricals, surbhi association
41.00 | Supplying & fixing 63 mm dia gun metal short branch pipe with 20 mm nominal internal diameter size nozzle conforming to IS 903 suitable for instantaneous connection to interconnect hose pipe coupling as required. Gun Metal | 6.00 | Each |  | 2500.00 | 15000.00 | 1500.00 | 9000.00 | 9000.00 | surbhi association
42.00 | Supplying and fixing 63 mm dia, 15 m long RRL hose pipe with 63 mm dia male and female couplings duly bound with GI wire, rivets etc. conforming to IS 636 (type-A) as required. Gun Metal | 12.00 | Each |  | 3850.00 | 46200.00 | 4200.00 | 50400.00 | 46200.00 | Techno Electricals
43.00 | Supplying and fixing first-aid Hose Reel with MS construction spray painted in post office red, conforming to IS 884 complete with the following as required. 20 mm nominal internal dia water hose thermoplastic (Textile reinforced) type -2 as per IS: 12585 20 mm nominal internal dia gun metal globe valve & nozzle. Drum and brackets for fixing the equipmets on wall. Connections from riser with 25 mm dia stop gun metal valve & M.S. Pipe and socket. 40 mm | 6.00 | Each |  | 4000.00 | 24000.00 | 5900.00 | 35400.00 | 24000.00 | Techno Electricals
44.00 | Supplying and fixing of fire brigade connection of cast iron body with gun metal male instantaneous inlet couplings complete with cap and chain as reqd. for suitable dia MS pipe connection conforming to IS 904 as required. 2 way-100 mm dia M.S. Pipe | 1.00 | Each |  | 5000.00 | 5000.00 | 6000.00 | 6000.00 | 5000.00 | Techno Electricals
| Total in Figures |  |  |  |  | 3342300.00 |  | 3047770.00
Lowest Amount Quoted BY: surbhi association(3047770.00)

## BOQ Summary
BOQ Summary Details Tender Title: Construction of Domestic Air Cargo Terminal Building and associated works at Raja Bhoj Airport, Bhopal. SH - Provision of Power Supply, Fire Fighting and allied works. Tender ID: 2022_AAI_112216_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | surbhi association | 3047770.00 | L1
| 2 | Techno Electricals | 3342300.00 | L2