## BoQ1
Government eProcurement System Created By: SUBHASH KUMAR Created Date/Time: 31-May-2022 06:27 PM Tender Title: Provision of VRF ACs SPLIT ACs and Air Curtain in Terminal Building at Darbhanga Airport Tender ID: 2022_AAI_112694_1
Tender Inviting Authority: Sr. Manager (E-E), AAI, Darbhanga Airport
Name of Work: Provision of VRF ACs, Split ACs & Air Curtains in Terminal Building at Darbhanga Airport.
Contract No: 2022_AAI_112694_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Snowmex Refrigeration(GSTN-33ACPFS8798E1ZD) |  | ELEMECH SOLUTION PVT LTD(GSTN-NA) |  | COOL CARE REFRIGERATION(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SH:A:- SITC of VRF System ACs
1.01 | Supply, Installation, Testing & Commissioning of top discharge type Full Inverter VRF/VRV air conditioning System comprising of modular type high efficiency all inverter technology based hermetically sealed scroll compressors suitable for R-410A refrigerant(pre Charged) suitable for operation on 415V,3phase,50Hz Ac supply ,with air cooled condencer having propeller type fan with BLDC motor & protective coated fins , interconnecting piping,suction line insulation etc, microprocessor control panel suitable for automatic operation, high speed inverter control mechanism incorporating all safety function including unit mounted starter panel complete with IP-55 protection consisting of power disconnecting switches,starters for compressor motors, under voltage/over voltage trip, single phase priventers,communication card etc. having minimum COP not less than 3.0 at 100% load including necessary pressure test with N2 to direct any league of the refrigerant piping system, toping up of refrigerant, minor machinery work etc. complete as required as follow. (all components should be mounted on welded steel based frame, structure steel profile / panels whose cost shall be deemed to be included in the item rate. outdoor coolling capacity at ari condition : which indivisual unit above 16 HP shall have minimum 2 nos compressor and all compressor shall be of digital inverter scroll type.
1.02 | (i) Nominal Capacity : 64HP . | 1.00 | Job |  | 886000.00 | 886000.00 | 1033466.00 | 1033466.00 | 850000.00 | 850000.00 | 850000.00 | COOL CARE REFRIGERATION
1.03 | (ii) Nominal Capacity : 34 HP | 1.00 | Job |  | 565000.00 | 565000.00 | 584165.00 | 584165.00 | 525501.00 | 525501.00 | 525501.00 | COOL CARE REFRIGERATION
2.00 | Supply Installation, Testing & Commissioning of following VRF INDOOR UNITS including pressure testing &vaccum as per following capacities.
2.01 | (i) 4 way Cassette IDU - 4.0 TR with Panel & Cordless Remote. | 16.00 | Job |  | 33500.00 | 536000.00 | 40915.00 | 654640.00 | 40500.00 | 648000.00 | 536000.00 | Snowmex Refrigeration
2.02 | (ii) Floor Standing IDU - 8.0 TR with Panel & Cordless Remote . | 4.00 | Job |  | 122200.00 | 488800.00 | 195865.00 | 783460.00 | 135500.00 | 542000.00 | 488800.00 | Snowmex Refrigeration
3.00 | Supply. Installation, Testing & Commissioning of Refnet joints of minimum thickness as that of refrigerant piping including Pressure testing & Vaccum
3.01 | (i) Indoor Unit - Y Joints | 22.00 | job |  | 3450.00 | 75900.00 | 558.00 | 12276.00 | 4800.00 | 105600.00 | 12276.00 | ELEMECH SOLUTION PVT LTD
3.02 | (ii) Outdoor Unit - Y Joints | 5.00 | job |  | 5980.00 | 29900.00 | 837.00 | 4185.00 | 6500.00 | 32500.00 | 4185.00 | ELEMECH SOLUTION PVT LTD
4.00 | Supply, Installation, Testing & Commissioning of refrigerant piping connecting indoor unit & outdoor units including thermal insulation. Refrigerant piping shall be made of hard drawn copper pipe suitable for variable refrigerant flow system including all fittings, i.e. bends, elbows, tees with an internal joint type fitting etc. Pipiline must be tested for requisit pressure. Max. support distance shall be 8 ft. All refrigerant piping shall be insulated with min. 13 & 19 mm thk. nitrile rubber based insulating material as per the following :
4.01 | (i) 22.7 mm dia with 19mm thick nitrile rubber insulation | 400.00 | RMT |  | 832.00 | 332800.00 | 927.00 | 370800.00 | 400.00 | 160000.00 | 160000.00 | COOL CARE REFRIGERATION
4.02 | (ii) 44.5 mm dia with 19mm thick nitrile rubber insulation | 300.00 | RMT |  | 2123.00 | 636900.00 | 3244.00 | 973200.00 | 360.00 | 108000.00 | 108000.00 | COOL CARE REFRIGERATION
4.03 | (iii) 19.5 mm dia with 19mm thick nitrile rubber insulation | 200.00 | RMT |  | 705.00 | 141000.00 | 804.00 | 160800.00 | 400.00 | 80000.00 | 80000.00 | COOL CARE REFRIGERATION
4.04 | (iv) 34.9 mm dia with 19mm thick nitrile rubber insulation | 200.00 | RMT |  | 1657.00 | 331400.00 | 2030.00 | 406000.00 | 550.00 | 110000.00 | 110000.00 | COOL CARE REFRIGERATION
4.05 | (v) 41.3 mm dia with 19mm thick nitrile rubber insulation | 60.00 | RMT |  | 2082.00 | 124920.00 | 2754.00 | 165240.00 | 1850.00 | 111000.00 | 111000.00 | COOL CARE REFRIGERATION
4.06 | (vi) 38.1 mm dia with 19mm thick nitrile rubber insulation | 30.00 | RMT |  | 1815.00 | 54450.00 | 2386.00 | 71580.00 | 1560.00 | 46800.00 | 46800.00 | COOL CARE REFRIGERATION
4.07 | (vii) 31.8 mm dia with 19mm thick nitrile rubber insulation | 30.00 | RMT |  | 1370.00 | 41100.00 | 1711.00 | 51330.00 | 500.00 | 15000.00 | 15000.00 | COOL CARE REFRIGERATION
4.08 | (viii) 28.6 mm dia with 19mm thick nitrile rubber insulation | 30.00 | RMT |  | 1090.00 | 32700.00 | 1411.00 | 42330.00 | 890.00 | 26700.00 | 26700.00 | COOL CARE REFRIGERATION
4.09 | (ix) 25.4 mm dia with 19mm thick nitrile rubber insulation | 30.00 | RMT |  | 1040.00 | 31200.00 | 1170.00 | 35100.00 | 100.00 | 3000.00 | 3000.00 | COOL CARE REFRIGERATION
4.10 | (x) 15.9 mm dia with 19mm thick nitrile rubber insulation | 30.00 | RMT |  | 610.00 | 18300.00 | 771.00 | 23130.00 | 650.00 | 19500.00 | 18300.00 | Snowmex Refrigeration
4.11 | (xi) 12.7 mm dia with 19mm thick nitrile rubber insulation | 30.00 | RMT |  | 505.00 | 15150.00 | 537.00 | 16110.00 | 300.00 | 9000.00 | 9000.00 | COOL CARE REFRIGERATION
4.12 | (xii) 9.5 mm dia with 19mm thick nitrile rubber insulation | 30.00 | RMT |  | 425.00 | 12750.00 | 425.00 | 12750.00 | 350.00 | 10500.00 | 10500.00 | COOL CARE REFRIGERATION
4.13 | (xiii) 6.4 mm dia with 19mm thick nitrile rubber insulation | 30.00 | RMT |  | 396.00 | 11880.00 | 282.00 | 8460.00 | 1.00 | 30.00 | 30.00 | COOL CARE REFRIGERATION
4.14 | Supply, Installation, Testing & Commissioning of drain piping from hard drawn CPVC material of 25mm size and duly insulated witth 10 mm nitrile rubber insulation | 600.00 | RMT |  | 140.00 | 84000.00 | 407.00 | 244200.00 | 80.00 | 48000.00 | 48000.00 | COOL CARE REFRIGERATION
4.15 | Supply, Installation, Testing & Commissioning of drain piping from hard drawn CPVC material of 30mm sizes and duly insulated witth 10 mm nitrile rubber insulation | 400.00 | RMT |  | 160.00 | 64000.00 | 548.00 | 219200.00 | 110.00 | 44000.00 | 44000.00 | COOL CARE REFRIGERATION
4.16 | Supply & Charging of extra refrigerant R-410A in VRF system | 50.00 | KG. |  | 975.00 | 48750.00 | 1115.00 | 55750.00 | 800.00 | 40000.00 | 40000.00 | COOL CARE REFRIGERATION
5.00 | Supply & fixing of control cum trans-mission wiring of copper between indoor and out door unit in PVC Conduit.
5.01 | (i) 3C x 2.5 mm2 Cu (Control cable from ODU to IDU for VRF units) | 700.00 | RMT |  | 185.00 | 129500.00 | 227.00 | 158900.00 | 150.00 | 105000.00 | 105000.00 | COOL CARE REFRIGERATION
5.02 | (ii) 2CX1.5 mm2 Cu (Control cable from ODU to IDU for VRF units) | 200.00 | RMT |  | 160.00 | 32000.00 | 120.00 | 24000.00 | 130.00 | 26000.00 | 24000.00 | ELEMECH SOLUTION PVT LTD
6.00 | SUB HEAD B:-SITC of Split ACs
6.01 | SITC of 1 Phase, 1.5 TR split type of 5 star rating Inverter Air-conditioners along with high wall type indoor unit suitable to operate from 230±10%, 50 Hz, 1 phase power supply (along with necessary wiring from nearest power source to the required outdoor and indoor units) having high EER Compressor and cooling capacity of 5200Watts (Nominal) with Indoor & Outdoor Copper coil refrrigeration with ecofriendly refregiration Gas to maintain room temperature 20±2°C. The indoor unit should have real time clock, operating facility from cordless remote, along with time and temperature display. Outdoor unit to be installed as Directed by Engineer-in-Charge. | 2.00 | job |  | 38500.00 | 77000.00 | 61929.00 | 123858.00 | 56140.00 | 112280.00 | 77000.00 | Snowmex Refrigeration
6.02 | Supply, fabrication and erection of metallic structure fabricated from suitable size of MS angle frame with two coats of primer to be used for suspension of outdoor compressor units (as per Item No.6.01 ) as direction of Engineer-in-Charge. | 2.00 | job |  | 30000.00 | 60000.00 | 11851.00 | 23702.00 | 950.00 | 1900.00 | 1900.00 | COOL CARE REFRIGERATION
6.03 | Supply and fixing of extra copper refrigerant piping complete with suction / liquid line, insulation (i.e. cunifoam with neoprene / rubber lining), and all the accessories as per site requirement as directed by Engineer-in-Charge. | 20.00 | Mtrs |  | 890.00 | 17800.00 | 747.00 | 14940.00 | 1386.00 | 27720.00 | 14940.00 | ELEMECH SOLUTION PVT LTD
6.04 | Supply & Laying of Extra 2 core x 2.5 sqmm unarmoured PVC insulated & Sheathed copper conductor cable of 1.1 KV grade as directed by Engineer-in-Charge. | 10.00 | Mtrs. |  | 180.00 | 1800.00 | 199.00 | 1990.00 | 120.00 | 1200.00 | 1200.00 | COOL CARE REFRIGERATION
6.05 | Supply and laying of 25 mm dia PVC pipe to be used for drainage of condensate from indoor units to the nearest drain-port as directed by Engineer-in-Charge | 20.00 | Mtrs. |  | 140.00 | 2800.00 | 379.00 | 7580.00 | 105.00 | 2100.00 | 2100.00 | COOL CARE REFRIGERATION
7.00 | SH:C-SITC of Air Curtains
7.01 | SITC of Industrial Aytomatic Air Curtains with altra high speed wind,optimized motor power, stainless steel impeller, metal suction impeller,air speed ranging to 12m/sec. to 25m/sec., model with high speed volume and for suitable gate sizes. | 5.00 | Job |  | 39800.00 | 199000.00 | 27885.00 | 139425.00 | 71491.00 | 357455.00 | 139425.00 | ELEMECH SOLUTION PVT LTD
| Total in Figures |  |  |  |  | 5082800.00 |  | 6422567.00 |  | 4168786.00
Lowest Amount Quoted BY: COOL CARE REFRIGERATION(4168786.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of VRF ACs SPLIT ACs and Air Curtain in Terminal Building at Darbhanga Airport Tender ID: 2022_AAI_112694_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | COOL CARE REFRIGERATION | 4168786.00 | L1
| 2 | Snowmex Refrigeration | 5082800.00 | L2
| 3 | ELEMECH SOLUTION PVT LTD | 6422567.00 | L3