## BoQ1
Government eProcurement System Created By: UMESH CHAURASIA Created Date/Time: 10-Jun-2022 11:46 AM Tender Title: Construction of Domestic Air Cargo Terminal Building and associated works at Raja Bhoj Airport, Bhopal. SH- Electrical Works - AC and Cold Storage Tender ID: 2022_AAI_114860_1
Tender Inviting Authority: SM(E-E), AAI, R.B. Airport, Bhopal
Name of Work: Construction of Domestic Air Cargo Terminal Building and associated works at Raja Bhoj Airport, Bhopal. SH: Electrical Works – AC & Cold Storage.
Contract No: AAI/BPL/ENGG(E)/NIT-04/2022-23
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Weartech Engineers Pvt Ltd(GSTN-23AABCW1561C1ZV) |  | VOLGA AIR TECHNOLOGIES INDIA(GSTN-23AFGPC9885C1ZC)
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Design, Supply, Installation, testing and commissioning of Capacity : 15000 BTU/ Hrs X 2 Nos (01 Working + 01 standby) Refrigeration system for maintaining temperature in cold room with cooling system working on CFC free refrigerant complete in all respect for cold room of size 8.20 feet X 16.70 feet X 10 feet (H) for pharma products including Evaporative unit with matching condensing unit, Blower, Coil, Expansion valve, condensor, copressor, motor, refrigerant piping (upto 7 mtr length included)/drain piping, insulation of cold room's wall, ceiling, door with 60 mm prefab CFC free PUF panel inside PPGI & Out side PPGI and floor with 60/50 mm CFC free PUF pannels PP/GI with anti skid floor and heavy duty hinges and handles with inside & out side PPGI finish with provision for locking the door from out side with all accesseries like kick plate, light switch, Digital temperature indicator, Door Closures safety release knob, controller, safety alarm etc to achieve the required temperature of +2 to +8 degree centigrade in cold rooms with automated data logger suitable for PC Connectivity (Without PC). FLOOR - P P OUTER 6 MM MARINE PLY - 1.2 MM Aluminium. checkered plate, as per specifications i/c copper piping, cabling and starter Installation, testing and commissioning refrigeration units as required. | 2.00 | Each |  | 595000.00 | 1190000.00 | 625433.00 | 1250866.00 | 1190000.00 | Weartech Engineers Pvt Ltd
2.00 | Supply Installation, Testing & Commissioning of modular type Variable Refrigerant Flow/Variable Refrigerant Volume air cooled Outdoor units suitable for cooling and heating, having all hermetically sealed inverter type Scroll Compressor(s), minimum two compressors for above 14 HP modules, microprocessor based Controller, top discharge type condensing unit(s), with Ecofriendly Refrigerant, vibration isolators, with suitable foundation etc. complete as required. The unit shall deliver the rated capacity at AHRI Conditions and work even at 50°C ambient temperature without tripping. The unit shall be suitable to work on 400V +/- 10%, 3 Phase, 50Hz AC power supply. The unit shall be filled with first charge of the refrigerant and ready for use as required. The COP at AHRI conditions shall not be less than 3.1 and IEER not less than 6.5. 40 HP ODU | 1.00 | Nos. |  | 757183.00 | 757183.00 | 658750.00 | 658750.00 | 658750.00 | VOLGA AIR TECHNOLOGIES INDIA
3.00 | Supply, installation, testing and commissioning of following minimum capacity 4- way flow VRV/VRF Cassette Type Indoor ceiling mounted unit equipped with synthetic washable media pre-filter, fan section with low noise fan/dynamically balanced blower, multispeed motor, coil section with DX Copper coil, electronic expansion valve, outer cabinet, drain pump, grill, necessary supports, vibration isolation, cord less remote control etc., suitable for operation on single phase 230 V ± 10%, 50Hz AC supply, complete, as required. The unit shall have automatic force shut down provision in case of fire on receiving signal from BMS System. The cooling capacity of indoor unit will be at air inlet conditions of 27 Degree C DB and 19 Degree C WB temperature. (INDOOR UNIT-CASSETTE TYPE) 3.2 TR | 6.00 | Nos. |  | 47555.00 | 285330.00 | 37050.00 | 222300.00 | 222300.00 | VOLGA AIR TECHNOLOGIES INDIA
4.00 | Supply, installation, testing and commissioning of following minimum capacity 4- way flow VRV/VRF Cassette Type Indoor ceiling mounted unit equipped with synthetic washable media pre-filter, fan section with low noise fan/dynamically balanced blower, multispeed motor, coil section with DX Copper coil, electronic expansion valve, outer cabinet, drain pump, grill, necessary supports, vibration isolation, cord less remote control etc., suitable for operation on single phase 230 V ± 10%, 50Hz AC supply, complete, as required. The unit shall have automatic force shut down provision in case of fire on receiving signal from BMS System. The cooling capacity of indoor unit will be at air inlet conditions of 27 Degree C DB and 19 Degree C WB temperature. (INDOOR UNIT-CASSETTE TYPE) 2.4 TR | 1.00 | Nos. |  | 46718.00 | 46718.00 | 35900.00 | 35900.00 | 35900.00 | VOLGA AIR TECHNOLOGIES INDIA
5.00 | Supply, installation, testing and commissioning of following minimum capacity 4- way flow VRV/VRF Cassette Type Indoor ceiling mounted unit equipped with synthetic washable media pre-filter, fan section with low noise fan/dynamically balanced blower, multispeed motor, coil section with DX Copper coil, electronic expansion valve, outer cabinet, drain pump, grill, necessary supports, vibration isolation, cord less remote control etc., suitable for operation on single phase 230 V ± 10%, 50Hz AC supply, complete, as required. The unit shall have automatic force shut down provision in case of fire on receiving signal from BMS System. The cooling capacity of indoor unit will be at air inlet conditions of 27 Degree C DB and 19 Degree C WB temperature. (INDOOR UNIT-CASSETTE TYPE) 2 TR | 1.00 | Nos. |  | 42541.00 | 42541.00 | 35325.00 | 35325.00 | 35325.00 | VOLGA AIR TECHNOLOGIES INDIA
6.00 | Supply, installation, testing and commissioning of following minimum capacity 4- way flow VRV/VRF Cassette Type Indoor ceiling mounted unit equipped with synthetic washable media pre-filter, fan section with low noise fan/dynamically balanced blower, multispeed motor, coil section with DX Copper coil, electronic expansion valve, outer cabinet, drain pump, grill, necessary supports, vibration isolation, cord less remote control etc., suitable for operation on single phase 230 V ± 10%, 50Hz AC supply, complete, as required. The unit shall have automatic force shut down provision in case of fire on receiving signal from BMS System. The cooling capacity of indoor unit will be at air inlet conditions of 27 Degree C DB and 19 Degree C WB temperature. (INDOOR UNIT-CASSETTE TYPE) 1.6 TR | 2.00 | Nos. |  | 41646.00 | 83292.00 | 35095.00 | 70190.00 | 70190.00 | VOLGA AIR TECHNOLOGIES INDIA
7.00 | Supply, installation, testing and commissioning of following minimum capacity 4- way flow VRV/VRF Cassette Type Indoor ceiling mounted unit equipped with synthetic washable media pre-filter, fan section with low noise fan/dynamically balanced blower, multispeed motor, coil section with DX Copper coil, electronic expansion valve, outer cabinet, drain pump, grill, necessary supports, vibration isolation, cord less remote control etc., suitable for operation on single phase 230 V ± 10%, 50Hz AC supply, complete, as required. The unit shall have automatic force shut down provision in case of fire on receiving signal from BMS System. The cooling capacity of indoor unit will be at air inlet conditions of 27 Degree C DB and 19 Degree C WB temperature. (INDOOR UNIT-CASSETTE TYPE) 1.2 TR | 1.00 | Nos. |  | 40515.00 | 40515.00 | 34750.00 | 34750.00 | 34750.00 | VOLGA AIR TECHNOLOGIES INDIA
8.00 | Supply, installation, testing and commissioning of following minimum capacity VRV / VRF Highwall type Indoor unit equipped with washable synthetic media pre-filter, fan section with low noise fan / dynamically balanced blower, multi speed motor, coil section with DX copper coil, electronic expansion valve, outer cabinet, cordless remote control, drainpan, necessary accessories etc., suitable for operation on 230V ± 10 %, 50Hz, single phase AC supply, complete as required. The unit shall have automatic force shut down provision in case of fire on receiving signal from BMS System. The cooling capacity of indoor unit will be at air inlet conditions of 27 Degree C DB and 19 Degree C WB temperature. (HIGH WALL TYPE) 1.45 TR | 2.00 | Each |  | 26460.00 | 52920.00 | 23150.00 | 46300.00 | 46300.00 | VOLGA AIR TECHNOLOGIES INDIA
9.00 | Supply, installation, testing and commissioning of following minimum capacity VRV / VRF Highwall type Indoor unit equipped with washable synthetic media pre-filter, fan section with low noise fan / dynamically balanced blower, multi speed motor, coil section with DX copper coil, electronic expansion valve, outer cabinet, cordless remote control, drainpan, necessary accessories etc., suitable for operation on 230V ± 10 %, 50Hz, single phase AC supply, complete as required. The unit shall have automatic force shut down provision in case of fire on receiving signal from BMS System. The cooling capacity of indoor unit will be at air inlet conditions of 27 Degree C DB and 19 Degree C WB temperature. (HIGH WALL TYPE) 1.3 TR | 2.00 | Each |  | 25864.00 | 51728.00 | 20275.00 | 40550.00 | 40550.00 | VOLGA AIR TECHNOLOGIES INDIA
10.00 | Supply, installation, testing and commissioning of following minimum capacity VRV / VRF Highwall type Indoor unit equipped with washable synthetic media pre-filter, fan section with low noise fan / dynamically balanced blower, multi speed motor, coil section with DX copper coil, electronic expansion valve, outer cabinet, cordless remote control, drainpan, necessary accessories etc., suitable for operation on 230V ± 10 %, 50Hz, single phase AC supply, complete as required. The unit shall have automatic force shut down provision in case of fire on receiving signal from BMS System. The cooling capacity of indoor unit will be at air inlet conditions of 27 Degree C DB and 19 Degree C WB temperature. (HIGH WALL TYPE) 1 TR | 3.00 | Each |  | 24372.00 | 73116.00 | 19700.00 | 59100.00 | 59100.00 | VOLGA AIR TECHNOLOGIES INDIA
11.00 | SITC of Seamless heavy gauge Copper refrigerant piping of adequate size duly insulated with nitrile insulation of adequate thickness. Refrigeration piping will have to be taken in the piping rack / Cable tray Support individually connecting to all indoor units for the respective floors. Even necessary supports, fittings, valves & ref. joints where ever required will be included.(Supply + Return) with 13mm thick insulation on liquid line & 19mm thick insulation sleeves on Suction Line) | 125.00 | Meter |  | 1750.00 | 218750.00 | 1350.00 | 168750.00 | 168750.00 | VOLGA AIR TECHNOLOGIES INDIA
12.00 | Supply, installation, testing & commissioning of ref nut / Y-joints of brass for indoor and outdoor units for suitable size as per requirement. For Outdoor Unit | 1.00 | Each |  | 4500.00 | 4500.00 | 5312.50 | 5312.50 | 4500.00 | Weartech Engineers Pvt Ltd
13.00 | Supply, installation, testing & commissioning of Ref nut / Y-joints of brass for indoor and outdoor units for suitable size as per requirement. For Indoor Unit | 18.00 | Each |  | 2500.00 | 45000.00 | 4062.50 | 73125.00 | 45000.00 | Weartech Engineers Pvt Ltd
14.00 | Supply and fixing of drain piping in hard PVC with all fittings, supports and clamps, including drilling hole in wall to route the drain pipe with 6mm thick nitrile rubber insulation.- 25mm with 9mm nitrile tubes. | 50.00 | Meter |  | 175.00 | 8750.00 | 140.00 | 7000.00 | 7000.00 | VOLGA AIR TECHNOLOGIES INDIA
15.00 | Supply and drawing Control Cable between the indoor units & outdoor units. 2C x 0.75 Sq.mm Shielded Braided PVC inner sheathed, copper conductor, communication cable from indoor to outdoor units & between central controller. | 100.00 | RMT |  | 165.00 | 16500.00 | 120.00 | 12000.00 | 12000.00 | VOLGA AIR TECHNOLOGIES INDIA
16.00 | Supply, fabrication and installation at proposed location of MS base frame ( for VRF machine Out Door Unit).The same shall be fabricated form 100mm wide "C" channels & shall be painted with primer and black paint. | 2.00 | Nos. |  | 3500.00 | 7000.00 | 4375.00 | 8750.00 | 7000.00 | Weartech Engineers Pvt Ltd
| Total in Figures |  |  |  |  | 2923843.00 |  | 2728968.50
Lowest Amount Quoted BY: VOLGA AIR TECHNOLOGIES INDIA(2728968.50)

## BOQ Summary
BOQ Summary Details Tender Title: Construction of Domestic Air Cargo Terminal Building and associated works at Raja Bhoj Airport, Bhopal. SH- Electrical Works - AC and Cold Storage Tender ID: 2022_AAI_114860_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | VOLGA AIR TECHNOLOGIES INDIA | 2728968.50 | L1
| 2 | Weartech Engineers Pvt Ltd | 2923843.00 | L2