## BoQ1
Government eProcurement System Created By: Debdeep Dutta Created Date/Time: 13-Jun-2022 11:24 AM Tender Title: Provision of Advance Lightning Arrestor and Grounding System for Terminal Building at Silchar Airport. Tender ID: 2022_AAI_115150_1
Tender Inviting Authority: Asstt. G.M. (Engg-Electrical), AAI, Silchar Airport.
Name of Work: Provision of Advance Lightning Arrestor and Grounding System for Terminal Building at Silchar Airport (SH: Provision of External Lightning Protection at Silchar Airport).
Tender Id: 2022_AAI_115150_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Vrinda Nano Technologies Pvt Ltd(GSTN-06AABCV6699N1ZG) |  | JCC ENGINEERS PRIVATE LIMITED(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply, Installation, Testing & Commissioning of Parallel Connectors for (700mm air terminal) connecting two conductors in parallel manner. Material- superior grade Stainless Steel, with clamping range- Rd / Rd 7-10 mm complete as required. | 60.00 | Each | 0.00 | 590.00 | 35400.00 | 750.00 | 45000.00 | 35400.00 | Vrinda Nano Technologies Pvt Ltd
2.00 | Supply, Installation, Testing & Commissioning of Air-termination rod of diameter- 10 mm, length- 1000 mm, of material- Al chamfered on both ends complete as required. | 4.00 | Each | 0.00 | 650.00 | 2600.00 | 550.00 | 2200.00 | 2200.00 | JCC ENGINEERS PRIVATE LIMITED
3.00 | Supply, Installation, Testing & Commissioning of Air-termination rod having length- 3000 mm, of Material- AlMgSi, of Diameter Ø 16 / 10 mm, chamfered on both ends complete as required. | 27.00 | Each | 0.00 | 1400.00 | 37800.00 | 1620.00 | 43740.00 | 37800.00 | Vrinda Nano Technologies Pvt Ltd
4.00 | Supply, Installation, Testing & Commissioning of Air-termination rod having length- 3500 mm, of Material-AlMgSi, of Diameter Ø 16 / 10 mm, chamfered on both ends complete as required. | 2.00 | Each | 0.00 | 2150.00 | 4300.00 | 1925.00 | 3850.00 | 3850.00 | JCC ENGINEERS PRIVATE LIMITED
5.00 | Supply, Installation, Testing & Commissioning of Air-termination rod having length- 4500mm, of Diameter Ø22/16/10 mm, of radius 320 mm, Material of air-termination rod- Al, Material of tripod- St/tZn complete as required. | 4.00 | Each | 0.00 | 36250.00 | 145000.00 | 35000.00 | 140000.00 | 140000.00 | JCC ENGINEERS PRIVATE LIMITED
6.00 | Supply, Installation, Testing & Commissioning of Air-termination rod having length- 5500mm, of Diameter Ø22/16/10 mm, of radius 320 mm, Material of air-termination rod- Al, Material of tripod- St/tZn complete as required. | 1.00 | Each | 0.00 | 20150.00 | 20150.00 | 22230.00 | 22230.00 | 20150.00 | Vrinda Nano Technologies Pvt Ltd
7.00 | Supply, Installation, Testing & Commissioning of Side Wall Clamp for air terminal, Material - superior grade Stainless Steel, Clamping range - 16/10 mm complete as required. | 70.00 | Each | 0.00 | 910.00 | 63700.00 | 1050.00 | 73500.00 | 63700.00 | Vrinda Nano Technologies Pvt Ltd
8.00 | Supply, Installation, Testing & Commissioning of protecting roofing sheets of material EVA (Ethylene-vinyl acetate) under the concrete base of approx weight 17 kg. complete as required. Size of the roofing sheet is approx outside diameter 370 mm and inside diameter 360 mm. | 22.00 | Each | 0.00 | 260.00 | 5720.00 | 245.00 | 5390.00 | 5390.00 | JCC ENGINEERS PRIVATE LIMITED
9.00 | Supply, Installation, Testing & Commissioning of Concrete base for air-termination rods, for self-supporting airtermination rods in the tripod. Support Wedge- Ø16 mm, Diameter- Ø 337 mm, Material- concrete, Material of wedge- superior grade Stainless Steel & approx Weight 17kg. | 61.00 | Each | 0.00 | 610.00 | 37210.00 | 575.00 | 35075.00 | 35075.00 | JCC ENGINEERS PRIVATE LIMITED
10.00 | Supply, Installation, Testing & Commissioning of Air-termination rod clamps for connecting air-termination rods with one or two conductors. Material of clamp Al, with clamping range of air-termination rod 8-10 mm and the clamping range of conductor Rd 2x 8-10 mm complete as required. | 4.00 | Each | 0.00 | 350.00 | 1400.00 | 400.00 | 1600.00 | 1400.00 | Vrinda Nano Technologies Pvt Ltd
11.00 | Supply, Installation, Testing & Commissioning of Air-termination rod clamps for connecting air-termination rods with one or two conductors. Material of clamp Al, with clamping range of air-termination rod 16 mm and Clamping range of conductor Rd 2x 8-10 mm complete as required. | 29.00 | Each | 0.00 | 260.00 | 7540.00 | 275.00 | 7975.00 | 7540.00 | Vrinda Nano Technologies Pvt Ltd
12.00 | Supply, Installation, Testing & Commissioning of Universal connector of Material- superior grade Stainless Steel, with clamping range- 8- 10mm, with truss head screw of approx size M10x35 mm complete as required. | 141.00 | Each | 0.00 | 150.00 | 21150.00 | 160.00 | 22560.00 | 21150.00 | Vrinda Nano Technologies Pvt Ltd
13.00 | Supply, Installation, Testing & Commissioning of Roof Conductor of Diameter Ø8 mm, Cross-section- 50 mm2, of Material- AlMgSi complete as required. | 1160.00 | Mtr | 0.00 | 165.00 | 191400.00 | 162.00 | 187920.00 | 187920.00 | JCC ENGINEERS PRIVATE LIMITED
14.00 | Supply, Installation, Testing & Commissioning of Conductor holder for Parapet wall/Side wall of Material- superior grade Stainless Steel, for Rd 8-10 mm Fl 20 mm, Height- 20 mm complete as required. | 560.00 | Each | 0.00 | 175.00 | 98000.00 | 190.00 | 106400.00 | 98000.00 | Vrinda Nano Technologies Pvt Ltd
15.00 | Supply, Installation, Testing & Commissioning of Conductor holder with a slotted saddle clamp, for fixing round conductors. For use with different materials, e.g. Al, superior grade Stainless Steel, St/tZn and Cu, fixed conductor routing, with female thread complete as required. | 100.00 | Each | 0.00 | 80.00 | 8000.00 | 110.00 | 11000.00 | 8000.00 | Vrinda Nano Technologies Pvt Ltd
16.00 | Supply, Installation, Testing & Commissioning of Conductor holder with a slotted saddle clamp, for fixing round conductors. For use with different materials, e.g. Al, superior grade Stainless Steel, St/tZn and Cu, fixed conductor routing, with female thread complete as required. | 500.00 | Each | 0.00 | 130.00 | 65000.00 | 155.00 | 77500.00 | 65000.00 | Vrinda Nano Technologies Pvt Ltd
17.00 | Supply & application of Lord glue for connecting metal to metal. | 3.00 | Each | 0.00 | 9515.00 | 28545.00 | 10500.00 | 31500.00 | 28545.00 | Vrinda Nano Technologies Pvt Ltd
18.00 | Supply & application of Lord glue for connecting metal to fiberglass. | 2.00 | Each | 0.00 | 7500.00 | 15000.00 | 6500.00 | 13000.00 | 13000.00 | JCC ENGINEERS PRIVATE LIMITED
19.00 | Supply, Installation, Testing & Commissioning of Connection Clamps for Steel/metal column. Clamping range of the clamp- 3-18 mm, Material of the clamp- superior grade Stainless Steel, Clamping range of conductor Rd 6-10 mm complete as required. | 10.00 | Each | 0.00 | 490.00 | 4900.00 | 550.00 | 5500.00 | 4900.00 | Vrinda Nano Technologies Pvt Ltd
20.00 | Supply, Installation, Testing & Commissioning of Pipe clamp for integrating pipes into the protective and functional equipotential bonding, complete version with adjustable superior grade Stainless Steel tensioning strap, for connecting 1 conductor Rd D10 mm or 1-2 conductors Rd D6-8 mm or 4-50 mm² (solid / stranded)to pipe size 16-89 mm (3/8-3'') complete as required. | 10.00 | Each | 0.00 | 650.00 | 6500.00 | 710.00 | 7100.00 | 6500.00 | Vrinda Nano Technologies Pvt Ltd
21.00 | Down conductor: Supply, Installation, Testing & Commissioning of Conductor of Diameter Ø8 mm, Cross-section- 50 mm2, of Material- AlMgSi complete as required. | 150.00 | Mtr | 0.00 | 175.00 | 26250.00 | 185.00 | 27750.00 | 26250.00 | Vrinda Nano Technologies Pvt Ltd
22.00 | Down conductor: Supply, Installation, Testing & Commissioning of Conductor holder for Parapet wall/Side wall of Material- superior grade Stainless Steel, for Rd 8-10 mm Fl 20 mm, Height- 20 mm complete as required. | 150.00 | Each | 0.00 | 190.00 | 28500.00 | 180.00 | 27000.00 | 27000.00 | JCC ENGINEERS PRIVATE LIMITED
23.00 | Down conductor: Supply, Installation, Testing & Commissioning of CUI Conductor the dangerous area of touch and step voltages for living beings is defined as an area of approx. 3 m around the down conductor, from ground level up to a height of approx. 3 m. Material of conductor- Cu, Material of insulation- XLPE, Diameter Ø conductor- 20 mm complete as required. | 39.00 | Each | 0.00 | 16500.00 | 643500.00 | 16500.00 | 643500.00 | 643500.00 | JCC ENGINEERS PRIVATE LIMITED, Vrinda Nano Technologies Pvt Ltd
24.00 | Down conductor: Supply, Installation, Testing & Commissioning of Conductor Holders for installing the CUI conductor on walls or facades. Conductor leading- fixed, Material of conductor holder- superior grade Stainless Steel, Conductor holder support- Rd 20 mm, Height of conductor holder- 10 mm complete as required. | 117.00 | Each | 0.00 | 520.00 | 60840.00 | 550.00 | 64350.00 | 60840.00 | Vrinda Nano Technologies Pvt Ltd
25.00 | Down conductor: Supply, Installation, Testing & Commissioning of Universal connector of Material- StSt, with clamping range- 8-10mm, with truss head screw M10x35 mm complete as required. | 39.00 | Each | 0.00 | 135.00 | 5265.00 | 165.00 | 6435.00 | 5265.00 | Vrinda Nano Technologies Pvt Ltd
26.00 | Earthing: Supply, Installation, Testing & Commissioning of UNI Disconnecting Clamps with intermediate plate for round and flat conductor of Material- superior grade Stainless Steel, Material thickness- 2.5 mm, with clamping range- Rd / Fl 8-10 / 30 mm complete as required. | 20.00 | Each | 0.00 | 225.00 | 4500.00 | 250.00 | 5000.00 | 4500.00 | Vrinda Nano Technologies Pvt Ltd
27.00 | Earthing: Supply, Installation, Testing & Commissioning of GI flat (25x6mm) Strip. Having width- 25mm, Thickness- 6mm, Material- Hot dipped Galvanized Iron, Cross Section- 150 mm2 Coating thickness- Avg. 70 microns complete as required. | 100.00 | Mtr | 0.00 | 245.00 | 24500.00 | 260.00 | 26000.00 | 24500.00 | Vrinda Nano Technologies Pvt Ltd
28.00 | Earthing: Supply, Installation, Testing & Commissioning of GI strip holder of material- Dow moulded compound, having height- 19mm, Slot Size- 25x6 mm complete as required. | 40.00 | Each | 0.00 | 100.00 | 4000.00 | 125.00 | 5000.00 | 4000.00 | Vrinda Nano Technologies Pvt Ltd
29.00 | Earthing: Supply, Installation, Testing & Commissioning of Earthing Copper bonded rod with Low carbon steel, high tensile strength copper bonded rod with min 254 microns of copper plating, Diameter- 17.2 mm, Length- 3 meters, Material- Copper Bonded, Coating thickness- 250 microns (min). The backfill material shall be highly conductive and should be non - polluting and safe for use near potable ground water systems. The backfill Material shall be carbon based, low resistance, non corrosive, highly conductive powdered material that improves grounding effectiveness, especially in areas of high soil resistivity such as rocky and sandy areas. This material shall be suitable to be installed in either slurry or dry form. The backfill material shall confirm to the following specifications: (20Kg Quantity) a) Shall be highly electrically conductive and non-soluble. b) Shall not leach into ground. c) Shall have a resistivity of less than 0.12 ohm meter d) Shall be compatible with all copper grounding systems. e) Shall contain a corrosion inhibitor to mitigate corrosion of copper f) Shall contain Sulphur less than 2%. g) Shall have pH value between 6.5 to 7.5 h) Shall be tested for loss of ignition test at 800° + Centigrade and the result shall be less than 5%. i) Shall not contain hazardous chemicals j) Shall not be affected by drought and shall be stable between -60˚ to +60˚ C temperature. k) Shall not depend on continuous presence of moisture for conductivity. StSt 316 grade clamp to terminate the load on earth electrode. Dimension- 160x35x3 mm., Poly plastic pit cover of material- Polymer Body & Cover, approx dimensions- 308 mm (L) x 308 mm (W) X 214 mm (H), Weight 2.5 kg (5.50 LBS). | 10.00 | Each | 0.00 | 24750.00 | 247500.00 | 24500.00 | 245000.00 | 245000.00 | JCC ENGINEERS PRIVATE LIMITED
| Total in Figures |  |  |  |  | 1844170.00 |  | 1893075.00
Lowest Amount Quoted BY: Vrinda Nano Technologies Pvt Ltd(1844170.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of Advance Lightning Arrestor and Grounding System for Terminal Building at Silchar Airport. Tender ID: 2022_AAI_115150_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Vrinda Nano Technologies Pvt Ltd | 1844170.00 | L1
| 2 | JCC ENGINEERS PRIVATE LIMITED | 1893075.00 | L2