## BoQ1
Government eProcurement System Created By: AJIYARAKATH RAZAK Created Date/Time: 27-Jun-2022 03:26 PM Tender Title: Construction of passenger terminal building along with office block at Juhu Airport. Tender ID: 2022_AAI_116823_1
Tender Inviting Authority:
Name of Work:Construction of Passenger Terminal Building along with Office Block at Juhu Airport.
Contract No: AAI/AGM(E-C)/E-NIT/JJ/TB
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | D B Infratech(GSTN-NA) |  | K N RAI(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Earth work in excavation by mechanical means (Hydraulic excavator)/manual means over areas (exceeding 30 cm in depth, 1.5 m in width as well as 10 sqm on plan) including getting out and disposal of excavated earth lead upto 50 m and lift upto 1.5 m, as directed by Engineer-in-charge. a)All kinds of soil | 561.00 | Cum |  | 250.00 | 140250.00 | 180.00 | 100980.00 | 100980.00 | K N RAI
2.00 | Extra for every additional lift of 1.5 m or part thereof in excavation / banking excavated or stacked materials. a) All kinds of soil | 271.00 | Cum |  | 25.00 | 6775.00 | 225.00 | 60975.00 | 6775.00 | D B Infratech
3.00 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m | 554.00 | Cum |  | 200.00 | 110800.00 | 150.00 | 83100.00 | 83100.00 | K N RAI
4.00 | Excavating, supplying and filling of local earth (including royalty) by mechanical transport upto a lead of 5km also including ramming and watering of the earth in layers not exceeding 20 cm in trenches, plinth, sides of foundation etc. complete. | 209.00 | Cum |  | 650.00 | 135850.00 | 600.00 | 125400.00 | 125400.00 | K N RAI
5.00 | Providing & laying stone soling for level / base course with stone of size 100mm to 250mm with screenings & filler materials(combination of aggrgate & stone dust etc.) including packing, ramming and dressing, etc. complete and as per direction of Engineer incharge.(Payment shall be made for compacted thickness only) | 406.00 | Cum |  | 1600.00 | 649600.00 | 1500.00 | 609000.00 | 609000.00 | K N RAI
6.00 | Providing and laying in position ready mixed or site batched design mix cement concrete for plain cement concrete work; using coarse aggregate and fine aggregate derived from natural sources, Portland Pozzolana/Ordinary Portland /Portland Slag cement, admixtures in recommended proportions as per IS: 9103 to accelerate / retard setting of concrete, to improve durability and workability without impairing strength; including pumping of concrete to site of laying, curing, carriage for all leads; but excluding the cost of centering, shuttering and finishing as per direction of the engineer-in-charge; for the following grades of concrete. Note: Extra cement up to 10% of the minimum specified cement content in design mix shall be payable separately. In case the cement content in design mix is more than 110% of the minimum specified cement content, the contractor shall have discretion to either re-design the mix or bear the cost of extra cement. All works upto plinth level : Concrete of M15 grade with minimum cement content of 240 kg /cum | 99.00 | Cum |  | 7500.00 | 742500.00 | 6000.00 | 594000.00 | 594000.00 | K N RAI
7.00 | Providing and laying in position ready mixed or site batched design mix cement concrete for plain cement concrete work; using coarse aggregate and fine aggregate derived from natural sources, Portland Pozzolana/Ordinary Portland /Portland Slag cement, admixtures in recommended proportions as per IS: 9103 to accelerate / retard setting of concrete, to improve durability and workability without impairing strength; including pumping of concrete to site of laying, curing, carriage for all leads; but excluding the cost of centering, shuttering and finishing as per direction of the engineer-in-charge; for the following grades of concrete. Note: Extra cement up to 10% of the minimum specified cement content in design mix shall be payable separately. In case the cement content in design mix is more than 110% of the minimum specified cement content, the contractor shall have discretion to either re-design the mix or bear the cost of extra cement. All works above plinth and upto floor V level a)Concrete of M15 grade with minimum cement content of 240 kg /cum | 191.00 | Cum |  | 10500.00 | 2005500.00 | 6200.00 | 1184200.00 | 1184200.00 | K N RAI
8.00 | Providing and laying damp-proof course 40mm thick with cement concrete 1:2:4 (1 cement : 2 coarse sand (zone-III): 4 graded stone aggregate 12.5mm nominal size) | 48.00 | Sqm |  | 760.00 | 36480.00 | 300.00 | 14400.00 | 14400.00 | K N RAI
9.00 | Providing & applying a coat of residual petroleum bitumen of grade of VG-10 of approved quality using 1.7kg per square metre on damp proof course after cleaning the surface with brushes and finally with apiece of cloth lightly soaked in kerosene oil. | 48.00 | Sqm |  | 340.00 | 16320.00 | 100.00 | 4800.00 | 4800.00 | K N RAI
10.00 | Centering and shuttering including strutting, propping etc. and removal of form for : a)Foundations, footings, bases of columns, etc. for mass concrete | 119.00 | Sqm |  | 600.00 | 71400.00 | 300.00 | 35700.00 | 35700.00 | K N RAI
11.00 | Centering and shuttering including strutting, propping etc. and removal of form for : a)Walls (any thickness) including attached pilasters, butteresses, plinth and string courses etc. | 188.00 | Sqm |  | 700.00 | 131600.00 | 500.00 | 94000.00 | 94000.00 | K N RAI
12.00 | Centering and shuttering including strutting, propping etc. and removal of form for : a)Suspended floors, roofs, landings, balconies and access platform | 332.00 | Sqm |  | 900.00 | 298800.00 | 520.00 | 172640.00 | 172640.00 | K N RAI
13.00 | Centering and shuttering including strutting, propping etc. and removal of form for : a)Lintels, beams, plinth beams, girders, bressumers and cantilevers | 500.00 | Sqm |  | 800.00 | 400000.00 | 530.00 | 265000.00 | 265000.00 | K N RAI
14.00 | Centering and shuttering including strutting, propping etc. and removal of form for : a)Columns, Pillars, Piers, Abutments, Posts and Struts | 232.00 | Sqm |  | 800.00 | 185600.00 | 560.00 | 129920.00 | 129920.00 | K N RAI
15.00 | Centering and shuttering including strutting, propping etc. and removal of form for : a)Stairs, (excluding landings) except spiral-staircases | 9.00 | Sqm |  | 900.00 | 8100.00 | 650.00 | 5850.00 | 5850.00 | K N RAI
16.00 | Extra for additional height in centering, shuttering where ever required with adequate bracing, propping etc., including cost of de-shuttering and decentering at all levels, over a height of 3.5 m, for every additional height of 1 metre or part thereof (Plan area to be measured). a)Suspended floors, roofs, landing, beams and balconies (Plan area to be measured) | 259.00 | Sqm |  | 240.00 | 62160.00 | 150.00 | 38850.00 | 38850.00 | K N RAI
17.00 | Providing and fixing Gl Clip in Metal Ceiling System of 600x600 mm module which includes providing and fixing 'C' wall angle of size 20x30x20 mm made of 0.5 mm thick pre painted steel along the perimeter of the room with help of nylon sleeves and wooden screws at 300 mm center to centre, suspending the main C carrier of size 10x38x10 mm made of G.I steel 0.7 mm thick from the soffit with help of soffit cleat 37x27x25x1.6 mm, rawl plugs of size 38x12 mm and C carrier suspension clip and main carrier bracket at 1000 mm c/c. Inverted triangle shaped Spring Tee having height of 24 mm and width of 34 mm made of Gl steel 0.45 mm thick is then fixed to the main C carrier and in direction perpendicular to it at 600 mm centers with help of suspension brackets. Wherever the main C carrier and spring T have to join, C carrier and spring T connectors have to be used. All sections to be galvanized @ 120 gms/sqm (both side inclusive), fixing with clip in tiles into spring T with : a)GI Metal Ceiling Clip in plain Beveled edge global white color tiles of size 600x600 and 0.5 mm thick with 25 mm height, made of G I sheet having galvanizing of 100 gms/ sqm (both sides inclusive) and electro statically polyester powder coated of thickness 60 microns (minimum), including factory painted after bending. | 377.00 | Sqm |  | 1500.00 | 565500.00 | 2550.00 | 961350.00 | 565500.00 | D B Infratech
18.00 | Designing ,Providing and fixing KALZIP/ KINGSPAN / GALAXY ROOFING RIGIDAL 65/400 “SELF SUPPORTED” CONCEALED FIX ALLUMINIUM STANDING SEAM ROOFING SYSTEM as per approved make IN 0.90 MM THICK AA 3004 aluminum ALLOY, comprising of the following layers.:For designing wind load calculation shall be as per IS 875 and pull out strength of fasteners for the roofing system to be submitted to Engineer in charge. Sound transmission class (STC) report shall be submitted from reputed NABL accredited labs. Contractor shall submit System warranty 15years and Installation warranty 10 year required i) Top Layer – 65/400 of Straight / Tapered / Curved profiled sheeting manufactured from Aluminium alloy AlMn 1Mg 1 as specified in BSEN 485-2 Quality AA 3004,minimum thickness of 0.9 mm STUCCO Embosed Finish on the exposed surface as approved by Engineer-in-Charge. Sheets are to be laid in single length (straight sheet)to meet the requirement of the building roof geometry . The profile should have 3micro ribs mini ribs to provide additional strength at the pan, and material test certificate (MTC) to be submitted. The support aluminium clip shall be manufactured from extruded aluminium alloy 6061 T6 in accordance with BSEN 485 part 2. Each aluminium clip shall be coupled with a 5mm thick black polyamide thermal barrier base pad. The material properties shall be as follows: tensile strength: minimum 200 N/mm2, Yield Stress: min 185 N/mm2 .Aluminum sheet to be laid in Single length to meet the requirements of the building geometry (straight sheet) and fixed on Aluminum clip and which is fixed to steel with SS-304 screws. ii)The insulation shall be 125 mm thick (laid in two layers of 75 & 50 mm fiberglass with minimum density 24 kg/m3 or Rockwool with minimum density 64 kg/m3 to achieve minimum U value of 0.26 W/m2 K,and minimum R- Value of insulation -3.70sqm-k/w as approved by Engineer-In-Charge. iii) Third Layer: Top Hats - Galvanised steel Top hats of min. thickness of 1.6mm and to be installed over the VCL, cement board, with min. yield strength of 240 Mpa and to be fixed with Steel fasteners. iv) Fourth layer : Vapour Control Layer -) Scrim reinforced Polyethylene film heavy duty type Vapour control layer should be laid providing a minimum water Vapour resistance of 336MNs/g and water permeability of 0.61g/m2/day” having specific weight of 200 gsm. v) Fifth Layer: Cement Board/bision Board - One layer of 10mm thick cement/bision board layer to be laid over GI bracket. vi) Sixth Layer: Brackets - Galvanised steel bracket of min. thickness 2mm to be provided over liner, with min. yield strength of 240 Mpa and to be fixed with SS Steel fasteners. vii) Seventh Layer - Bottom sheet – Trapezoidal bare Galvalume 0.50mm thick profile sheet of 980-1050 mm effective cover width and 28-35 mm height ribs with pan at 200-250 mm centre-to-centre. The feed material is manufactured out of nominal 0.50 mm (BMT), Hi-strength steel with min. 550 MPa yield strength. metallic hot dip coated with Aluminium-Zinc alloy (55% Aluminium, 45% Zinc) as per AS 1397 - Zincalume AZ150 (Min. 150 gms/sq.mt total on both sides) Fixed to the purlins with self drilling screws at 500mm spacing. With all required system accessories such as Aluminium clips, flashings, eaves, gables, etc., as per shop drawings, specifications and as directed by the Engineer-in-Charge. viii) The entire Double skin system is installed over the structure purlin. The measurement shall be based on finished/covered surface area. The contractor shall prepare the shop drawings based on the drawings supplied by the Engineer-in-charge for approval. The rate shall includes for flashings, sealants and work shall carried out by specialized agency. ix) Item includes supplying, installation and fixing of profiled aluminum sheeting including cost of system accessories insulation, vapour barrier, liner sheet,cement board, fasteners, gaskets, brackets, screws, rivets, sealants, flashing at all location including sky light , welding if any etc,grattings, inner closure fillers, fixtures, all machineries and all taxes, i.e., custom duty, excluding GST etc etc., complete as desired. The above work is to be carried out by a specialized agency as per approved by the Engineer-in-Charge. KEY ROOF PERFORMANCES: The thermal U value of the roof built-up shall be 0.261 W/mK. Acoustic requirement: Sound Transmission class (STC) = 39 ±3 . | 180.00 | Sqm |  | 5000.00 | 900000.00 | 11500.00 | 2070000.00 | 900000.00 | D B Infratech
19.00 | Providing and fixing 15 cm wide, 45 cm overall semi-circular plain G.S. sheet gutter with iron brackets 40x3mm size, bolts, nuts and washers etc., including making necessary connections with rain water pipes complete. a)0.80 mm thick with zinc coating not less than 275 gm/m² | 60.00 | Metre |  | 1600.00 | 96000.00 | 1200.00 | 72000.00 | 72000.00 | K N RAI
20.00 | Providing and laying autoclaved aerated cement blocks masonry with 100 mm thick AAC blocks in super structure above plinth level up to floor V level in cement mortar 1:4 (1 cement : 4 coarse sand ). The rate includes providing and placing in position 2 Nos 6 mm dia M.S. bars at every third course of masonry work. | 105.00 | Cum |  | 11500.00 | 1207500.00 | 7500.00 | 787500.00 | 787500.00 | K N RAI
21.00 | 12 mm cement plaster of mix : a)1:4 (1 cement: 4 coarse sand) | 749.00 | Sqm |  | 625.00 | 468125.00 | 400.00 | 299600.00 | 299600.00 | K N RAI
22.00 | 6 mm cement plaster of mix : 1:3 (1 cement : 3 fine sand) | 284.00 | Sqm |  | 550.00 | 156200.00 | 380.00 | 107920.00 | 107920.00 | K N RAI
23.00 | 18 mm cement plaster in two coats under layer 12 mm thick cement plaster 1:5 (1 cement : 5 coarse sand) finished with a top layer 6 mm thick cement plaster 1:6 (1 cement : 6 fine sand). | 450.00 | Sqm |  | 700.00 | 315000.00 | 450.00 | 202500.00 | 202500.00 | K N RAI
24.00 | Providing and applying plaster of paris putty of 2 mm thickness over plastered surface to prepare the surface even and smooth complete. | 1244.00 | Sqm |  | 150.00 | 186600.00 | 125.00 | 155500.00 | 155500.00 | K N RAI
25.00 | Finishing walls with textured exterior paint of required shade : a)New work (Two or more coats applied @ 3.28 ltr/10 sqm) over and including priming coat of exterior primer applied @ 2.20kg/10 sqm | 450.00 | Sqm |  | 180.00 | 81000.00 | 100.00 | 45000.00 | 45000.00 | K N RAI
26.00 | Wall painting with premium acrylic emulsion paint of interior grade, having VOC (Volatile Organic Compound ) content less than 50 grams/ litre of approved brand and manufacture, including applying additional coats wherever required to achieve even shade and colour. a)Two coats | 1326.00 | Sqm |  | 280.00 | 371280.00 | 120.00 | 159120.00 | 159120.00 | K N RAI
27.00 | French spirit polishing : a) Two or more coats on new works including a coat of wood filler | 37.00 | Sqm |  | 200.00 | 7400.00 | 750.00 | 27750.00 | 7400.00 | D B Infratech
28.00 | Providing and laying in position ready mixed or site batched design mix cement concrete for reinforced cement concrete work; using coarse aggregate and fine aggregate derived from natural sources, Portland Pozzolana / Ordinary Portland /Portland Slag cement, admixtures in recommended proportions as per IS: 9103 to accelerate / retard setting of concrete, to improve durability and workability without impairing strength; including pumping of concrete to site of laying, curing, carriage for all leads; but excluding the cost of centering, shuttering, finishing and reinforcement as per direction of the engineer-in-charge; for the following grades of concrete. Note: Extra cement up to 10% of the minimum specified cement content in design mix shall be payable separately. In case the cement content in design mix is more than 110% of the specified minimum cement content, the contractor shall have discretion to either re-design the mix or bear the cost of extra cement. a) All works upto plinth level Concrete of M30 grade with minimum cement content of 350 kg /cum | 75.00 | Cum |  | 10500.00 | 787500.00 | 7850.00 | 588750.00 | 588750.00 | K N RAI
29.00 | Providing and laying in position ready mixed or site batched design mix cement concrete for reinforced cement concrete work; using coarse aggregate and fine aggregate derived from natural sources, Portland Pozzolana / Ordinary Portland /Portland Slag cement, admixtures in recommended proportions as per IS: 9103 to accelerate / retard setting of concrete, to improve durability and workability without impairing strength; including pumping of concrete to site of laying, curing, carriage for all leads; but excluding the cost of centering, shuttering, finishing and reinforcement as per direction of the engineer-in-charge; for the following grades of concrete. Note: Extra cement up to 10% of the minimum specified cement content in design mix shall be payable separately. In case the cement content in design mix is more than 110% of the specified minimum cement content, the contractor shall have discretion to either re-design the mix or bear the cost of extra cement. All works above plinth level upto floor V level Concrete of M30 grade with minimum cement content of 350 kg /cum | 81.00 | Cum |  | 11000.00 | 891000.00 | 7800.00 | 631800.00 | 631800.00 | K N RAI
30.00 | Steel reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete upto plinth level. a)Thermo-Mechanically Treated bars of grade Fe-500D or more. | 5605.00 | Kg |  | 90.00 | 504450.00 | 81.00 | 454005.00 | 454005.00 | K N RAI
31.00 | Steel reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete above plinth level. a) Thermo-Mechanically Treated bars of grade Fe-500D or more. | 6451.00 | Kg |  | 91.00 | 587041.00 | 81.00 | 522531.00 | 522531.00 | K N RAI
32.00 | Steel work in built up tubular (round, square or rectangular hollow tubes etc.) trusses etc., including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer, including welding and bolted with special shaped washers etc. complete. a)Hot finished welded type tubes | 6380.00 | Kg |  | 135.00 | 861300.00 | 120.00 | 765600.00 | 765600.00 | K N RAI
33.00 | Design supply & installation of suspended Spider Glazing system designed to withstand the wind pressure as per IS 875 (Part-III). The Suspended System held with Spider Fittings of SS-316 Grade Steel of approved manufacturer with glass panel having 12 mm thick clear toughened glass held together with SS- 316 Grade Stainless steel Spider & bolt assembly with laminated glass fins 21 mm thick. The Glass fins and glass panel assembly shall be connected to Slab/ beams by means of SS- 316 Grade stainless steel brackets & Anchor bolts and at the bottom using SS channel of 50x25x2mm using fastener & anchor bolts, non staining weather sealants of approved make, Teflon/ nylon bushes and separators to prevent bi-metallic contacts, all complete to perform as per specification and approved drawings. The complete system to be designed to accommodate thermal expansion & seismic movements etc. The joints between glass panels (6 to 8 mm) and gaps at the perimeter & in U channel of the assembly to be filled with non staining weather sealant, so as to make the entire system fully water proof & dust proof. The rate shall include all design, Engineering and shop drawing including approval from structural designer, labour, T&P, scaffolding, other incidental charges including wastage, enabling temporary services all fitting fixers nut bolts, washer, Buffer plates, fastener, purpose of payment, actual elevation area of Glazing including thickness of joints and the portion of Glass panel inside the SS channel shall be measured. | 110.00 | Sqm |  | 4300.00 | 473000.00 | 9000.00 | 990000.00 | 473000.00 | D B Infratech
34.00 | Providing and fixing 12 mm thick frameless toughened glass door shutter of approved brand and manufacture, including providing and fixing top & bottom pivot & double action hydraulic floor spring type fixing arrangement and making necessary holes etc. for fixing required door fittings, all complete as per direction of Engineer-in charge (Door handle, lock and stopper etc.to be paid separately). | 31.00 | Sqm |  | 5225.00 | 161975.00 | 3800.00 | 117800.00 | 117800.00 | K N RAI
35.00 | Designing, fabricating, testing, installing and fixing in position Curtain Wall with Aluminium Composite Panel Cladding, with open grooves for linear as well as curvilinear portions of the building , for all heights and all levels etc. including: (a) Structural analysis & design and preparation of shop drawings for pressure equalisation or rain screen principle as required, proper drainage of water to make it watertight including checking of all the structural and functional design. (b) Providing, fabricating and supplying and fixing panels of aluminium composite panel cladding in pan shape in metalic colour of approved shades made out of 4mm thick aluminium composite panel material consisting of 3mm thick FR grade mineral core sandwiched between two Aluminium sheets (each 0.5mm thick). The aluminium composite panel cladding sheet shall be coil coated, with Kynar 500 based PVDF / Lumiflon based fluoropolymer resin coating of approved colour and shade on face # 1 and polymer (Service) coating on face # 2 as specified using stainless steel screws, nuts, bolts, washers, cleats, weather silicone sealant, backer rods etc. (c) The fastening brackets of Aluminium alloy 6005 T5 / MS with Hot Dip Galvanised with serrations and serrated washers to arrest the wind load movement, fasteners, SS 316 Pins and anchor bolts of approved make in SS 316, Nylon separators to prevent bi-metallic contacts all complete required to perform as per specification and drawing The item includes cost of all material & labour component, the cost of all mock ups at site, cost of all samples of the individual components for testing in an approved laboratory, field tests on the assembled working curtain wall with aluminium composite panel cladding, cleaning and protection of the curtain wall with aluminium composite panel cladding till the handing over of the building for occupation. Base frame work for ACP cladding is payable under the relevant aluminium item.s The Contractor shall provide curtain wall with aluminium composite panel cladding, having all the performance characteristics all complete , as per the Architectural drawings, as per item description, as specified, as per the approved shop drawings and as directed by the Engineer-in-Charge. However, for the purpose of payment, only the actual area on the external face of the curtain wall with Aluminum Composite Panel Cladding (including width of groove) shall be measured in sqm. up to two decimal places. | 48.00 | Sqm |  | 5225.00 | 250800.00 | 4500.00 | 216000.00 | 216000.00 | K N RAI
36.00 | Providing and fixing 18 mm thick gang saw cut, mirror polished, premoulded and prepolished, machine cut for kitchen platforms, vanity counters, window sills, facias and similar locations of required size, approved shade, colour and texture laid over 20 mm thick base cement mortar 1:4 (1 cement : 4 coarse sand), joints treated with white cement, mixed with matching pigment, epoxy touch ups, including rubbing, curing, moulding and polishing to edges to give high gloss finish etc. complete at all levels. Granite of any colour and shade a)Area of slab upto 0.50 sqm | 4.00 | Sqm |  | 4560.00 | 18240.00 | 4000.00 | 16000.00 | 16000.00 | K N RAI
37.00 | Providing and fixing 18 mm thick gang saw cut, mirror polished, premoulded and prepolished, machine cut for kitchen platforms, vanity counters, window sills, facias and similar locations of required size, approved shade, colour and texture laid over 20 mm thick base cement mortar 1:4 (1 cement : 4 coarse sand), joints treated with white cement, mixed with matching pigment, epoxy touch ups, including rubbing, curing, moulding and polishing to edges to give high gloss finish etc. complete at all levels. a)Area of slab over 0.50 sqm | 87.00 | Sqm |  | 4560.00 | 396720.00 | 3400.00 | 295800.00 | 295800.00 | K N RAI
38.00 | Providing and fixing aluminium work for doors, windows, ventilators and partitions with extruded built up standard tubular sections/ appropriate Z sections and other sections of approved make conforming to IS: 733 and IS: 1285, fixing with dash fasteners of required dia and size, including necessary filling up the gaps at junctions, i.e. at top, bottom and sides with required EPDM rubber/ neoprene gasket etc. Aluminium sections shall be smooth, rust free, straight, mitred and jointed mechanically wherever required including cleat angle, Aluminium snap beading for glazing / paneling, C.P. brass / stainless steel screws, all complete as per architectural drawings and the directions of Engineer-in-charge. (Glazing, paneling and dash fasteners to be paid for separately) : For fixed portion a)Anodised aluminium (anodised transparent or dyed to required shade according to IS: 1868, Minimum anodic coating of grade AC 15) | 200.00 | Kg |  | 525.00 | 105000.00 | 630.00 | 126000.00 | 105000.00 | D B Infratech
39.00 | For shutters of doors, windows & ventilators including providing and fixing hinges/ pivots and making provision for fixing of fittings wherever required including the cost of EPDM rubber / neoprene gasket required (Fittings shall be paid for separately) a) Anodised aluminium (anodised transparent or dyed to required shade according to IS: 1868, Minimum anodic coating of grade AC 15) | 250.00 | Kg |  | 570.00 | 142500.00 | 650.00 | 162500.00 | 142500.00 | D B Infratech
40.00 | Providing and fixing glazing in aluminium door, window, ventilator shutters and partitions etc. with EPDM rubber / neoprene gasket etc. complete as per the architectural drawings and the directions of engineer-in-charge . (Cost of aluminium snap beading shall be paid in basic item): a) With float glass panes of 5 mm thickness (weight not less than 12.50 kg/ sqm) | 31.00 | Sqm |  | 6175.00 | 191425.00 | 1400.00 | 43400.00 | 43400.00 | K N RAI
41.00 | Filling the gap in between aluminium frame & adjacent RCC/ Brick/ Stone work by providing weather silicon sealant over backer rod of approved quality as per architectural drawings and direction of Engineer-in-charge complete a) Upto 5mm depth and 5 mm width | 102.00 | Metre |  | 240.00 | 24480.00 | 100.00 | 10200.00 | 10200.00 | K N RAI
42.00 | Providing and fixing anodised aluminium grill (anodised transparent or dyed to required shade according to IS: 1868 with minimum anodic coating of grade AC 15) of approved design/pattern, with approved standard section and fixed to the existing window frame with C.P. brass/ stainless steel screws @ 200 mm centre to centre, including cutting the grill to proper opening size for fixing and operation of handles and fixing approved anodised aluminium standard section around the opening, all complete as per requirement and direction of Engineer-in-charge. (Only weight of grill to be measured for payment). | 93.00 | Kg |  | 525.00 | 48825.00 | 700.00 | 65100.00 | 48825.00 | D B Infratech
43.00 | Providing and fixing zinc alloyed (white powder coated) touch lock for uPVC sliding window with necessary screws etc. complete. | 30.00 | Each |  | 525.00 | 15750.00 | 160.00 | 4800.00 | 4800.00 | K N RAI
44.00 | Providing and fixing steel roller for uPVC sliding door with necessary screws etc. complete. | 51.00 | Each |  | 340.00 | 17340.00 | 150.00 | 7650.00 | 7650.00 | K N RAI
45.00 | Providing and laying integral cement based water proofing treatment including preparation of surface as required for treatment of roofs, balconies, terraces etc consisting of following operations: (a) Applying a slurry coat of neat cement using 2.75 kg/sqm of cement admixed with water proofing compound conforming to IS. 2645 and approved by Engineer-in-charge over the RCCslab including adjoining walls upto 300 mm height including cleaning the surface before treatment. (b) Laying brick bats with mortar using broken bricks/brick bats 25 mm to 115 mm size with 50% of cement mortar 1:5 (1 cement : 5 coarse sand) admixed with water proofing compound conforming to IS : 2645 and approved by Engineer-in-charge over 20 mm thick layer of cement mortar of mix 1:5 (1 cement :5 coarse sand ) admixed with water proofing compound conforming to IS : 2645 and approved by Engineer-in-charge to required slope and treating similarly the adjoining walls upto 300 mm height including rounding of junctions of walls and slabs. (c) After two days of proper curing applying a second coat of cement slurry using 2.75 kg/ sqm of cement admixed with water proofing compound conforming to IS : 2645 and approved by Engineer in-charge. (d) Finishing the surface with 20 mm thick jointless cement mortar of mix 1:4 (1 cement :4 coarse sand) admixed with water proofing compound conforming to IS : 2645 and approved by Engineer in-charge including laying glass fibre cloth of approved quality in top layer of plaster and finally finishing the surface with trowel with neat cement slurry and making pattern of 300x300 mm square 3 mm deep. (e) The whole terrace so finished shall be flooded with water for a minimum period of two weeks for curing and for final test.“All above operations to be done in order and as directed and specified by the Engineer-in-Charge a) With average thickness of 120 mm and minimum thickness at khurra as 65 mm. | 348.00 | Sqm |  | 1570.00 | 546360.00 | 1400.00 | 487200.00 | 487200.00 | K N RAI
46.00 | Providing and laying integral cement based treatment for water proofing on horizontal surface at all depth below ground level for under ground structures as directed by Engineer-in-Charge and consisting of : (i) Ist layer of 22 mm to 25 mm thick approved and specified rough stone slab over a 25 mm thick base of cement mortar 1:3 (1 cement : 3 coarse sand) mixed with water proofing compound conforming to IS:2645 in the recommended proportion over the leveling course (leveling course to be paid separately). Joints sealed and grouted with cement slurry mixed with water proofing compound. (ii) 2nd layer of 25 mm thick cement mortar 1:3 (1 cement: 3 coarse sand) mixed with water proofing compound in recommended proportions. (iii) Finishing top with stone aggregate of 10 mm to 12 mm nominal size spreading @ 8 cudm/sqm thoroughly embedded in the 2nd layer. a) Using rough kota stone. | 68.00 | Sqm |  | 1520.00 | 103360.00 | 1410.00 | 95880.00 | 95880.00 | K N RAI
47.00 | Providing and laying integral cement based treatment for water proofing on the vertical surface by fixing specified stone slab 22 mm to 25 mm thick with cement slurry mixed with water proofing compound conforming to IS:2645 in recommended proportions with a gap of 20 mm (minimum) between stone slabs and the receiving surfaces and filling the gaps with neat cement slurry mixed with water proofing compound and finishing the exterior of stone slab with cement mortar 1:3 (1 cement : 3 coarse sand) 20 mm thick with neat cement punning mixed with water proofing compound in recommended proportion complete at all levels and as directed by Engineer-in-charge : a) Using rough Kota stone | 94.00 | Sqm |  | 1520.00 | 142880.00 | 1500.00 | 141000.00 | 141000.00 | K N RAI
48.00 | Making khurras 45x45 cm with average minimum thickness of 5 cm cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate of 20 mm nominal size) over P.V.C. sheet 1 m x1 m x 400 micron, finished with 12 mm cement plaster 1:3 (1 cement : 3 coarse sand) and a coat of neat cement, rounding the edges and making and finishing the outlet complete | 22.00 | Each |  | 430.00 | 9460.00 | 300.00 | 6600.00 | 6600.00 | K N RAI
49.00 | Preparation and consolidation of sub grade with power road roller of 8 to 12 tonne capacity after excavating earth to an average of 22.5 cm depth, dressing to camber and consolidating with road roller including making good the undulations etc. and re-rolling the sub grade and disposal of surplus earthwith lead upto 50 metres. | 2880.00 | Sqm |  | 100.00 | 288000.00 | 50.00 | 144000.00 | 144000.00 | K N RAI
50.00 | Providing and laying graded granular material (moorum) in layers not exceeding 20cm (loose) in thickness (each layer) and as directed by the Engineer-in-charge. Breaking clods, watering, consolidating each layers with power road roller 8-10 tonne, under optimum moisture content to give density not less than that specified of the maximum modified standard proctor density at OMC including levelling, fine dressing to the required camber, grade and slope etc. complete. (payment to be made for the compacted quantity only). | 830.00 | Cum |  | 950.00 | 788500.00 | 900.00 | 747000.00 | 747000.00 | K N RAI
51.00 | Construction of granular sub-base by providing close graded Material conforming to specifications, mixing in a mechanical mix plant at OMC, carriage of mixed material by tippers to work site, for all leads lifts, spreading in uniform layers of specified thickness with motor grader on prepared surface and compacting with vibratory power roller to achieve the desired density, complete as per specifications and directions of Engineer-in-Charge. a) With material conforming to Grade-III (size range 26.5 mm to 0.075 mm ) having CBR Value-20 | 435.00 | Cum |  | 2200.00 | 957000.00 | 2500.00 | 1087500.00 | 957000.00 | D B Infratech
52.00 | Providing, laying, spreading and compacting graded stone aggregate (size range 53 mm to 0.075 mm ) to wet mix macadam (WMM) specification including premixing the material with water at OMC in for all leads & lifts, laying in uniform layers with mechanical paverfinisher in sub- base / base course on well prepared surface and compacting with vibratory roller of 8 to 10 tonne capacity to achievethe desired density, complete as per specifications and directions of Engineer-in-Charge. | 435.00 | Cum |  | 4500.00 | 1957500.00 | 2600.00 | 1131000.00 | 1131000.00 | K N RAI
53.00 | Providing and applying tack coat using hot straight run bitumen of grade VG - 10,including heating the bitumen, spraying the bitumen with mechanically operated spray unit fitted on bitumen boiler, cleaning and preparing the existing road surface as per specifications : a) On W.M.M. @ 0.75 Kg / sqm | 2870.00 | Sqm |  | 115.00 | 330050.00 | 90.00 | 258300.00 | 258300.00 | K N RAI
54.00 | Providing and applying tack coat using hot straight run bitumen of grade VG - 10,including heating the bitumen, spraying the bitumen with mechanically operated spray unit fitted on bitumen boiler, cleaning and preparing the existing road surface as per specifications : b) On bituminous surface @ 0.50 Kg / sqm | 2870.00 | Sqm |  | 100.00 | 287000.00 | 80.00 | 229600.00 | 229600.00 | K N RAI
55.00 | Providing and laying bituminous macadam using crushed stone aggregates of specified grading premixed with bituminous binder , transported to site by tippers, laid over a previously prepared surface with paver finisher equiped with electronic sensor to the required grade, level and alignment and rolling with smooth wheeled, vibratory and tandem rollers as per specifications to achieve the desired compaction and density , complete as per specificatons and directions of Engineer-in-Charge.: a) 50 to 100 mm average compacted thickness with bitumen of grade VG-30 @ 3.50% (percentage by weight of total mix) prepared in Drum Type Hot Mix Plant of 60-90 TPH capacity | 220.00 | Cum |  | 11500.00 | 2530000.00 | 10500.00 | 2310000.00 | 2310000.00 | K N RAI
56.00 | Providing and laying Bituminous concrete using crushed stone aggregates of specified grading, premixed with bituminous binder and filler, transporting the hot mix to work site by tippers, laying with paver finisher equiped with electronic sensor to the required grade, level and alignment and rolling with smooth wheeled, vibratory and tandem rollers to achieve the desired compaction and density as per specification, complete and as per directions of Engineer-in-Charge. a) 40/50 mm compacted thickness with bitumen of grade VG-30 @ 5.5% (percentage by weight of total mix) and lime filler @ 3% (percentage by weight of Aggregate) prepared in drum Type Hot Mix Plant of 60-90 TPH capacity. | 66.00 | Cum |  | 11500.00 | 759000.00 | 16000.00 | 1056000.00 | 759000.00 | D B Infratech
57.00 | Painting road surface marking with adequate nos of coats to give uniform finish with ready mixed road marking paint conforming to IS : 164, on bituminous surface in white/yellow shade, including cleaning the surface of all dirt, scales, oil, grease and foreign material etc. complete. a) New work (Two or more coats) | 175.89 | Sqm |  | 715.00 | 125761.35 | 450.00 | 79150.50 | 79150.50 | K N RAI
58.00 | Providing and laying at or near ground level factory made kerb stone of M-25 grade cement concrete in position to the required line, level and curvature, jointed with cement mortar 1:3 (1 cement: 3 coarse sand), including making joints with or without grooves (thickness of joints except at sharp curve shall not to more than 5mm), including making drainage opening wherever required complete etc. as per direction of Engineer-in-charge (length of finished kerb edging shall be measured for payment). (Precast C.C. kerb stone shall be approved by Engineer-in-charge). | 37.00 | Cum |  | 10000.00 | 370000.00 | 8000.00 | 296000.00 | 296000.00 | K N RAI
59.00 | Providing and laying 60mm thick faciory made cement concrete interlocking paver block of M -30 grade made by block making machine with strong vibratory compaction, of approved size, design & shape, laid in required colour and pattern over and including 50mm thick compacted bed of coarse sand, filling the joints with line sand etc. all complete as per the direction of Engineer-in-charge. | 1230.00 | Sqm |  | 1050.00 | 1291500.00 | 750.00 | 922500.00 | 922500.00 | K N RAI
60.00 | Providing and fixing stainless steel ( Grade 304) railing made of Hollow tubes, channels, plates etc., including welding, grinding, buffing, polishing and making curvature (wherever required) and fitting the same with necessary stainless steel nuts and bolts complete, i/c fixing the railing with necessary accessories & stainless steel dash fasteners , stainless steel bolts etc., of required size, on the top of the floor or the side of waist slab with suitable arrangement as per approval of Engineer-in charge, (for payment purpose only weight of stainless steel members shall be considered excluding fixing accessories such as nuts, bolts, fasteners etc.). | 1000.00 | Kg |  | 450.00 | 450000.00 | 650.00 | 650000.00 | 450000.00 | D B Infratech
61.00 | Providing and laying Vitrified tiles in floor with different sizes (thickness to be specified by the manufacturer), with water absorption less than 0.08% and conforming to IS:15622, of approved brand & manufacturer, in all colours and shade, laid with cement based high polymer modified quick set tile adhesive (water based) conforming to IS : 15477, in average 6 mm thickness, including grouting of joints (Payment for grouting of joints to be made separately). a) Size of Tile 1000x1000 mm | 376.57 | Sqm |  | 1710.00 | 643934.70 | 1500.00 | 564855.00 | 564855.00 | K N RAI
62.00 | Providing and laying Vitrified tiles in different sizes (thickness to be specified by the manufacturer), with water absorption less than 0.08% and conforming to IS: 15622, of approved brand & manufacturer, in all colours and shade, in skirting, riser of steps, laid with cement based high polymer modified quick set tile adhesive (water based) conforming to IS: 15477, in average 6 mm thickness, including grouting of joints (Payment for grouting of joints to be made separately). a) Size of Tile 1000x1000 mm | 12.16 | Sqm |  | 1710.00 | 20793.60 | 1650.00 | 20064.00 | 20064.00 | K N RAI
63.00 | Providing and fixing Ist quality ceramic glazed wall tiles conforming to IS: 15622 (thickness to be specified by the manufacturer), of approved make, in all colours, shades except burgundy, bottle green, black of any size as approved by Engineer-in-Charge, in skirting, risers of steps and dados, over 12 mm thick bed of cement mortar 1:3 (1 cement : 3 coarse sand) and jointing with grey cement slurry @ 3.3kg per sqm, including pointing in white cement mixed with pigment of matching shade complete. | 168.00 | Sqm |  | 1520.00 | 255360.00 | 770.00 | 129360.00 | 129360.00 | K N RAI
64.00 | Providing wood work in frames of doors, windows, clerestory windows and other frames, wrought framed and fixed in position with hold fast lugs or with dash fasteners of required dia & length ( hold fast lugs or dash fastener shall be paid for separately). a) Second class teak wood | 1.00 | Cum |  | 190000.00 | 190000.00 | 200000.00 | 200000.00 | 190000.00 | D B Infratech
65.00 | Providing and fixing ISI marked flush door shutters conforming to IS : 2202 (Part I) decorative type, core of block board construction with frame of 1st class hard wood and well matched teak 3 ply veneering with vertical grains or cross bands and face veneers on both faces of shutters a) 35 mm thick including ISI marked Stainless Steel butt hinges with necessary screws | 12.00 | Sqm |  | 5225.00 | 62700.00 | 4000.00 | 48000.00 | 48000.00 | K N RAI
66.00 | Providing and fixing aluminium tower bolts, ISI marked, anodised (anodic coating not less than grade AC 10 as per IS : 1868 ) transparent or dyed to required colour or shade, with necessary screws etc. complete : a) 300x10 mm | 10.00 | Each |  | 430.00 | 4300.00 | 120.00 | 1200.00 | 1200.00 | K N RAI
67.00 | Providing and fixing aluminium extruded section body tubular type universal hydraulic door closer (having brand logo with ISi, IS : 3564, embossed on the body, door weight upto 36 kg to 80 kg and door width from 701 mm to 1000 mm), with double speed adjustment with necessary accessories and screws etc. complete. | 13.00 | Each |  | 2660.00 | 34580.00 | 1000.00 | 13000.00 | 13000.00 | K N RAI
68.00 | Providing and fixing bright finished brass handles with screws etc. complete: a) 125 mm | 26.00 | Each |  | 810.00 | 21060.00 | 210.00 | 5460.00 | 5460.00 | K N RAI
69.00 | Providing and fixing bright finished brass hanging type floor door stopper with necessary screws, etc. complete. | 10.00 | Each |  | 710.00 | 7100.00 | 100.00 | 1000.00 | 1000.00 | K N RAI
70.00 | Providing and fixing chromium plated brass 100 mm mortice latch and lock with 6 levers and a pair of lever handles of approved quality with necessary screws etc. complete. | 10.00 | Each |  | 2660.00 | 26600.00 | 750.00 | 7500.00 | 7500.00 | K N RAI
71.00 | Extra for providing lipping with 2nd class teak wood battens 25 mm minimum depth on all edges of flush door shutters (over all area of door shutter to be measured). | 12.00 | Sqm |  | 4275.00 | 51300.00 | 350.00 | 4200.00 | 4200.00 | K N RAI
72.00 | Providing 40x5 mm flat iron hold fast 40 cm long including fixing to frame with 10 mm diameter bolts, nuts and wooden plugs and embedding in cement concrete block 30x10x15cm 1:3:6 mix (1 cement : 3 coarse sand : 6 graded stone aggregate 20mm nominal size). | 52.00 | Each |  | 190.00 | 9880.00 | 150.00 | 7800.00 | 7800.00 | K N RAI
73.00 | Providing and fixing partition upto ceiling height consisting of G.I. frame and required board, including providing and fixing of frame work made of special section power pressed/ roll form G.I. sheet with zinc coating of 120 gms/ sqm(both side inclusive), consisting of floor and ceiling channel 50mm wide having equal flanges of 32 mm and 0.50 mm thick, fixed to the floor and ceiling at the spacing of 610 mm centre to centre with dash fastener of 12.5 mm dia meter 50 mm length or suitable anchor fastener or metal screws with nylon plugs and the studs 48 mm wide having one flange of 34 mm and other flange 36 mm and 0.50 mm thick fixed vertically within flanges of floor and ceiling channel and placed at a spacing of 610 mm centre to centre by 6 mm dia bolts and nuts, including fixing of studs along both ends of partition fixed flush to wall with suitable anchor fastener or metal screws with nylon plugs at spacing of 450 mm centre to centre, and fixing of boards to both side of frame work by 25 mm long dry wall screws on studs, floor and ceiling channels at the spacing of 300 mm centre to centre. The boards are to be fixed to the frame work with joints staggered to avoid through cracks, Galvanised M.S. fixing channel of 99 mm width (0.9 mm thick having two flanges of 9.5 mm each with zinc coating of 120 gms/sqm(both side inclusive)) to be provided at the horizontal joints of two boards, fixed to the studs using metal to metal flat head screws, including jointing and finishing to a flush finish with recommended jointing compound, jointing tape, angle beads at corners (25 mm x 25 mm x 0.5 mm), joint finisher and two coats of primer suitable for board as per manufacture's specification and direction of engineer in charge all complete a) 75 mm overall thickness partition with 12.5 mm thick double skin fire rated Glass Reinforced Gypsum (GRG) plaster board conforming to IS: 2095: (part 3) : 1996 (Board with BIS certification marks) | 147.00 | Sqm |  | 1190.00 | 174930.00 | 1450.00 | 213150.00 | 174930.00 | D B Infratech
74.00 | Providing and fixing bright finished brass parliamentary hinges with necessary screws etc. complete : a) 150x125x27x5 mm | 39.00 | Each |  | 430.00 | 16770.00 | 400.00 | 15600.00 | 15600.00 | K N RAI
75.00 | Providing and fixing Fiber Glass Reinforced plastic (FRP) Door Frames of cross-section 90 mm x 45 mm having single rebate of 32 mm x 15 mm to receive shutter of 30 mm thickness. The laminate shall be moulded with fire resistant grade unsaturated polyester resin and chopped mat. Door frame laminate shall be 2mm thick and shall be filled with suitable wooden block in all the three legs. The frame shall be covered with fiber glass from all sides. M.S. stay shall be provided at the bottom to steady the frame. | 16.00 | Metre |  | 4275.00 | 68400.00 | 575.00 | 9200.00 | 9200.00 | K N RAI
76.00 | Providing and fixing to existing door frames a) 30 mm thick Fiberglass Reinforced Plastic (F.R.P.) flush door shutter in different plain and wood finish made with fire retardant grade unsaturated polyester resin, moulded to 3 mm thick FRP laminate all around, with suitable wooden blocks inside at required places for fixing of fittings and polyurethane foam (PUF)/Polystyrene foam to be used as filler material throughout the hollow panel, casted monolithically with testing parameters of F.R.P. laminate conforming to table - 3 of IS: 14856, complete as per direction of Engineer-in-charge. | 8.00 | Sqm |  | 5225.00 | 41800.00 | 4000.00 | 32000.00 | 32000.00 | K N RAI
77.00 | Providing and fixing on wall face unplasticised Rigid PVC rain water pipes conforming to IS : 13592 Type A, including jointing with seal ring conforming to IS : 5382, leaving 10 mm gap for thermal expansion, (i) Single socketed pipes. a) 110 mm diameter | 128.00 | Metre |  | 710.00 | 90880.00 | 325.00 | 41600.00 | 41600.00 | K N RAI
78.00 | Providing and laying non-pressure NP2 class (light duty) R.C.C. pipes with collars jointed with stiff mixture of cement mortar in the proportion of 1:2 (1 cement : 2 fine sand) including testing of joints etc. complete : a)300 mm dia. R.C.C. pipe | 50.00 | Metre |  | 1710.00 | 85500.00 | 1100.00 | 55000.00 | 55000.00 | K N RAI
79.00 | Providing and laying non-pressure NP2 class (light duty) R.C.C. pipes with collars jointed with stiff mixture of cement mortar in the proportion of 1:2 (1 cement : 2 fine sand) including testing of joints etc. complete : a) 450 mm dia. R.C.C. pipe | 50.00 | Metre |  | 2375.00 | 118750.00 | 1600.00 | 80000.00 | 80000.00 | K N RAI
80.00 | Constructing brick masonry manhole in cement mortar 1:4 ( 1 cement : 4 coarse sand ) with R.C.C. top slab with 1:1.5:3 mix (1 cement : 1.5 coarse sand (zone- III) : 3 graded stone aggregate 20 mm nominal size), foundation concrete 1:4:8 mix (1 cement : 4 coarse sand (zone- III) : 8 graded stone aggregate 40 mm nominal size), inside plastering 12 mm thick with cement mortar 1:3 (1 cement : 3 coarse sand) finished with floating coat of neat cement and making channels in cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) finished with a floating coat of neat cement complete as per standard design Inside size 90x80 cm and 45 cm deep including C.I. cover with frame (light duty) 455x610 mm internal dimensions, total weight of cover and frame to be not less than 38 kg (weight of cover 23 kg and weight of frame 15 kg) a)With common burnt clay F.P.S. (non modular) bricks of class designation 7.5 | 10.00 | Each |  | 33250.00 | 332500.00 | 9000.00 | 90000.00 | 90000.00 | K N RAI
81.00 | Constructing brick masonry manhole in cement mortar 1:4 ( 1 cement : 4 coarse sand ) with R.C.C. top slab with 1:1.5:3 mix (1 cement : 1.5 coarse sand (zone- III) : 3 graded stone aggregate 20 mm nominal size), foundation concrete 1:4:8 mix (1 cement : 4 coarse sand (zone- III) : 8 graded stone aggregate 40 mm nominal size), inside plastering 12 mm thick with cement mortar 1:3 (1 cement : 3 coarse sand) finished with floating coat of neat cement and making channels in cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) finished with a floating coat of neat cement complete as per standard design Inside size 120x90 cm and 90 cm deep including C.I. cover with frame (medium duty) 500 mm internal diameter, total weight of cover and frame to be not less than 116 kg (weight of cover 58 kg and weight of frame 58 kg) : b)With common burnt clay F.P.S. (non modular) bricks of class designation 7.5 | 10.00 | Each |  | 38000.00 | 380000.00 | 21200.00 | 212000.00 | 212000.00 | K N RAI
82.00 | Providing and fixing square-mouth S.W. gully trap class SP-1 complete with C.I. grating brick masonry chamber with water tight C.I. cover with frame of 300 x300 mm size (inside) the weight of cover to be not less than 4.50 kg and frame to be not less than 2.70 kg as per standard design: 100x100 mm size P type a) With common burnt clay F.P.S. (non modular) bricks of class designation 7.5 | 10.00 | Each |  | 9500.00 | 95000.00 | 1400.00 | 14000.00 | 14000.00 | K N RAI
83.00 | Preparation & submission of all the relevant detailed architechtural working drawings etc. & obtaining requisite approval/NOCs etc as & when required, from various departments of MCGM/other government depts. Etc. including laisoning with MCGM etc. for the building covered in the work of terminal building along with office block at Juhu Airport all complete as per the direction of Engineer in Charge. | 1.00 | Job |  | 700000.00 | 700000.00 | 1100000.00 | 1100000.00 | 700000.00 | D B Infratech
84.00 | Preparation and submission of detailed structural design and drawings for RCC members/ roofing & truss for architectural plan of terminal building /office block given by AAI including carrying out soil investigation & submission of soil investigation report. The contractor shall get approved the structural consultant from AAI before proceeding with the consultancy. The consultant must have rendered similar structural consultancy works directly to Central Govt State/Govt PSUs/Reputed firms ( in case of experience with Private firms,TDS certificate from the client shall be submitted) he structural drawings and designs as submitted by the consultant shall be got vetted /approved by any of the IITS/NITS and the fee for the same shall be bome by the contractor. The contractor /consultant shall intimate AAI the details of IITS/ NIT's from where structural designs and drawings will be vetted/approved. The consultant & Contractor shall coordinate for the time schedule to be taken by IIT/NIT so as to ensure adherence off overall time of submission of the above by the Consultant & Contractor to meet the overall project completion time. No addiitional time period or any cost shall be allowed to the contractor for designing preparation of drawings/ vetting of design and drawings from IIT/NIT etc. Major Engineering decision and specification shall be reviewed by AAI to the extent desired. Approval of any design/system by IIT/ NIT or AAI shall however, not relieve the consultant & contractor in discharging their responsibilities regarding the adequacy of design and proper execution of the work. The consultant shall be fully responsible for adequacy, accuracy and quality of the structural design, safety of the structure. The services rendered by the consultant shall be in accordance with the acceptable standards of safety, environment and public health. The item includes the preperation and submission of Engineering/Structural drawings of Passenger Terminal building along with office block , water supply, plumbing,sewarage and drainage service lines, plans and layout drawings as per the relevant IS codes, building codes and sound Engineering practices in accordance with the architectural/concepsual drawings.The contractor shall submit atleast six sets of good for construction drawings or revision there of. | 1.00 | Job |  | 600000.00 | 600000.00 | 850000.00 | 850000.00 | 600000.00 | D B Infratech
85.00 | Supplying & installation of Sintex water treatment system consisting of Sintex PWTS STBF-5000 l/d with intermediate tank 1000 l/d and treated water storage tank 1000 l/d along with tertiary treatment plant (TTP) (0.5 m3/hr) with inbuilt standard man holes & manhole covers, making internal leak-proof pipe connections inside the package STP tank, with provision of inlet, outlet, vent & blower pipe within the tank.Supply of necessary FRP Straps, eye bolt, wire rope & turn buckle for anchoring, factory made deadmans, air blowers of required capacity (2 nos.) , sludge return pump, control panel, hydrochloride & making all the inlet & outlet connections including connection of sewage outlet pipe to STP inlet, connection of blowers & sludge pump with control panel, piping arrangements for aeration & arrangement for sludge return as per the directions of E.I.C. | 1.00 | Each |  | 332500.00 | 332500.00 | 95000.00 | 95000.00 | 95000.00 | K N RAI
86.00 | Providing and fixing 8 mm dia C.P. / S.S. Jet with flexible tube upto 1 metre long with S.S. triangular plate to Eureopean type W.C. of quality and make as approved by Engineer - in - charge. | 7.00 | Each |  | 6175.00 | 43225.00 | 95000.00 | 665000.00 | 43225.00 | D B Infratech
87.00 | Providing and fixing CP Brass 32mm size Bottle Trap of approved quality & make and as per the direction of Engineer-in-charge. | 7.00 | Each |  | 2375.00 | 16625.00 | 1400.00 | 9800.00 | 9800.00 | K N RAI
88.00 | Providing and fixing mirror of superior glass (of approved quality) and of required shape and size with plastic moulded frame of approved make and shade with 6 mm thick hard board backing : a) Rectangular shape 453x357 mm | 7.00 | Each |  | 1710.00 | 11970.00 | 1500.00 | 10500.00 | 10500.00 | K N RAI
89.00 | Providing and fixing toilet paper holder a) C.P. brass | 7.00 | Each |  | 1100.00 | 7700.00 | 1256.00 | 8792.00 | 7700.00 | D B Infratech
90.00 | Providing and fixing soil, waste and vent pipes : 100 mm dia a) Sand cast iron S&S pipe as per IS: 1729 | 200.00 | Metre |  | 1100.00 | 220000.00 | 1600.00 | 320000.00 | 220000.00 | D B Infratech
91.00 | Providing and filling the joints with spun yarn, cement slurry and cement mortar 1:2 ( 1 cement : 2 fine sand) in S.C.I./ C.I. Pipes : a) 75 mm dia pipe | 40.00 | Each |  | 430.00 | 17200.00 | 350.00 | 14000.00 | 14000.00 | K N RAI
92.00 | Providing and fixing bend of required degree with access door, insertion rubber washer 3 mm thick, bolts and nuts complete. 100 mm dia a) Hubless centrifugally cast (spun) iron epoxy coated inside & outside as per IS:15905 | 12.00 | Each |  | 850.00 | 10200.00 | 815.00 | 9780.00 | 9780.00 | K N RAI
93.00 | Providing and fixing heel rest sanitary bend 100 mm dia a) Sand cast iron S&S as per IS - 1729 | 12.00 | Each |  | 1140.00 | 13680.00 | 800.00 | 9600.00 | 9600.00 | K N RAI
94.00 | Providing and fixing single unequal plain junction of required degree : 100x100x75 mm a) Hubless centrifugally cast (spun) iron epoxy coated inside & outside as per IS:15905 | 12.00 | Each |  | 1140.00 | 13680.00 | 755.00 | 9060.00 | 9060.00 | K N RAI
95.00 | Painting sand cast iron/ centrifugally cast (spun) iron soil, waste vent pipes and fittings with two coats of synthetic enamel paint of any colour such as chocolate grey, or buff etc. over a coat of primer (of approved quality) for new work : a) 100 mm diameter pipe | 200.00 | Metre |  | 280.00 | 56000.00 | 1600.00 | 320000.00 | 56000.00 | D B Infratech
96.00 | Providing and fixing double equal junction of required degree with access door, insertion rubber washer 3 mm thick, bolts and nuts complete : 100x100x100x100 mm a) Sand cast iron S&S as per IS - 1729 | 12.00 | Each |  | 2375.00 | 28500.00 | 1500.00 | 18000.00 | 18000.00 | K N RAI
97.00 | Providing and fixing Hubless centrifugally cast iron offsets epoxy coated inside & outside as per IS:15905 65 mm offsets a) With 100 mm dia pipe | 12.00 | Each |  | 900.00 | 10800.00 | 900.00 | 10800.00 | 10800.00 | D B Infratech, K N RAI
98.00 | Providing lead caulked joints to sand cast iron/centrifugally cast (spun) iron pipes and fittings of diameter : a)100 mm | 40.00 | Each |  | 430.00 | 17200.00 | 1100.00 | 44000.00 | 17200.00 | D B Infratech
99.00 | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply, including all CPVC plain & brass threaded fittings, i/c fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings with one step CPVC solvent cement and the cost of cutting chases and making good the same including testing of joints complete as per direction of Engineer in Charge. Concealed work, including cutting chases and making good the walls etc. a) 20 mm nominal outer dia Pipes | 80.00 | Metre |  | 190.00 | 15200.00 | 175.00 | 14000.00 | 14000.00 | K N RAI
100.00 | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply including all CPVC plain & brass threaded fittings This includes jointing of pipes & fittings with one step CPVC solvent cement, trenching, refilling & testing of joints complete as per direction of Engineer in Charge. a)32 mm nominal outer dia Pipes | 100.00 | Metre |  | 280.00 | 28000.00 | 475.00 | 47500.00 | 28000.00 | D B Infratech
101.00 | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply including all CPVC plain & brass threaded fittings This includes jointing of pipes & fittings with one step CPVC solvent cement, trenching, refilling & testing of joints complete as per direction of Engineer in Charge. a) 40 mm nominal outer dia Pipes | 100.00 | Metre |  | 525.00 | 52500.00 | 600.00 | 60000.00 | 52500.00 | D B Infratech
102.00 | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply including all CPVC plain & brass threaded fittings This includes jointing of pipes & fittings with one step CPVC solvent cement, trenching, refilling & testing of joints complete as per direction of Engineer in Charge. a) 50 mm nominal outer dia Pipes | 250.00 | Metre |  | 620.00 | 155000.00 | 1000.00 | 250000.00 | 155000.00 | D B Infratech
103.00 | Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) : a) 50 mm nominal bore | 2.00 | Each |  | 3040.00 | 6080.00 | 3600.00 | 7200.00 | 6080.00 | D B Infratech
104.00 | Providing and fixing gun metal non- return valve of approved quality (screwed end) :50 mm nominal bore a) Horizontal | 2.00 | Each |  | 3325.00 | 6650.00 | 3200.00 | 6400.00 | 6400.00 | K N RAI
105.00 | Providing and placing on terrace (at all floor levels) polyethylene water storage tank, IS : 12701 marked, with cover and suitable locking arrangement and making necessary holes for inlet, outlet and overflow pipes but without fittings and the base support for tank. | 10000.00 | Per Litre |  | 1.20 | 12000.00 | 12.00 | 120000.00 | 12000.00 | D B Infratech
106.00 | Providing and fixing enclosed type water meter (bulk type) conforming to IS : 2373 and tested by Municipal Board complete with bolts, nuts, rubber insertions etc. (The tail pieces if required will be paid separately) : a) 100 mm dia nominal bore | 1.00 | Each |  | 8075.00 | 8075.00 | 1275.00 | 1275.00 | 1275.00 | K N RAI
107.00 | Providing & fixing Health faucet in Chrome Finish complete with 1.2 Meter Long Flexible Tube & Wall Hoo of model similar to (ALD-CHR-573) of Jaguar or equivalent | 7.00 | Each |  | 3040.00 | 21280.00 | 1400.00 | 9800.00 | 9800.00 | K N RAI
108.00 | Providing and fixing urinal partions of standard dimensions of approved shape of Merino (Besco) or equivalent and made of 12 mm thick compact laminated phenolic Core Board based on thermostate resisn, homogenously reinforced with cellulose fibre and laminated on both side with suede finish, scratch & impact resistant. The urnial partions shall be fixed on walls with right angle brackets in stainless steel of grade 304 with necesary stainless steel screws of grade 304 complete as per the direction of Engineer incharge. a) Urinal partition of size 1200 mm x 450 mm. | 5.00 | Each |  | 4275.00 | 21375.00 | 3200.00 | 16000.00 | 16000.00 | K N RAI
109.00 | Providing and fixing first quality rimless white vitreous china wall hung P trap water closet (European type) with soft close slim seat cover with lid , C.P. bolts, nuts, hinges , rubber buffers, alongwith concealed flush tank of min 10 Litres capacity , flush control plates/flush valve with water volume adjustment and flush pipe etc , Chair Brackets, CP brass, screws and washers including cutting and making good the walls and floors etc all complete and as per direction of Engineer-in-charge. Wall hung WC similar to (CNS-WHT-963SPP) of Jaguar with soft close slim seat cover with lid or equivalent and Concealed Flush Tank (JCS-WHT-2400) of Jaguar or equivalent with flush plates (Code JCP-CHR-102415) of Jaguar or equivalent. | 7.00 | Each |  | 850.00 | 5950.00 | 14000.00 | 98000.00 | 5950.00 | D B Infratech
110.00 | Providing and fixing white vitreous china battery based infrared sensor operated urinal of approx. size 740 x 480 x 300 mm having pre & post flushing with water ,having water inlet from back side, including fixing to wall with suitable brackets all as per manufacturers specification and direction of Engineer-in-charge. Urinal similar to (URS-WHT-13255) of Jaguar or equivalent , Sensor faucet valve for urinal similar to (SNR-CHR-51097) of Jaguar or equivalent. | 5.00 | Each |  | 11875.00 | 59375.00 | 1450.00 | 7250.00 | 7250.00 | K N RAI
111.00 | Providing and fixing under counter wash basin of size 605 x 430 x 200 mm with Fixing Accessories, 15 mm dia CP Brass single hole pillar cock of approved quality and make, including painting of fittings , cutting and making good the walls wherever required with suitable brackets all as per manufacturers specification and direction of Engineer-in-charge. Under Counter Wash basin similar to (CNS-WHT-705) of Jaguar or equivalent , Auto Closing Pillar Cock for wash basin similar to (PRS-CHR-031) of Jaguar or equivalent. | 7.00 | Each |  | 4275.00 | 29925.00 | 8500.00 | 59500.00 | 29925.00 | D B Infratech
112.00 | Providing and fixing trap of self cleansing design with screwed down or hinged grating with or without vent arm complete, including cost of cutting and making good the walls and floors : PVC Nahanitrap of size 3.1/2 HT x 75 all complete as per directions of Engineer in charge. | 15.00 | Each |  | 430.00 | 6450.00 | 425.00 | 6375.00 | 6375.00 | K N RAI
113.00 | Providing & fixing of PVC reducer of size 50x40mm. This includes jointing of pipes & fittings with one step PVC solvent including trenching,refilling & testing of joints complete as per direction of Engineer in Charge. | 36.00 | Each |  | 430.00 | 15480.00 | 55.00 | 1980.00 | 1980.00 | K N RAI
114.00 | Providing & fixing of PVC Vent Cowl of size 110 mm. This includes jointing of pipes & fittings with one step PVC solvent including trenching,refilling & testing of joints complete as per direction of Engineer in Charge | 48.00 | Each |  | 2375.00 | 114000.00 | 80.00 | 3840.00 | 3840.00 | K N RAI
115.00 | Providing & fixing of PVC cleaning pipe plug of size 110mm. This includes jointing of pipes & fittings with one step PVC solvent cement and testing of joints complete as per direction of Engineer in Charge. | 12.00 | Each |  | 1520.00 | 18240.00 | 325.00 | 3900.00 | 3900.00 | K N RAI
116.00 | Providing & fixing of PVC Plug bend of size 110mm. This includes jointing of pipes & fittings with one step PVC solvent cement and testing of joints complete as per direction of Engineer in Charge. | 12.00 | Each |  | 570.00 | 6840.00 | 200.00 | 2400.00 | 2400.00 | K N RAI
117.00 | Providing & fixing of PVC Plug Y of size 110mm. This includes jointing of pipes & fittings with one step PVC solvent cement and testing of joints complete as per direction of Engineer in Charge. | 12.00 | Each |  | 570.00 | 6840.00 | 425.00 | 5100.00 | 5100.00 | K N RAI
118.00 | Providing and fixing on wall face unplasticised - PVC moulded fittings/ accessories for unplasticised Rigid PVC rain water pipes conforming to IS : 13592 Type A, including jointing with seal ring conforming to IS : 5382, leaving 10 mm gap for thermal expansion. Bend 87.5° a) 110 mm bend | 25.00 | Each |  | 570.00 | 14250.00 | 205.00 | 5125.00 | 5125.00 | K N RAI
119.00 | Structural steel work riveted, bolted or welded in built up sections, trusses and framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete. | 1249.00 | Kg |  | 120.00 | 149880.00 | 125.00 | 156125.00 | 149880.00 | D B Infratech
120.00 | Surface dressing of the ground including removing vegetation and in equalities not exceeding 15 cm deep and disposal of rubbish, lead up to 50 m and lift up to 1.5 m. a) All kinds of soil | 1000.00 | Sqm |  | 100.00 | 100000.00 | 35.00 | 35000.00 | 35000.00 | K N RAI
121.00 | Providing and fixing G.I. chain link fabric fencing of required width in mesh size 50x50 mm including strengthening with 2 mm dia wire or nuts, bolts and washers as required complete as per the direction of Engineer-in-charge a) Made of G.I. wire of dia 4 mm | 90.00 | Sqm |  | 350.00 | 31500.00 | 810.00 | 72900.00 | 31500.00 | D B Infratech
122.00 | Painting with synthetic enamel paint of approved brand and manufacture to give an even shade : a) Two or more coats on new work | 236.00 | Sqm |  | 280.00 | 66080.00 | 110.00 | 25960.00 | 25960.00 | K N RAI
123.00 | SITC of LT Panel Design,Supply, Installation, Testing and Commissioning of cubicle type LT panel, IP 42 , suitable for 415V+/-10%, 3 Phase, 4 wire 50 Hz AC supply system, fabricated in compartmentalized Design,Supply, Installation, Testing and Commissioning of cubicle type LT panel, IP 42 , suitable for 415V+/-10%, 3 Phase, 4 wire 50 Hz AC supply system, fabricated in compartmentalized modular design from CRCA sheet steel of 2 mm thick for frame work and covers, 3 mm thick for gland, plates i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having TPN Aluminium alloy bus bars for high conductivity, SMC bus bar supports, entire panel shall have a common Copper earth bus bar of size as per IS 3043 subject to minimum 50 mm x 6 mm at the rear with 2 Nos. earth stud, solid /flexible connections from main earth bus bar to switchgears with required size of Cooper / Aluminium conductors / bus bars and control wiring with 2.5 sqmm PVC insulated copper conductor cable (FRLS), cable alleys, cable gland plates in two half, including provision of SPD's. Surge Protection Devices (SPD’S) shall be provided at main LT cum synchronizing Panel incoming feeders (Type 1+2 / Class B) i/c providing following switchgears / accessories as per specifications conforming to IS 8623 / IEC 60439 PTTA type & shall be of Form-3b construction. Incomer 250 Amp ,4 Pole MCCB with 36 kA breaking capacity MCCB with adjustable setting , thermal magnetic release with O/C & S/C protectionand terminal spreaders suitable for termination of 3.5Cx 185 sqmm aluminium armoured cable --- 02 Set with E & M interlock All MCCBs shall be provided with Door Interlock with Panel doorDigital Multi function digital meter to read V,A,kVA, KW, kVAR, PF, Hz etc with LED display with required Nos CTs, control circuit wiring with 2 Amp MCB for controlling - 02 set Indication Lamps, LED type, R,Y,B Phase indicating lamp with 6 Amp MCB for controlling- 02 Set Indication Lamps, LED type for MCCB 'ON' , 'OFF' lamps with 6 Amp MCB for controlling -02 Set Sets TP+N Surge protection device (Type 1+2 / Class B) Including with inbuilt use and all necessary accessories and wire connections as per specifications.- 01 Set Bus Coupler 1 No. 250 Amps, 36 kA 4 Pole breaking capacity MCCB with adjustable setting , thermal magnetic release with O/C & S/C protection. 3 Sets Indication Lamps, LED type, for RYB with 2 Amp control MCB.& breaker 'ON' , 'OFF', 'TRIP' & spring charged lamps with 6 Amp MCB for controlling Bus BarsTPN aluminium extensible type main bus bars of minimum 400 Amps. capacity with heat shrinkable coloured sleeves having 100% neutral bus as that of phase i/c SMC bus bar supports at required inetrvals complete for cross section, side supports & their spacing etc for withstanding fault level 36 kA for 1 sec. Outgoings 160 Amp ,4 Pole MCCB with 36 kA breaking capacity MCCB with adjustable setting , thermal magnetic release with O/C & S/C protection and terminal spreaders-02 sets Digital Multi function digital meter to read V,A,kVA, KW, kVAR, PF, Hz etc with LED display with required Nos CTs, control circuit wiring with 6 Amp MCB for controlling - 02 set Indication Lamps, LED type, R,Y,B Phase indicating lamp with 2 Amp MCB for controlling- 02 Set Indication Lamps, LED type for MCCB 'ON' , 'OFF' lamps with 2 Amp MCB for controlling -02 Set All MCCBs shall be provided with Door Interlock with Panel door 4 Nos. 63 A 4 pole MCCB with 36 kA breaking capacity MCCB with adjustable setting , thermal magnetic release with O/C & S/C protection and terminal spreader 2 Nos. 40 A 4 pole MCCB with 36 kA breaking capacity MCCB with adjustable setting , thermal magnetic release with O/C & S/C protection and terminal spreader Note: All incomers and buscoupler breakers shall be electrically and mechaniically interlocked with suitable accessories. | 1.00 | Job |  | 300000.00 | 300000.00 | 425000.00 | 425000.00 | 300000.00 | D B Infratech
124.00 | Design,Supply, Installation, Testing and Commissioning of cubicle type LT panel, IP 42 , suitable for 415V+/-10%, 3 Phase, 4 wire 50 Hz AC supply system, fabricated in compartmentalized modular design from CRCA sheet steel of 2 mm thick for frame work and covers, 3 mm thick for gland, plates i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having TPN Aluminium alloy bus bars for high conductivity, SMC bus bar supports, entire panel shall have a common Copper earth bus bar of size as per IS 3043 subject to minimum 50 mm x 6 mm at the rear with 2 Nos. earth stud, solid /flexible connections from main earth bus bar to switchgears with required size of Cooper / Aluminium conductors / bus bars and control wiring with 2.5 sqmm PVC insulated copper conductor cable (FRLS), cable alleys, cable gland plates in two half, shall be provided a providing following switchgears / accessories as per specifications conforming to IS 8623 / IEC 60439 PTTA type & shall be of Form-3b construction. Incomer 160 Amp ,4 Pole MCCB with 36 kA breaking capacity MCCB with adjustable setting , thermal magnetic release with O/C & S/C protectionand terminal spreaders --- 04 Set ( 2 main incomer+ 2 DG sets incomer) Digital Multi function digital meter to read V,A,kVA, KW, kVAR, PF, Hz etc with LED display with required Nos CTs, control circuit wiring with 2 Amp MCB for controlling - 04 set Indication Lamps, LED type, R,Y,B Phase indicating lamp with 2 Amp MCB for controlling- 04 Set Indication Lamps, LED type for MCCB 'ON' , 'OFF' lamps with 2 Amp MCB for controlling -04 Set All MCCBs shall be provided with Door Interlock with Panel door 160 A 4 Pole Automatic Changeover Switch for selection of DG Set & Main Incomer Switch with controller having complete protection --- 02 Set Digital Multi function digital meter to read V,A,kVA, KW, kVAR, PF, Hz etc with LED display with required Nos CTs, control circuit wiring with 2 Amp MCB for controlling - 02 set Indication Lamps, LED type, R,Y,B Phase indicating lamp with 2 Amp MCB for controlling- 02 Set Indication Lamps, LED type for MCCB 'ON' , 'OFF' lamps with 2 Amp MCB for controlling -02 Set Bus Coupler 1 No. 160 Amps, 36 kA 4 Pole breaking capacity MCCB with adjustable setting , thermal magnetic release with O/C & S/C protection. 3 Sets Indication Lamps, LED type, for RYB with 2 Amp control MCB.& breaker 'ON' , 'OFF', 'TRIP' & spring charged lamps with 6 Amp MCB for controlling Bus Bars TPN aluminium extensible type main bus bars of minimum 250 Amps. capacity with heat shrinkable coloured sleeves having 100% neutral bus as that of phase i/c SMC bus bar supports at required inetrvals complete for cross section, side supports & their spacing etc for withstanding fault level 36 kA for 1 sec. Outgoings 12 Nos. 63 A 4 pole MCCB with 36 kA breaking capacity MCCB with adjustable setting , thermal magnetic release with O/C & S/C protection and terminal spreader 8 Nos. 40 A 4 pole MCCB with 36 kA breaking capacity MCCB with adjustable setting , thermal magnetic release with O/C & S/C protection and terminal spreader | 1.00 | Job |  | 250000.00 | 250000.00 | 600000.00 | 600000.00 | 250000.00 | D B Infratech
125.00 | Supply of 1.1kV grade, 3.5 Core 185 Sq.mm. XLPE insulated PVC sheathed Aluminium stranded conductor armoured power cable grade conforming to IS-7098 Part-I Part 1 amended upto date etc. complete as required. | 50.00 | Metre |  | 1300.00 | 65000.00 | 900.00 | 45000.00 | 45000.00 | K N RAI
126.00 | Supply of 1.1kV grade, 3.5 Core 150 Sq.mm. XLPE insulated PVC sheathed Aluminium stranded conductor armoured power cable grade conforming to IS-7098 Part-I Part 1 amended upto date etc. complete as required. | 100.00 | Metre |  | 1100.00 | 110000.00 | 720.00 | 72000.00 | 72000.00 | K N RAI
127.00 | Supply of 1.1kV grade, 3.5 Core 35 Sq.mm. XLPE insulated PVC sheathed Aluminium stranded conductor armoured power cable grade conforming to IS-7098 Part-I Part 1 amended upto date etc. complete as required. | 300.00 | Metre |  | 850.00 | 255000.00 | 230.00 | 69000.00 | 69000.00 | K N RAI
128.00 | Supply of 1.1kV grade, 3.5 Core 25 Sq.mm. XLPE insulated PVC sheathed Aluminium stranded conductor armoured power cable grade conforming to IS-7098 Part-I Part 1 amended upto date etc. complete as required. | 300.00 | Metre |  | 750.00 | 225000.00 | 220.00 | 66000.00 | 66000.00 | K N RAI
129.00 | Supplying and installing following size of perforated painted with powder coating M.S. cable trays with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required 150 mm width X 50 mm depth X 1.6 mm thickness | 150.00 | Metre |  | 550.00 | 82500.00 | 540.00 | 81000.00 | 81000.00 | K N RAI
130.00 | Laying of cables: Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required. Upto 35 sq. mm | 50.00 | Meter |  | 180.00 | 9000.00 | 40.00 | 2000.00 | 2000.00 | K N RAI
131.00 | Above 95 sq. mm and upto 185 sq. mm (clamped with 25/40x3mm MS flat clamp) | 10.00 | Metre |  | 200.00 | 2000.00 | 120.00 | 1200.00 | 1200.00 | K N RAI
132.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required. Upto 35 sq. mm | 500.00 | Metre |  | 180.00 | 90000.00 | 30.00 | 15000.00 | 15000.00 | K N RAI
133.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required. Upto 35 sq. mm | 50.00 | Metre |  | 180.00 | 9000.00 | 32.00 | 1600.00 | 1600.00 | K N RAI
134.00 | Above 95 sq. mm and upto 185 sq. mm | 140.00 | Metre |  | 200.00 | 28000.00 | 60.00 | 8400.00 | 8400.00 | K N RAI
135.00 | End termination of cables: Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated & PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 3½ X 185 sq. mm (57mm) | 4.00 | Set |  | 680.00 | 2720.00 | 800.00 | 3200.00 | 2720.00 | D B Infratech
136.00 | 3½ X 150 sq. mm (50mm) | 8.00 | Set |  | 640.00 | 5120.00 | 570.00 | 4560.00 | 4560.00 | K N RAI
137.00 | 3½ X 35 sq. mm (32 mm) | 14.00 | Set |  | 600.00 | 8400.00 | 315.00 | 4410.00 | 4410.00 | K N RAI
138.00 | 3½ X 25 sq. mm (25 mm) | 14.00 | Set |  | 550.00 | 7700.00 | 259.00 | 3626.00 | 3626.00 | K N RAI
139.00 | Earthing: Earthing with GI earth pipe 4.5 m long, 40 mm dia including accessories, and providing masonary enclosure with cover plate having locking arrangement and watering pipe etc with charcoal or coke and salt complete as required. | 4.00 | Set |  | 10000.00 | 40000.00 | 6000.00 | 24000.00 | 24000.00 | K N RAI
140.00 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe From earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 25.00 | Metre |  | 225.00 | 5625.00 | 600.00 | 15000.00 | 5625.00 | D B Infratech
141.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | 60.00 | Metre |  | 200.00 | 12000.00 | 210.00 | 12600.00 | 12000.00 | D B Infratech
142.00 | Safety Equipments: Providing of set of 4 Nos. 9.5 Litre capacity GI bucket painted in post office red colour with prior coat of red oxide paint and written with white paint ‘FIRE’ and mounted on MS angle iron frame with bracket of appropriate size & capacity i/c filling sand etc. | 2.00 | Set |  | 1150.00 | 2300.00 | 6250.00 | 12500.00 | 2300.00 | D B Infratech
143.00 | Supply and fixing of fire retardant electrically insulated synthetic mat of class C 3 mm thick suitable for 11KV AC grade and 240V DC system meeting requirements of IS 15652:2006 tested for breakdown strength, tensile/elongation, aging properties, insulation resistance, effect to acid, alkaline, diesel, transformer oil & leakage current test, fire test etc. having minimum width of 1000 mm ± 20 mm along with all allied materials such as Pu-resin, Chemi bound, special PVC adhesive, liquid primer etc. in what so ever quantity required to complete the job as per site conditions and as per instructions from Engineer-in-Charge. | 50.00 | Metre |  | 700.00 | 35000.00 | 1950.00 | 97500.00 | 35000.00 | D B Infratech
144.00 | Supply & fixing shock treatment chart both in Hindi & English duly mounted on a wooden frame with 3 mm thick glass as reqd. (approximate front area 1.00 sq. metre) | 2.00 | Nos. |  | 2975.00 | 5950.00 | 600.00 | 1200.00 | 1200.00 | K N RAI
145.00 | Supply and fixing safety instruction chart both in Hindi & English duly framed with 3 mm thick glass as required. (approximate front area 1.00 sq. metre) | 2.00 | Nos. |  | 3825.00 | 7650.00 | 610.00 | 1220.00 | 1220.00 | K N RAI
146.00 | Supply of First aid box containing material as prescribed by St. John Ambulance brigade (Applicable for medium risk) OR Indian Red Cross conforming to IS 2217-1963 complete as required. | 2.00 | Nos. |  | 3825.00 | 7650.00 | 3100.00 | 6200.00 | 6200.00 | K N RAI
147.00 | Providing & fixing danger plates made of mild steel at least 2 mm thick & vitreous enamelled white on both sides & with inscriptions in signal red colour on front side as read. High Voltage – size 250 mm x 200 mm | 1.00 | Nos. |  | 3975.00 | 3975.00 | 395.00 | 395.00 | 395.00 | K N RAI
148.00 | Medium Voltage – size 200 mm x 150 mm | 3.00 | Nos. |  | 2720.00 | 8160.00 | 320.00 | 960.00 | 960.00 | K N RAI
149.00 | Supplying of Rubber hand gloves suitable for 11KV as per IS Standard. | 10.00 | Pairs |  | 1000.00 | 10000.00 | 589.00 | 5890.00 | 5890.00 | K N RAI
150.00 | Providing Single Line Diagram on 5mm thick Aluminium sheet in A0 Size duly laminated as per IS Standard. | 2.00 | Nos. |  | 3825.00 | 7650.00 | 3400.00 | 6800.00 | 6800.00 | K N RAI
151.00 | SITC of DG Sets & UPS Supply Installation Testing Commissioning of "Silent Type" Radiator Cooled, Diesel Generating Setalong with having Prime mover power rating of 62.5 KVA at 0.8 lagging power factor, 415 volts, 1500 RPM, 3 phase system, as per ISO 8528 and consisting of the following: (a) Diesel Engine: 4 stroke, 12/16 cylinder, electronic governor, power command control module, radiator cooled, electric start, of suitable BHP at 1500 RPM suitable for above output of alternator at 40 Degree C, 50% RH & at 1000 Meter MSL and conforming to BS 5514, BS 649, IS 10000, capable of taking 10% over loading for one hour after 12 hours of continuous operation. The engine will be fitted complete with all the required accessories. (b) Alternator: Synchronous alternator rated for 62.5 KVA, 415 volts at 1500 RPM, 3 phase 50 Hz, AC supply with 0.8 lagging power factor at 40 Degree C, 50% RH & at 1000 Meter MSL. The alternator shall be having SPDP enclosure, brushless, continuous duty, self-excited and self-regulated through AVR, QDCT for synchronising, terminal arrangement i/c 1000A alumunium bus-duct box with other associated equipment conforming to IS:4722 / BS 2613 suitable for tropical conditions and with class F insulation. (c) AMF Panel for control, metering and alarm system having mains supply failure monitor, supply failure timer, restoration timer, three impulse automatic engine start/stop and failure to start lockout, RPM indication, battery voltage sensing, selector switch and push button, manual/Auto/Test selector switch , Generator start/stop, generator breaker close/trip , Mains breaker close/trip, LED indication, multifunction meter etc suitable for 62.5 KVA DG set (d) Base Frame & Foundation: Both the engine and alternator shall be mounted on suitable base frame made of MS channel with necessary reinforcement which shall be installed on existing concrete foundation and vibration isolation arrangement including earthing of Dg sets as per recommendations of manufacturer. (e) Fuel Tank: Day service fuel tank of 990 litres capacity fabricated out of 3 mm thick M.S. sheet complete with all standard accessories and fuel piping between fuel tank and diesel engine with MS class 'C' pipes of suitable dia. Complete with valves, level indications & accessories as required as per specifications. f) Exhaust System: Dry Exhaust manifold with residential exhaust silencer and catalytic convertor. (g) Starting System: 24V DC starting system comprising of starter motors: voltage regulator and arrangement for initial excitation complete with suitable nos. of batteries with MS battery stand etc. as required as per specifications (h) Acoustic Enclosure : Acoustic and weather proof enclosure with arrangement for fresh air intake for cooling of the engine & alternator, extraction, discharging hot air in to the atmosphere as per specifications. (i) The work should be as per Central Electrical Authority / Pollution control board standards. DG set complete as described above and as per specifications | 2.00 | Nos. |  | 700000.00 | 1400000.00 | 850000.00 | 1700000.00 | 1400000.00 | D B Infratech
152.00 | Supply, installation, testing and commissioning of 10 KVA, 3 Phase input and 3 Phase output UPS based on online double conversion PWM IGBT based technology having input voltage range 400±10 % with high output power factor , operating Temp. :0 ~ 55 ͦC, Humidity 0 ~ 90% (non-condensing),Noise Level Less than 60dBA @ 1 meter, designed to withstand all kinds of loads.,Intelligent Battery Management to prolong battery life-cycle.,Redundant fan design and independent ventilation enhance durable operation under harsh environments with provision of accepting dual-Mains Input, overload/short-circuit withstand capability alongwith sealed maintenance free batteries giving a back up of minimum 30 min. at full load alongwith all accessories including interconnecting cables, lugs, Base Frames, Battery Rack & Battery Circuit breaker etc complete as required. | 2.00 | Nos. |  | 42500.00 | 85000.00 | 110000.00 | 220000.00 | 85000.00 | D B Infratech
153.00 | INTERNAL ELECTRIFICATION Supplying recessed mounted 10 watt, (107x107)mm panel LED lighting fixture with high lumen output, environmental friendly, energy efficient, etc. complete as required (Model:TRIM LED PANEL SQUARE , Item Code: LHEBLEP7IN1W010 10W, Make : HAVELLS or equivalent approved make). | 17.00 | Each |  | 510.00 | 8670.00 | 470.00 | 7990.00 | 7990.00 | K N RAI
154.00 | Supplying of 09 watts LED bulb with B-22 base suitable to operate on single phase 230 V , 50 Hz supply etc complete as per specificaions. | 13.00 | Each |  | 400.00 | 5200.00 | 130.00 | 1690.00 | 1690.00 | K N RAI
155.00 | Supplying recessed mounting 24 watt decorative 2 x 2 flat LED lighting fixture with high lumen output, environmental friendly, energy efficient, etc. complete as required (Model:VENUSNEOHE2x2r24WlLED840PIRSENSOR, Make : HAVELLS or equivalent approved make). | 45.00 | Each |  | 550.00 | 24750.00 | 4725.00 | 212625.00 | 24750.00 | D B Infratech
156.00 | Supplying of Exhaust fan of 250 mm sweep, 1200 RPM, provided with Robust Motor for continuous running of fan, gravity shutter, louvers including all accessories and suitable to operate on single phase, 230 V, 50 Hz A.C. supply. | 7.00 | Each |  | 1530.00 | 10710.00 | 1400.00 | 9800.00 | 9800.00 | K N RAI
157.00 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed steel conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc. as required. Group B | 85.00 | Point |  | 550.00 | 46750.00 | 1425.00 | 121125.00 | 46750.00 | D B Infratech
158.00 | Wiring for circuit/submain wiring alongwith earth wire with the following sizes of FRLSH PVC insulated copper conductor, single core cable in surface / recessed steel conduit as required. 2 X 2.5 sq. mm + 1 X 2.5 sq. mm earth wire | 2060.00 | Metre |  | 180.00 | 370800.00 | 300.00 | 618000.00 | 370800.00 | D B Infratech
159.00 | 2 X 4 sq. mm + 1 X 4 sq. mm earth wire | 1487.00 | Metre |  | 200.00 | 297400.00 | 378.00 | 562086.00 | 297400.00 | D B Infratech
160.00 | 4 X 6 sq. mm + 2 X 6 sq. mm earth wire | 525.00 | Metre |  | 225.00 | 118125.00 | 600.00 | 315000.00 | 118125.00 | D B Infratech
161.00 | Supplying and fixing following size/ modules, GI box alongwith modular base & cover plate for modular switches in recess etc as required. 1 or 2 Module (75mm X 75mm) | 21.00 | Each |  | 210.00 | 4410.00 | 290.00 | 6090.00 | 4410.00 | D B Infratech
162.00 | 3 Module (100mm X 75mm) | 48.00 | Each |  | 300.00 | 14400.00 | 300.00 | 14400.00 | 14400.00 | D B Infratech, K N RAI
163.00 | Supplying and fixing following modular switch/socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required. 5/6 amps switch | 76.00 | Each |  | 640.00 | 48640.00 | 65.00 | 4940.00 | 4940.00 | K N RAI
164.00 | 3 pin 5/6 amp socket outlet | 48.00 | Each |  | 470.00 | 22560.00 | 82.00 | 3936.00 | 3936.00 | K N RAI
165.00 | Telephone socket outlet | 17.00 | Each |  | 380.00 | 6460.00 | 110.00 | 1870.00 | 1870.00 | K N RAI
166.00 | TV antenna socket outlet | 4.00 | Each |  | 350.00 | 1400.00 | 95.00 | 380.00 | 380.00 | K N RAI
167.00 | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 5/6 & 15/16 amps modular socket outlet and 15/16 amps modular switch, connection etc. as required. | 57.00 | Each |  | 900.00 | 51300.00 | 510.00 | 29070.00 | 29070.00 | K N RAI
168.00 | Supplying and drawing 2 pair 0.5 mm dia FRLS PVC insulated annealed copper conductor, unarmored telephone cable in the existing surface/ recessed steel/ PVC conduit as required. | 200.00 | Metre |  | 100.00 | 20000.00 | 32.00 | 6400.00 | 6400.00 | K N RAI
169.00 | Supplying and drawing co-axial TV cable RG-6 grade, 0.7 mm solid copper conductor PE insulated, shielded with fine tinned copper braid and protected with PVC sheath in the existing surface/ recessed steel/ PVC conduit as required. | 100.00 | Metre |  | 150.00 | 15000.00 | 42.00 | 4200.00 | 4200.00 | K N RAI
170.00 | Supplying and fixing of following sizes of steel conduit along with accessories in surface/recess including painting in case of surface conduit, or cutting the wall and making good the same in case of recessed conduit as required. 20 mm | 300.00 | Metre |  | 150.00 | 45000.00 | 242.00 | 72600.00 | 45000.00 | D B Infratech
171.00 | Supplying and fixing PVC batten/ angle holder with brass ring including connection etc. as required. | 13.00 | Each |  | 380.00 | 4940.00 | 110.00 | 1430.00 | 1430.00 | K N RAI
172.00 | Installation, testing and commissioning of pre-wired, LED lighting fixture of all types, complete with all accessories, etc. directly on ceiling/ wall, including connection with 1.5 sq. mm FRLSH PVC insulated, copper conductor, single core cable and earthing etc. as required. | 62.00 | Each |  | 1360.00 | 84320.00 | 200.00 | 12400.00 | 12400.00 | K N RAI
173.00 | Installation of exhaust fan in the existing opening, including making good the damage, connection, testing, commissioning etc. as required. a) Upto 450 mm sweep | 7.00 | Each |  | 1870.00 | 13090.00 | 400.00 | 2800.00 | 2800.00 | K N RAI
174.00 | Extra for fixing the louvers/ shutters complete with frame for a exhaust fan of all sizes. | 7.00 | Each |  | 425.00 | 2975.00 | 190.00 | 1330.00 | 1330.00 | K N RAI
175.00 | Supplying and fixing 6 amps to 32 amps rating, 240/415 volts, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. Single pole | 174.00 | Each |  | 210.00 | 36540.00 | 210.00 | 36540.00 | 36540.00 | D B Infratech, K N RAI
176.00 | Triple Pole | 8.00 | Each |  | 510.00 | 4080.00 | 800.00 | 6400.00 | 4080.00 | D B Infratech
177.00 | Supplying and fixing following rating, four pole, 415 volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required. 40 Amps | 6.00 | Each |  | 760.00 | 4560.00 | 1000.00 | 6000.00 | 4560.00 | D B Infratech
178.00 | Supplying and fixing following rating, four pole, 415 volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required. 63 Amps | 6.00 | Each |  | 1060.00 | 6360.00 | 900.00 | 5400.00 | 5400.00 | K N RAI
179.00 | Supplying and fixing following rating, four pole, 415 volts, residual current circuit breaker (RCCB), having a sensitivity current upto 100 milliamperes in the existing MCB DB complete with connections, testing and commissioning etc. as required. 63 AMP | 6.00 | Each |  | 1275.00 | 7650.00 | 3700.00 | 22200.00 | 7650.00 | D B Infratech
180.00 | 40 Amp | 6.00 | Each |  | 1060.00 | 6360.00 | 3500.00 | 21000.00 | 6360.00 | D B Infratech
181.00 | Supplying and fixing following way, three pole and neutral, sheet steel, MCB distribution board, 415 volts, on surface/recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator/MCCB ) 4 way (4 + 12), Double Door | 4.00 | Each |  | 2975.00 | 11900.00 | 3000.00 | 12000.00 | 11900.00 | D B Infratech
182.00 | 6 way (4 + 18), Double Door | 7.00 | Each |  | 3400.00 | 23800.00 | 3700.00 | 25900.00 | 23800.00 | D B Infratech
183.00 | 8 way (8 + 24), Double Door | 1.00 | Each |  | 40800.00 | 40800.00 | 4250.00 | 4250.00 | 4250.00 | K N RAI
184.00 | EXTERNAL LIGHTING Supply of following size XLPE insulated, PVC sheathed, Aluminium conductor armoured power cable of 1.1 KV grade confirming to IS - 7098 PART- I /IS 1554 part 1 with upto date amended etc. complete as required. 4 C x 10 sq.mm | 300.00 | Metre |  | 1100.00 | 330000.00 | 140.00 | 42000.00 | 42000.00 | K N RAI
185.00 | Supply of 30 W LED street light luminaire made out of high pressure die cast aluminium/ standard alloy housing (IP65 or higher) having minimum 3300 lumen output and suitable to operate on 230V, 50 Hz single phase AC supply with electronic driver and having surge protection etc, complete as per specifications. | 20.00 | Each |  | 3825.00 | 76500.00 | 2100.00 | 42000.00 | 42000.00 | K N RAI
186.00 | Supply and Erection of 50 mm 'B' class GI pipe for street light of length 4.5 metres on base plate in cement concrete 1:3:6 (1 Cement 3 Coarse sand 6 graded stone aggregate 40mm normal size) foundation of size not less than 400 x 400 1150 mm thick on 500 x 500 x 150 mm thick PCC (1:4:8) including 150 mm height of foundation above ground level (level above ground may be revised to suit the site conditions) alongwith providing, laying and fixing of 2 x 1 meter long 32 mm inner dia "B" Class GI pipe (Make: Jindal or equivalent approved make) having suitable bend and MS Clamp for fixing for cable entry including excavation and refilling etc as required, complete as per technical specifications. | 10.00 | Job |  | 7225.00 | 72250.00 | 9000.00 | 90000.00 | 72250.00 | D B Infratech
187.00 | Supply, installation, testing & commissioning of cable junction box IP 66 of size 155mm x 210mm x 92mm (Hensel DK 2525 or equivalent) on the wall with suitable clamps including providing and fixing 2 nos fuse 4 way, 20 amp terminal block,6 amp SP MCB C series for cable termination in the box and arrangement for providing loop earthing etc., including connections with cable complete as required. | 10.00 | Job |  | 3825.00 | 38250.00 | 2700.00 | 27000.00 | 27000.00 | K N RAI
188.00 | Installation ,Testing and Commissioning of prewired LED type street light fitting on the existing street light tubular pole of height 4.5 mtrs including providing and fixing suitable size GI pipe bracket of 1 mtr. length with size clamps, nuts, bolts and connections with 1.5 sq.mm FRLS PVC insulated, copper conductor, single core cable and earthing etc. as required. | 20.00 | Job |  | 4675.00 | 93500.00 | 800.00 | 16000.00 | 16000.00 | K N RAI
189.00 | Supply and laying of DWC HDPE pipe of 50 mm OD of PE 100 PN 6 ISI Marked along with all accessories like couplers, socket, bend etc. conforming to IS 4984 complete with fitting and cutting, jointing etc. direct in ground at a depth of 0.75m below the ground level i/c excavation and refilling the trench but excluding sand cushioning and protective covering etc. as required. | 250.00 | Metre |  | 1250.00 | 312500.00 | 175.00 | 43750.00 | 43750.00 | K N RAI
190.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/HUME/ METAL/HDPE pipe as required. a) Upto 35 sq. mm | 250.00 | Metre |  | 100.00 | 25000.00 | 30.00 | 7500.00 | 7500.00 | K N RAI
191.00 | Laying and fixing of one number PVC insulated and PVC sheathed/XLPE power cable of 1.1 KV grade of following size on wall/surface as required. a) Upto 35 sq. mm (clamped with 1mm thick saddle) | 50.00 | Metre |  | 100.00 | 5000.00 | 40.00 | 2000.00 | 2000.00 | K N RAI
192.00 | Supply and laying of 50 mm dia 'B' Class GI Pipe in concrete/bitumen for cable crossing/laying by cutting the bitumen/concrete of suitable size and depth of 600mm for laying the pipe, threading, cutting, jointing of pipe & filling the gaps with concrete 1:2:4 and making good the surface matching with original finish etc. as required and as per the instruction of Engineer-in-charge. | 30.00 | Metre |  | 760.00 | 22800.00 | 1200.00 | 36000.00 | 22800.00 | D B Infratech
193.00 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 1.00 | Jobs |  | 10625.00 | 10625.00 | 7000.00 | 7000.00 | 7000.00 | K N RAI
194.00 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe From earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 10.00 | Metre |  | 760.00 | 7600.00 | 700.00 | 7000.00 | 7000.00 | K N RAI
195.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | 10.00 | Metre |  | 200.00 | 2000.00 | 300.00 | 3000.00 | 2000.00 | D B Infratech
196.00 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing along with existing surface / recessed conduit / submain wiring / cable as required. | 300.00 | Metre |  | 100.00 | 30000.00 | 40.00 | 12000.00 | 12000.00 | K N RAI
197.00 | Supply and making end termination with brass compression gland and aluminium lugs for size 4 X 10 sqmm. of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 kv grade as required. | 20.00 | Job |  | 1020.00 | 20400.00 | 200.00 | 4000.00 | 4000.00 | K N RAI
198.00 | SITC of VRF System, Water Cooler,Hand dryer Supply Installation, Testing & Commissioning of modular type Variable Refrigerant Flow/Variable Refrigerant Volume air cooled Outdoor units suitable for cooling and heating, having all hermetically sealed inverter type Scroll Compressor(s), minimum two compressors for above 18 HP modules, microprocessor based Controller, top discharge type condensing unit(s), with R 410 A Refrigerant, vibration isolators, with suitable foundation including M.S Structure for installing outdoor units.MS STAND for the condenser stand - VRF ODU complete as required. The unit shall deliver the rated capacity at AHRI Conditions and work even at 50°C ambient temperature without tripping. The unit shall be suitable to work on 400V +/- 10%, 3 Phase, 50Hz AC power supply. The unit shall be filled with first charge of the refrigerant and ready for use as required. The COP at AHRI conditions shall not be less than 3.1 and IEER not less than 6.5 . | 3.00 | Each |  | 21250.00 | 63750.00 | 530000.00 | 1590000.00 | 63750.00 | D B Infratech
199.00 | Supply, installation, testing and commissioning of following minimum capacity 4-way flow VRV/VRF Cassette Type 4TR Indoor ceiling mounted unit equipped with synthetic washable media pre-filter, fan section with low noise fan/dynamically balanced blower, multispeed motor, coil section with DX Copper coil, electronic expansion valve, outer cabinet, drain pump, grill, necessary supports, vibration isolation, cord less remote control etc., suitable for operation on single phase 230 V ± 10%, 50Hz AC supply, complete, as required. The unit shall have automatic force shut down provision in case of fire on receiving signal from BMS System. The cooling capacity of indoor unit will be at air inlet conditions of 27 Degree C DB and 19 Degree C WB temperature. | 11.00 | Each |  | 2500.00 | 27500.00 | 40000.00 | 440000.00 | 27500.00 | D B Infratech
200.00 | Supply,Installation,testing and commissioning including vaccumiazation and Nitrogen testing of following nominal sizes of soft/hard drawn copper refrigerant piping for VRV/VRFsystem,complete with fittings,with suitable adjustable ring type hanger supports,jointing/brazing including accessories,insulated with XPLE Class-O tubular insulation/with Class O closed cell elastometric nitrile rubber tubular sleeves sections of specified thickness as given below for Suction and Liquid lines, all accessories as per specifications etc. as required : 9.5 mm dia (OD) (Soft drawn) with tube thickness 1.2 mm with 19 mm thick insulation | 200.00 | Meter |  | 1100.00 | 220000.00 | 320.00 | 64000.00 | 64000.00 | K N RAI
201.00 | Supply, Installation, testing & commissioning of 25 mm Drain Hard uPVC Pipes including bends, supports etc. complete as required. | 200.00 | Meter |  | 400.00 | 80000.00 | 240.00 | 48000.00 | 48000.00 | K N RAI
202.00 | Supply of approved make XLPE armoured cable of size 4 C x 25 sqmm with copper conductor 1.1 KV 650/1100 V grade as per IS 7098 (Part 1) 1988 etc complete as required. | 50.00 | Meter |  | 680.00 | 34000.00 | 2200.00 | 110000.00 | 34000.00 | D B Infratech
203.00 | Supply of approved make XLPE armoured cable of size 4 C x 10 sqmm with copper conductor 1.1 KV 650/1100 V grade as per IS 7098 (Part 1) 1988 etc complete as required. | 100.00 | Meter |  | 600.00 | 60000.00 | 1200.00 | 120000.00 | 60000.00 | D B Infratech
204.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 kV grade of following size on wall/surface as required. Upto 35 sqmm. | 220.00 | Meter |  | 550.00 | 121000.00 | 39.00 | 8580.00 | 8580.00 | K N RAI
205.00 | Supplying and making end termination with brass compression gland and copper lugs for following size of PVC insulated and PVC sheathed / XLPE copper conductor cable of 1.1 kV grade as required.4C X 25 sq. mm | 2.00 | Each |  | 510.00 | 1020.00 | 310.00 | 620.00 | 620.00 | K N RAI
206.00 | Supplying and making end termination with brass compression gland and copper lugs for following size of PVC insulated and PVC sheathed / XLPE copper conductor cable of 1.1 kV grade as required.4C X 10 sq. mm. | 2.00 | Each |  | 500.00 | 1000.00 | 260.00 | 520.00 | 520.00 | K N RAI
207.00 | Supplying and installing following size of perforated painted with powder coating M.S. cable trays with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required 300 mm width X 50 mm depth X 1.6 mm thickness. | 150.00 | Each |  | 1275.00 | 191250.00 | 1200.00 | 180000.00 | 180000.00 | K N RAI
208.00 | Supply, Laying and connecting of unarmoured multi core copper conductor control cable of size 4C x1.5Sq.mm as per the site requirement etc., complete as required. | 50.00 | Each |  | 760.00 | 38000.00 | 120.00 | 6000.00 | 6000.00 | K N RAI
209.00 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing along with existing surface / recessed conduit / submain wiring / cable as required. | 150.00 | Each |  | 100.00 | 15000.00 | 45.00 | 6750.00 | 6750.00 | K N RAI
210.00 | S.I.T.C. of floor mounted self contained drinking water cooler of 80 liters storage and 60 liters cooling capacity with inbuilt UV water purification system with Filter cartridge including with Sediment, activated carbon, UF, post carbon, full stainless steel body suitable for operation on 230 Volts +/- 10%, 50 Hz. Single phase A.C. supply,R134a as Refrigerant, Rotatry type compressor etc.including installation as per site requirement and making connections from existing water line to water cooler etc. as required as per EIC. | 5.00 | Nos. |  | 17000.00 | 85000.00 | 110000.00 | 550000.00 | 85000.00 | D B Infratech
211.00 | Supply of wall mounting hand dryer made up of Stainless steel, non magnetic malt finish with touch free infrared Activation, sensor range 12cm-15cm, hand dryer time less than 30 sec, air speed 95 m/s, blowing cfm greater than 270 m3h etc complete as required.etc complete as required make: Euronics, model: EH 27 NW or AAI approved make | 7.00 | Each |  | 3825.00 | 26775.00 | 11000.00 | 77000.00 | 26775.00 | D B Infratech
212.00 | SITC OF WATER PUMPING SYSTEM SITC of open well horizontal submersible pump set of 10 HP, 7.5 KW motor capacity, suction 80 mm, delivery 80/65 mm suitable for operation on 415 V capable of discharging water range of 20.6-9.5 LPS at head range of 14-40 meters having Cast-Iron delivery casing & motor body, Stainless steel shaft & Bronze impeller complete as required and as per direction of E-I-C. (Approved make: AAI Approved make) | 2.00 | Set |  | 25500.00 | 51000.00 | 44000.00 | 88000.00 | 51000.00 | D B Infratech
213.00 | Supply and laying of PVC insulated and PVC sheathed Flat 3C X 4 Sq. MM Industrial cable for submersible pump motor Copper Conductor armoured cable of 1.1 KV grade confirming to IS:694 with upto date amendments on surface, cable tray, trech etc. complete as required. | 25.00 | Metre |  | 250.00 | 6250.00 | 260.00 | 6500.00 | 6250.00 | D B Infratech
214.00 | Supply, Installation, Testing and Commissioning of DOL Starter suitable for 10 HP size pumping set and operation on 415 volt 3 phase 50 Hz A.C. supply alongwith O/L relay, Single Phasing Preventor, Ammeter, indication lamps and all other standard asscessories complete as required. | 2.00 | Each |  | 2380.00 | 4760.00 | 3400.00 | 6800.00 | 4760.00 | D B Infratech
215.00 | SITC OF FIRE FIGHTING SYSTEM A)PUMP ROOM:Main PUMP: Supply, Installation, testing and commissioning of Electric motor driven fire pumping set suitable for automatic operation consisting as per the below specification & TEFC specification: (a) End suction / high pressure, centrifugal pump, suitable for operation on 415 volts ± 10%, 3 phase, 50 HZ A.C supply. The installation shall be complete with flexible coupling and coupling guard as required. Fire pump shall have C.I. casing, CS diffusers, bronze impeller (hard finished and dynamically balanced) and C-40/SS-410 Shaft with gland type stuffing box, capable for delivering 2850 LPM Pump against a head of 40 meter. | 1.00 | Nos |  | 38250.00 | 38250.00 | 425000.00 | 425000.00 | 38250.00 | D B Infratech
216.00 | BOOSTER PUMP: Supply, Installation, testing and commissioning of End-suction pump, suitable for operation on 415 volts ± 10%, 3 phase, 50 HZ A.C supply. The installation shall be complete with coupling and coupling guard, fire pumps of capacity of 900 LPM Pump against a head of 40 meter. | 1.00 | Nos |  | 38250.00 | 38250.00 | 90000.00 | 90000.00 | 38250.00 | D B Infratech
217.00 | JOCKEY PUMP: Supply, Installation, testing and commissioning of End-suction pump, suitable for operation on 415 volts ± 10%, 3 phase, 50 HZ A.C supply. The installation shall be complete with coupling and coupling guard, fire pumps of capacity of 180 LPM Pump against a head of 40 meter. | 1.00 | Nos |  | 29750.00 | 29750.00 | 140000.00 | 140000.00 | 29750.00 | D B Infratech
218.00 | CONTROL PANEL: Fabricating, supplying & testing sheet cubical pattern fronthinged door floor mounted type panel for above pump comprising of isolation switch, manual strt delta starter with reset, overload, volt meter, ammeter along with CT's selector manual switches & with all components of L & T or simens make. | 1.00 | Set |  | 10200.00 | 10200.00 | 125000.00 | 125000.00 | 10200.00 | D B Infratech
219.00 | NON RETURN VALVE (N.R.V.): Providing, fixing & commissioning of N.R.V. With flanges, nuts, bolts, gasket. Etc. ( PN - 16 ) 150 mm dia | 1.00 | Nos |  | 3825.00 | 3825.00 | 22000.00 | 22000.00 | 3825.00 | D B Infratech
220.00 | BUTTERFLY VALVE: Providing, fixing & commissioning of B.F. valve . With flanges, nuts, bolts, gasket. Etc. (PN - 16) 150 mm dia Gear Operated | 1.00 | Nos |  | 4675.00 | 4675.00 | 14500.00 | 14500.00 | 4675.00 | D B Infratech
221.00 | PRESSURE GUAGE : Providing, fixing & commissioning of approved make Pressure guage | 4.00 | Nos |  | 2720.00 | 10880.00 | 1700.00 | 6800.00 | 6800.00 | K N RAI
222.00 | Air Release Valve : Providing, fixing & commissioning of approved make Pressure guage | 1.00 | Nos |  | 5525.00 | 5525.00 | 3000.00 | 3000.00 | 3000.00 | K N RAI
223.00 | PRESSURE SWITCH : Providing, Fixing & commissioning of approved make Pressure Switch | 1.00 | Nos |  | 3825.00 | 3825.00 | 6200.00 | 6200.00 | 3825.00 | D B Infratech
224.00 | Y-Strainer : Providing, Fixing & commissioning of approved make 150 nb Y-Strainer | 1.00 | Set |  | 4675.00 | 4675.00 | 11500.00 | 11500.00 | 4675.00 | D B Infratech
225.00 | B) SITC of following Downcomer Hydrant system component including all accessories such as pipe, fittings, flanges, reducers, coupling and painting etc complete as required. Hydrant ( First Aid Hose Reel + Hydrant ) | 6.00 | Points |  | 10625.00 | 63750.00 | 15000.00 | 90000.00 | 63750.00 | D B Infratech
226.00 | 150nb GI Pipe - Riser with all type of fittings ( Above Ground ) | 50.00 | Meters |  | 1020.00 | 51000.00 | 4000.00 | 200000.00 | 51000.00 | D B Infratech
227.00 | MS Support ( Chanel, Angle, Support Rod, Clamps | 700.00 | Kg |  | 120.00 | 84000.00 | 125.00 | 87500.00 | 84000.00 | D B Infratech
228.00 | C) SPRINKLER SYSTEM SITC of following Heavy, ‘C’ class M.S. pipes IS 1239 with screwed or welded joints, including all fittings, & MS supports, preparation of Sprinkler pipe network as per plan, by cutting the pipes to correct lengths; and with M.S.threaded fitting used for pipe size Below 50 NB & and using butt welds for 50 NB & above, Fixing with clamps to M.S. brackets / hangers including inserted rubber gaskets, painting, with a coat of Zinc Dichromate primer and two coat of approved Low VOC paint, Presssure Testing of piping shall be given 14 kgs/cm2 pressure for 24 Hrs as per NFPA 13. 100 mm dia ISI | 12.00 | Each |  | 2380.00 | 28560.00 | 1650.00 | 19800.00 | 19800.00 | K N RAI
229.00 | 80mm dia ISI | 9.00 | Each |  | 2210.00 | 19890.00 | 1250.00 | 11250.00 | 11250.00 | K N RAI
230.00 | 65mm dia ISI | 18.00 | Each |  | 2040.00 | 36720.00 | 1040.00 | 18720.00 | 18720.00 | K N RAI
231.00 | 50mm dia ISI | 60.00 | Each |  | 1870.00 | 112200.00 | 800.00 | 48000.00 | 48000.00 | K N RAI
232.00 | 40mm dia ISI | 42.00 | Each |  | 1700.00 | 71400.00 | 750.00 | 31500.00 | 31500.00 | K N RAI
233.00 | 25mm dia ISI | 42.00 | Each |  | 1530.00 | 64260.00 | 760.00 | 31920.00 | 31920.00 | K N RAI
234.00 | SITC of Pendant type sprinkler of 15 NB, Quartzoid bulb type 68 deg. quick Response, with adjustable escutcheon plate in SS 304. | 62.00 | Each |  | 680.00 | 42160.00 | 500.00 | 31000.00 | 31000.00 | K N RAI
235.00 | SITC of Upright type sprinkler of 15 NB, Quartzoid bulb type 79 deg, Quick Response, with SS 304 sprinkler guard if required | 62.00 | Each |  | 810.00 | 50220.00 | 530.00 | 32860.00 | 32860.00 | K N RAI
236.00 | SITC of 25 mm Sprinkler Flexible drop pipes made of Corruggated SS Tubing to with stand 16 Bar pressure with welded reducer on one end to directly accommodate sprinkler & female check nut on the other end to connect to the branch pipe with supports complete with Rosset Plate and required accessories to fix on the False ceiling with adjustable SS bar and clamps. 1500 mm long | 62.00 | Each |  | 760.00 | 47120.00 | 1440.00 | 89280.00 | 47120.00 | D B Infratech
237.00 | Set of following item with required fitting and accessories ( Tapping with building riser) SITC of Cast iron butterfly valve (150NB) for pressure rating PN 1 SITC of Cast iron dual plat NRV (150NB) for pressure rating PN 16 SITC of Flow Switch (150NB) SITC of 50 mm dia Ball valve SITC of Pressure Guage 0 - 16 Kg / cm2 with mounting arrangement and ball valve. | 2.00 | Set |  | 38250.00 | 76500.00 | 60000.00 | 120000.00 | 76500.00 | D B Infratech
238.00 | SITC of Air Vent Valves at Sprinkler Tapoffs with Ball Valve. | 1.00 | Job |  | 8100.00 | 8100.00 | 1250.00 | 1250.00 | 1250.00 | K N RAI
239.00 | Supply & Installation, testing & commissioning of supports (MS angles, channels), anchor fasteners, bolts, nuts, clamps, "U" bolts. Fittings such as reducer, tee, elbow, flanges shall be socket / butt welded, Form A for fire noc for both floor Fire fighting system, Hydro testing etc complete as required. | 2.00 | Job |  | 2125.00 | 4250.00 | 60000.00 | 120000.00 | 4250.00 | D B Infratech
240.00 | D) Fire Extinguisher Supply, installation of ISI mark 4.5 kg CO2 Fire Extinguisher with wall mounting brackets | 4.00 | Nos. |  | 10625.00 | 42500.00 | 6100.00 | 24400.00 | 24400.00 | K N RAI
241.00 | Supply, installation of ISI mark 6Kg ABC Type Stored Pressure Fire Extinguisher with wall mounting brackets | 4.00 | Nos. |  | 12750.00 | 51000.00 | 1900.00 | 7600.00 | 7600.00 | K N RAI
242.00 | SITC of MCP signages | 8.00 | Nos. |  | 5525.00 | 44200.00 | 750.00 | 6000.00 | 6000.00 | K N RAI
243.00 | SITC of Extinguisher Signages | 10.00 | Nos. |  | 4675.00 | 46750.00 | 720.00 | 7200.00 | 7200.00 | K N RAI
244.00 | SITC of Double Sided LED signages | 12.00 | Nos. |  | 3825.00 | 45900.00 | 4750.00 | 57000.00 | 45900.00 | D B Infratech
245.00 | SITC of Fire Evacuation Plan (297mm X 420mm) | 6.00 | Nos. |  | 3000.00 | 18000.00 | 5050.00 | 30300.00 | 18000.00 | D B Infratech
246.00 | E) FIRE ALARM SYSTEM FIRE ALARM SYSTEM EQUIPMENT Make: Notifier Supply of Microprocessor based 2-loop, True Peer-to-Peer Networkable Addressable Fire Alarm Control Panel with minimum 600 characters LCD display, 4000 event plus 1000 alarm log history events, QWERTY keypad for programming. The panel should be equipped with sufficient numbers of loops considering 20% spare capacity in each loop. Each loop shall have a capacity of minimum 300 addressable devices. The panel shall work in degrade mode in case of CPU failure. Four access levels, flash EPROM, 240 volts AC power supply, automatic battery charger, 24 volts sealed lead acid batteries sufficient for 24 hours normal working and 30 mins in alarm condition. The fire alarm panel shall be networkable on fiber optics network without any media convertor & shall data transmission rate minimum 80Mblps on fiber network & minimum 10Mbps on Copper wire network. The network capacity shall be minimum 120 network nodes. Designed to meet UL864, 10th Edition | 2.00 | Nos |  | 210000.00 | 420000.00 | 600000.00 | 1200000.00 | 420000.00 | D B Infratech
247.00 | Supply of Repeater Panel with minimum 8" LCD large color display or 600 character LCD display with control keys like "SILENCE", "RESET" etc. | 2.00 | Nos |  | 2150.00 | 4300.00 | 275000.00 | 550000.00 | 4300.00 | D B Infratech
248.00 | Supply of Addressable Multi-criteria Photo-Thermal Detector with sensitivity range of 0.5 to 4.0% obs/ft.The intelligent multi criteria detection device shall include the ability to combine the signal of the thermal sensor with the signal of the photoelectric signal in an effort to react hastily in the event of a fire situation. It shall also include the inherent ability to distinguish between a fire condition and a false alarm condition by examining the characteristics of the thermal and smoke sensing chambers and comparing them to a database of actual fire and deceptive phenomena. The detector shall have twin bi-colour LED for 360 deg viewing. Addressing shall be with user friendly rotary decimal switches. Designed to meet UL268, 7th Edition | 50.00 | Nos |  | 2500.00 | 125000.00 | 4000.00 | 200000.00 | 125000.00 | D B Infratech
249.00 | Supply of Response indicator for above false ceiling detectors. | 30.00 | Nos |  | 1020.00 | 30600.00 | 100.00 | 3000.00 | 3000.00 | K N RAI
250.00 | Supply of Addressable Rate of Rise Heat Detector rated at 9.4 deg C/min. The detector shall have twin bi-colour LED for 360 deg viewing. Addressing shall be with user friendly rotary decimal switches. | 50.00 | Nos |  | 1020.00 | 51000.00 | 3100.00 | 155000.00 | 51000.00 | D B Infratech
251.00 | Supply of Addressable Manual Call Point (Pull down / Break Glass Type). The device shall have an LED which shall blink in normal state & get steady on activation to monitor the heath status of the device. | 10.00 | Nos |  | 1530.00 | 15300.00 | 3200.00 | 32000.00 | 15300.00 | D B Infratech
252.00 | Supply of Addressable Relay Module for AHU, Access Control, Lifts, Staircase Pressurization, Fire Suppression & other Third Party Outputs. The relay module shall provide DPDTcontact rated at 24V DC, 2A. The device shall have an LED which shall blink in normal state & get steady on activation to monitor the heath status of the device. Addressing shall be with user friendly rotary decimal switches. Module shall be supplied with mounting plate from OEM for ease of installation & maintenance. | 6.00 | Nos |  | 2550.00 | 15300.00 | 3950.00 | 23700.00 | 15300.00 | D B Infratech
253.00 | Supply of Addressable Monitor Module for flow switches, Panic Bars & other Third Party Inputs. The monitor module shall monitor potential free contacts. The device shall have an LED which shall blink in normal state & get steady on activation to monitor the heath status of the device. Addressing shall be with user friendly rotary decimal switches. Module shall be supplied with mounting plate from OEM for ease of installation & maintenance. | 6.00 | Nos |  | 2380.00 | 14280.00 | 3300.00 | 19800.00 | 14280.00 | D B Infratech
254.00 | Supply of Isolator Module for Isolating short / dewired / loose circuits with automatic resetting arrangement. Isolator Base can also be proposed, however in that case needs to be considered with each detector & module. The device shall have an LED which shall blink in normal state & get steady on activation to monitor the heath status of the device. Addressing shall be with user friendly rotary decimal switches. Module shall be supplied with mounting plate from OEM for ease of installation & maintenance. | 6.00 | Nos |  | 12000.00 | 72000.00 | 3500.00 | 21000.00 | 21000.00 | K N RAI
255.00 | Supply of Sounder cum Strobe rated at 75 dBA @ 3m for Audible annunciation and 75cd flashintg at 1 Hz for visual indication. | 6.00 | Nos |  | 3825.00 | 22950.00 | 2600.00 | 15600.00 | 15600.00 | K N RAI
256.00 | Supply of 24VDC power supply unit for sounder cum strobes. The unit shall have in built battery charger & sufficient back of 24 hours in stand by & 30 mins in alarm condition. The power supply unit shall be monitored by fire alarm panel. | 3.00 | Nos |  | 210000.00 | 630000.00 | 61000.00 | 183000.00 | 183000.00 | K N RAI
257.00 | Supply of 2x1.5 sqmm fire alarm armoured cable, 600/1000V rated with annealed copper conductor having XLPE insulation, steel wire armouring & FRLS outer sheath complete as required. | 1500.00 | Metre |  | 120.00 | 180000.00 | 90.00 | 135000.00 | 135000.00 | K N RAI
258.00 | Installation, Testing & commissioning of above systems, etc complete as required. | 1.00 | Job |  | 25500.00 | 25500.00 | 425000.00 | 425000.00 | 25500.00 | D B Infratech
259.00 | LIGHTNING CONDUCTOR Providing and fixing of lightning conductor finial, made of 25 mm dia 300 mm long G.I. tube, having single prong at top, with 85 mm dia 6 mm thick G.I. base plate including holes etc. complete as required. | 2.00 | Each |  | 510.00 | 1020.00 | 500.00 | 1000.00 | 1000.00 | K N RAI
260.00 | Jointing copper / G.I. tape (with another copper/ G I tape, base of the finial or anyother metallic object) by riveting / nut bolting/ sweating and soldering etc as required. | 25.00 | Each |  | 100.00 | 2500.00 | 100.00 | 2500.00 | 2500.00 | D B Infratech, K N RAI
261.00 | Providing and fixing G.I. tape 20 mm X 3 mm thick on parapet or surface of wall for lightning conductor complete as required.(For horizontal run) | 150.00 | Metre |  | 100.00 | 15000.00 | 110.00 | 16500.00 | 15000.00 | D B Infratech
262.00 | Providing and fixing G.I. tape 20 mm X 3 mm thick on parapet or surface of wall for lightning conductor complete as required.(For Vertical run) | 50.00 | Metre |  | 100.00 | 5000.00 | 110.00 | 5500.00 | 5000.00 | D B Infratech
263.00 | Providing and fixing testing joint, made of 20 mm X 3 mm thick G.I. strip, 125 mm long, with 4 nos. of G.I. bolts, nuts, chuck nuts and spring washers etc. complete as required. | 2.00 | Each |  | 700.00 | 1400.00 | 109.00 | 218.00 | 218.00 | K N RAI
264.00 | Providing and laying G.I. tape 32 mm X 6 mm from earth electrode directly in ground as required. | 2.00 | Each |  | 2125.00 | 4250.00 | 200.00 | 400.00 | 400.00 | K N RAI
265.00 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 2.00 | Each |  | 2125.00 | 4250.00 | 6750.00 | 13500.00 | 4250.00 | D B Infratech
| Total in Figures |  |  |  |  | 40862510.65 |  | 43552103.50
Lowest Amount Quoted BY: D B Infratech(40862510.65)

## BOQ Summary
BOQ Summary Details Tender Title: Construction of passenger terminal building along with office block at Juhu Airport. Tender ID: 2022_AAI_116823_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | D B Infratech | 40862510.65 | L1
| 2 | K N RAI | 43552103.50 | L2