## BoQ1
Government eProcurement System Created By: Rudra Prasad Acharya Created Date/Time: 19-Jul-2022 01:09 PM Tender Title: SITC of Street Light Poles and Cable Tender ID: 2022_AAI_117212_1
Tender Inviting Authority: Senior Manager Engg (E), Airports Authority of India, B.P.I.Airport, Bhubaneswar.
Name of Work: Supply & Laying of LT cable for Street Light and allied works. SH:- SITC of Street Light Poles & Cable at B.P.I Airport, Bhubaneswar.
Contract No: 2022_AAI_117212 _1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | RASS CONTRACTOR AND ENGINEERS(GSTN-09AFIPR1600N1Z7) |  | Youngmen Traders(GSTN-19AEIPB6323B1ZZ) |  | EASTERN ENGINEERING(GSTN-21AOHPS4038K1ZU) |  | Awasthi Electric Works(GSTN-09ABAPA1866D1Z5) |  | Krishsons International Engineers And Consultants (I) Pvt. Ltd(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply of 9 meter High GI octagonal pole 3 mm thick with bottom dia 155 mm and top dia of 70 mm with single arm bracket (1 mtr overhang) with end nipple to suite light fixture including GI base plate of 260 x 260 x16mm, PCD-260 MM and 4 numbers of GI Foundation Bolt-M24X750 mm.The pole shall be provided with flush door at the bottom with proper locking arrangment and 01 no 6Amp. MCB with provision of connector for connection of incoming and outgoing cable size 4C X 16 sqm. etc. | 25.00 | Nos |  | 17550.00 | 438750.00 | 15000.00 | 375000.00 | 18500.00 | 462500.00 | 17500.00 | 437500.00 | 16000.00 | 400000.00 | 375000.00 | Youngmen Traders
2.00 | Provision of RCC foundation for erection of metallic pole of following length by providing and laying in position specified grade of reinforced cement concrete.1:1.5:3 (1 cement : 1.5 coarse sand : 3 graded stone aggregate 20 mm nominal size) and providing Steel reinforcement ( Thermo-Mechanically Treated bars of grade Fe-415 or more) for R.C.C. work including straightening, cutting, bending, placing in the foundation of minimum size of 400 mm(L) x 400 mm (W) x 1000 mm (H) including fixing of J bolts, providing minimum 32 mm HDPE pipe in the foundation for looping of cable, excavation and refilling etc. complete as required.
2.01 | 9 Meters | 25.00 | Each |  | 3850.00 | 96250.00 | 3500.00 | 87500.00 | 8200.00 | 205000.00 | 2500.00 | 62500.00 | 3000.00 | 75000.00 | 62500.00 | Awasthi Electric Works
3.00 | Supply of 45watt LED type street light luminaire with single piece die cast aluminium housing including driver,IP 66 of minimum 110lumens/watt output on the existing street light pole suitable to operate 230v, 50Hz single phase AC supply along with accessories etc. complete as required. | 30.00 | Nos |  | 1850.00 | 55500.00 | 1500.00 | 45000.00 | 2550.00 | 76500.00 | 1490.00 | 44700.00 | 1700.00 | 51000.00 | 44700.00 | Awasthi Electric Works
4.00 | Installation, testing & Commissioning of LED street light fitting on existing pole,supplying and drawing 3 X 1.5 sq.m PVC insulated copper couductor single core cable in the pole from fitting to MCB including connection testing and commissioning as required. | 25.00 | Each |  | 250.00 | 6250.00 | 150.00 | 3750.00 | 250.00 | 6250.00 | 150.00 | 3750.00 | 1000.00 | 25000.00 | 3750.00 | Youngmen Traders, Awasthi Electric Works
5.00 | Supply of Junction box of IP 66/ IP67 /IP 69 Thermoplastic PC-GFS Polycarbonate weatherproof junction box with multi-level knockouts for cable glands in different sizes. The Junction box shall have Mounting clamp with M32 gland, 6Amp SP MCB-1no with stud type terminal block complete as required. Minimum Dimension-205x255x112mm. | 60.00 | Each |  | 2250.00 | 135000.00 | 3500.00 | 210000.00 | 1500.00 | 90000.00 | 2500.00 | 150000.00 | 2800.00 | 168000.00 | 90000.00 | EASTERN ENGINEERING
6.00 | Earthing with G.I. earth pipe 4.5 meter long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 6.00 | Set |  | 3500.00 | 21000.00 | 6000.00 | 36000.00 | 15000.00 | 90000.00 | 6000.00 | 36000.00 | 4500.00 | 27000.00 | 21000.00 | RASS CONTRACTOR AND ENGINEERS
7.00 | Earthing with G.I. earth plate 600mm x 600mm x 6mm thick including accessories and providing masonary enclosure with cover plate having locking arrangement and watering pipe etc. including charcoal and salt complete as required. | 4.00 | Each |  | 6500.00 | 26000.00 | 7000.00 | 28000.00 | 7000.00 | 28000.00 | 8500.00 | 34000.00 | 5500.00 | 22000.00 | 22000.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
8.00 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing along with existing surface/ recessed conduit/submain wiring/ cable as required. | 1000.00 | Mtr |  | 20.00 | 20000.00 | 18.00 | 18000.00 | 25.00 | 25000.00 | 18.00 | 18000.00 | 20.00 | 20000.00 | 18000.00 | Youngmen Traders, Awasthi Electric Works
9.00 | Main LT Panel-1 (1500x1700x400mm):- Design, fabrication, supply, installation, testing and commissioning of double door, weather proof, dust & vermin proof, duly painted, fully compartmentalised free standing type outdoor type feeder pillar (with IP55 protection) fabricated from 2mm thick CRCA sheet including supply and fixing of following switch gears and accessories complete with bus bars, neutral link, interconnections, CTs, Ammeter and Voltmeter with selector switches and LED phase indicating lamps as required as per enclosed specifications and approved make. The price shall also include the foundation for installation of Panel.: Incoming: (i) 630A, 4P 36KA thermal magnetic releases with variable O/L & S/C - 1 No. (ii) Spreader Link- 1 No. (iii) EROM- 1 No. (iv) R-Y-B indicating lamps- 3 Nos. (v) 6A SP MCB - 10KA- 3 Nos (vi) Digital MFM Meter with RS485 Port - Class-1 - 1No (vii) CT 630/5 Metering CT - 3 Nos Outgoing: (i) 400A, 4P 36KA thermal magnetic releases with variable O/L & S/C protection & Ics=100%Icu - 1 No. (ii) Spreader Link- 1 No. (iii) EROM- 1 No. (iv) 250A, 4P 36KA thermal magnetic releases with variable O/L & S/C protection & Ics=100%Icu - 4 Nos. (v) Spreader Link- 4 Nos. (vi) EROM- 4 Nos. | 1.00 | Each |  | 200000.00 | 200000.00 | 295000.00 | 295000.00 | 350000.00 | 350000.00 | 370000.00 | 370000.00 | 485000.00 | 485000.00 | 200000.00 | RASS CONTRACTOR AND ENGINEERS
10.00 | Main LT panel-2(1400x1450x400mm):- Design, fabrication, supply, installation, testing and commissioning of double door, weather proof, dust & vermin proof, duly painted, fully compartmentalised free standing type outdoor type feeder pillar (with IP55 protection) fabricated from 2mm thick CRCA sheet including supply and fixing of following switch gears and accessories complete with bus bars, neutral link, interconnections, CTs, Ammeter and Voltmeter with selector switches and LED phase indicating lamps as required as per enclosed specifications and approved make.The price shall also include the foundation for installation of Panel: Incoming: (i) 630A, 4P 36KA MCCB with thermal magnetic releases with variable O/L & S/C - 1 No. (ii) Spreader Link- 1 No. (iii) EROM- 1 No. (iv) R-Y-B indicating lamps- 3 Nos. (v) 6A SP MCB - 10KA- 3 Nos (vi) Digital MFM Meter with RS485 Port - Class-1 - 1No (vii) CT 630/5 Metering CT - 3 Nos Outgoing: (i) 250A, 4P 36KA thermal magnetic releases with variable O/L & S/C protection & Ics=100%Icu - 4 Nos. (ii) Spreader Link- 4 Nos. (iii) EROM- 4 Nos. | 1.00 | Each |  | 160000.00 | 160000.00 | 235000.00 | 235000.00 | 465000.00 | 465000.00 | 315000.00 | 315000.00 | 395000.00 | 395000.00 | 160000.00 | RASS CONTRACTOR AND ENGINEERS
11.00 | Feeder Pillar-1(1285x1275x350mm):- Design, fabrication, supply, installation, testing and commissioning of double door, weather proof, dust & vermin proof, duly painted, fully compartmentalised free standing type outdoor type feeder pillar (with IP55 protection) fabricated from 2mm thick CRCA sheet including supply and fixing of following switch gears and accessories complete with bus bars, neutral link, interconnections, CTs, Ammeter and Voltmeter with selector switches and LED phase indicating lamps as required as per enclosed specifications and approved make. The price shall also include the foundation for installation of Panel: Incoming: (i) 250A, 4P 36KA MCCB with thermal magnetic based releases with variable O/L & S/Cprotection & Ics=100%Icu - 1 No. (ii) Spreader Link- 1 No. (iii) EROM- 1 No. (iv) R-Y-B indicating lamps- 3 Nos. (v) 6A SP MCB - 10KA- 3 Nos (vi) Digital MFM Meter with RS485 Port - Class-1 - 1No (vii) CT 250/5 Metering CT - 3 Nos Outgoing: (i) 100A, 4P 25KA MCCB with thermal magnetic releases with variable O/L & S/C protection & Ics=100%Icu - 4 Nos. (ii) Spreader Link- 4 Nos. (iii) EROM- 4 Nos. | 1.00 | Each |  | 100000.00 | 100000.00 | 165000.00 | 165000.00 | 410000.00 | 410000.00 | 158000.00 | 158000.00 | 130000.00 | 130000.00 | 100000.00 | RASS CONTRACTOR AND ENGINEERS
12.00 | Feeder Pillar-2(1500x1575x350mm):- Design, fabrication, supply, installation, testing and commissioning of double door, weather proof, dust & vermin proof, duly painted, fully compartmentalised free standing type outdoor type feeder pillar (with IP55 protection) fabricated from 2mm thick CRCA sheet including supply and fixing of following switch gears and accessories complete with bus bars, neutral link, interconnections, CTs, Ammeter and Voltmeter with selector switches and LED phase indicating lamps as required as per enclosed specifications and approved make. The price shall also include the foundation for installation of Panel: Incoming: (i) 250A, 4P 36KA MCCB with thermal magnetic based releases with variable O/L & S/Cprotection & Ics=100%Icu - 1 No. (ii) Spreader Link- 1 No. (iii) EROM- 1 No. (iv) R-Y-B indicating lamps- 3 Nos. (v) 6A SP MCB - 10KA- 3 Nos (vi) Digital MFM Meter with RS485 Port - Class-1 - 1No (vii) CT 250/5 Metering CT - 3 Nos Outgoing: (i) 100A, 4P 25KA MCCB with thermal magnetic releases with variable O/L & S/C protection & Ics=100%Icu - 9 Nos. (ii) Spreader Link- 9 Nos. (iii) EROM- 9 Nos. | 2.00 | Each |  | 155000.00 | 310000.00 | 245000.00 | 490000.00 | 248000.00 | 496000.00 | 253000.00 | 506000.00 | 180000.00 | 360000.00 | 310000.00 | RASS CONTRACTOR AND ENGINEERS
13.00 | Feeder Pillar-3 (1200x2075x350mm):- Design, fabrication, supply, installation, testing and commissioning of double door, weather proof, dust & vermin proof, duly painted, fully compartmentalised free standing type outdoor type feeder pillar (with IP55 protection) fabricated from 2mm thick CRCA sheet including supply and fixing of following switch gears and accessories complete with bus bars, neutral link, interconnections, CTs, Ammeter and Voltmeter with selector switches and LED phase indicating lamps as required as per enclosed specifications and approved make. The price shall also include the foundation for installation of Panel: Incoming: (i) 250A, 4P 36KA MCCB with thermal magnetic based releases with variable O/L & S/C protection & Ics=100%Icu - 1 No. (ii) Spreader Link- 1 No. (iii) EROM- 1 No. (iv) R-Y-B indicating lamps- 3 Nos. (v) 6A SP MCB - 10KA- 3 Nos (vi) Digital MFM Meter with RS485 Port - Class-1 - 1 No (vii) CT 250/5 Metering CT - 3 Nos Outgoing: (i) 100A, 4P 25KA MCCB with thermal magnetic releases with variable O/L & S/C protection & Ics=100%Icu - 7 Nos. (ii) Spreader Link- 7 Nos. (iii) EROM- 7 Nos. | 2.00 | Each |  | 130000.00 | 260000.00 | 225000.00 | 450000.00 | 201000.00 | 402000.00 | 225000.00 | 450000.00 | 170000.00 | 340000.00 | 260000.00 | RASS CONTRACTOR AND ENGINEERS
14.00 | Feeder Pillar-4 (For CISF Barrack):- Design, fabrication, supply, installation, testing and commissioning of double door, weather proof, dust & vermin proof, duly painted, fully compartmentalised free standing type outdoor type feeder pillar (with IP55 protection) fabricated from 2mm thick CRCA sheet including supply and fixing of following switch gears and accessories complete with bus bars, neutral link, interconnections, CTs, Ammeter and Voltmeter with selector switches and LED phase indicating lamps as required as per enclosed specifications and approved make. The price shall also include the foundation for installation of Panel: Incomer 125A 4P Changeover - 1 No. RYB Indicating Lamps - 6 Nos. 6A SP MCB -10 kA - 6 Nos. Outgoing 100A 4P 25KA MCCB with TM based releases with variable O/L & S/C protection - 2 Nos. Spreader Link - 2 Nos. EROM - 2 Nos. On/Off/Trip Indication - 6 Nos. Aux+TAC - 6 Nos. 63A 4P 25KA MCCB with TM based releases with variable O/L & S/C protection - 2 Nos. Spreader Link - 2 Nos. EROM - 2 Nos. On/Off/Trip Indication - 6 Nos. Aux/TAC - 6 Nos. | 1.00 | Each |  | 95000.00 | 95000.00 | 120000.00 | 120000.00 | 85000.00 | 85000.00 | 125000.00 | 125000.00 | 89800.00 | 89800.00 | 85000.00 | EASTERN ENGINEERING
15.00 | APFC Panel with passive filters. a) Supplying, installation, testing & commissioning of factory built floor mounted auto-manual power factor correction system panel of 125 KVAr capacity having 3 phase, Mixed Di-Electric(total power loss not exceeding 0.50 W/ KVAr) power capacitor in 07 stages. b) The system shall have microprocessor based power factor controller with power conditioner savers using rapid instruction semi conductor micro controller provided in the command module for target P.F. setting with digital P.F. display. The Controller consists: VAR / FIFO / BINARY mode, all three powers, i.e. KVA, KW and KVAR phase wise and system Harmonic in all three phases. All three voltages, phase to phase to neutral, Supports MODBUS - RTU Protocol with RS 485 Port . The controller graphical LCD display window shall be as per manufacturer’s standard and good engineering practice with programmable back light on time. c) The panel should be double door, weather proof, dust & vermin proof, duly painted, fully compartmentalised free standing type outdoor type feeder pillar (with IP55 protection) fabricated from 2mm thick CRCA sheet including supply and fixing of following switch gears and accessories complete with bus bars, neutral link, interconnections, CTs, Ammeter and Voltmeter with selector switches and LED phase indicating lamps as required as per enclosed specifications and approved make: 250 Amp TPN, 36 KA, MCCB - 1 No. LED Indicating light - 07 Sets - Red/ Green
15.01 | Capacitor Banks One numbers binary type automatic power factor sensing and correction relay (16 stages) complete with its all accessories etc. as required. All outgoing MCCB with thermal magnetic release with spreader link and phase barrier. 1 no. TP MCCB of 63 A, 25KA - 4 Nos. 1 no. TP MCCB of 25 A, 25KA - 2 Nos. 1 no. TP MCCB of 16 A, 25KA - 1 No. L.T. Power factor improving capacitor of indoor type suitable for operation on 415 volts AC 3 phase 50 Hz complete with banking arrangement, interconnections with suitable size of copper conductor PVC insulated PVC sheathed unarmoured cable, discharge resistance etc. as required. Bank of 5 KVAr rating - 1 Set Bank of 10 KVAr rating - 2 Sets Bank of 25KVAr rating - 4 Sets | 1.00 | Each |  | 215000.00 | 215000.00 | 290000.00 | 290000.00 | 250000.00 | 250000.00 | 321000.00 | 321000.00 | 240000.00 | 240000.00 | 215000.00 | RASS CONTRACTOR AND ENGINEERS
16.00 | Supply of following size 1.1 kv grade, XLPE insulated and PVC inner sheathed Aluminum /Copper conductor armoured power cable conforming to IS: 7098(Part 1)1988/ IS: 7098 (Part 1) with up to date amendments etc. complete as required.
16.01 | 4C x 16 sq.mm | 2700.00 | Mtr |  | 190.00 | 513000.00 | 120.00 | 324000.00 | 180.00 | 486000.00 | 148.00 | 399600.00 | 140.00 | 378000.00 | 324000.00 | Youngmen Traders
17.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL pipe as required.
17.01 | Upto 35 sq. mm | 2600.00 | Mtr |  | 25.00 | 65000.00 | 30.00 | 78000.00 | 250.00 | 650000.00 | 20.00 | 52000.00 | 18.00 | 46800.00 | 46800.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
18.00 | Rate for each one rupee value of work executed from the DSR-2018 (Electrical) Schedule & cost worked out on the basis of DSR-2018 (Electrical) rates. {For example, if the quoted rate for this item is Rs.0.90, then for executing DSR-2018 (Electrical) schedule works of value Rs.1,00,000.00 at DSR-2018 (Electrical) rates, the quoted amount will be Rs.90,000.00. And if quoted rate for this item is Rs.1.25, then quoted amount for the same will be Rs.1,25,000.00} | 400000.00 | Each |  | 1.45 | 580000.00 | .90 | 360000.00 | 1.50 | 600000.00 | .65 | 260000.00 | .65 | 260000.00 | 260000.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd, Awasthi Electric Works
| Total in Figures |  |  |  |  | 3296750.00 |  | 3610250.00 |  | 5177250.00 |  | 3743050.00 |  | 3512600.00
Lowest Amount Quoted BY: RASS CONTRACTOR AND ENGINEERS(3296750.00)

## BOQ Summary
BOQ Summary Details Tender Title: SITC of Street Light Poles and Cable Tender ID: 2022_AAI_117212_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | RASS CONTRACTOR AND ENGINEERS | 3296750.00 | L1
| 2 | Krishsons International Engineers And Consultants (I) Pvt. Ltd | 3512600.00 | L2
| 3 | Youngmen Traders | 3610250.00 | L3
| 4 | Awasthi Electric Works | 3743050.00 | L4
| 5 | EASTERN ENGINEERING | 5177250.00 | L5