## BoQ1
Government eProcurement System Created By: Kamal Kishore Created Date/Time: 07-Jul-2022 11:20 AM Tender Title: SITC of 1000 KVA, 33 KV/0.433 KV 3 Phase Transformer and other allied works at New ATC Power House at CA, Khajuraho Tender ID: 2022_AAI_117681_1
Tender Inviting Authority: Senior Manager (Engg-Elect.), Airports Authority of India, CA, Khajuraho.
Name of Work: “SITC of 1000 KVA, 33 KV/0.433 KV 3 Phase Transformer and other allied works at New ATC Power House at CA, Khajuraho.”
Contract No: 2022_AAI_117681_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | DOSHI ELECTRIC ENGG. CO.(GSTN-24AAEFD3355K1ZI) |  | Choubay And Co.(Agencies) Pvt.Ltd.(GSTN-09AAACC6073E1ZT) |  | Manish Electricals(GSTN-22ABLPM9012E1ZY) |  | Mona Generator Services Pvt. Ltd.(GSTN-07AAFCM4263P1ZZ) |  | Awasthi Electric Works(GSTN-09ABAPA1866D1Z5)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply, Installation, Testing & Commissioning of indoor,ONAN,1000 kVA, 33 KV/0.433 kV 3 Phase, 50Hz, Dyn 11, vector group, copper wound class A insulation, distribution transformer associated with winding , oil temperature indicators, Transformer with impedance as per IS, tapping for on Load Tap changing operation from + 5% to -10% in steps of 1.25% on HV side , having cable end boxes on HV side suitable for 3 x 185 sq.mm. XLPE cable of 33 kV grade and 1600 Amp. bus trunking arrangement of LV side with neutral ,all standard accessories,initial filling of transformer oil, supplying and grouting of suitable MS 'C class' channels with wheel locking arrangement and confirming to IS 1180 with eff. Level-1 [Amendment-4], supplying and providing emergency switch for tripping HT VCB & as per specification attached complete in all respects etc as required at site. | 1.00 | Job |  | 3000000.00 | 3000000.00 | 3300000.00 | 3300000.00 | 3400000.00 | 3400000.00 | 2960840.00 | 2960840.00 | 2990000.00 | 2990000.00 | 2960840.00 | Mona Generator Services Pvt. Ltd.
2.00 | Supply, Installation, Testing and Commissioning pre- fabricated sandwich TPN(R,Y,B,N having same current rating) bus trunking suitable for 3 Phase 4 wire, 433 V, 50 Hz AC supply system of aluminium bus bars of rating as specified below complete with bends, expansion joints, flanges, flexible end connections, horizontal supports & fire barriers . Bus trunking system shall be made out of 16 SWG CRCA sheet steel/extruded aluminium sheet powder coated enclosure minimum IP 54 protection . Earthing with 2 runs of aluminium earth strips of suitable size for fault current for 1 second etc including necessary supports,painting etc as per specifications. (Note: The bus trunking shall be measured along the centre line length of enclosure. The aluminium strips which will go inside LT panels & end termination box of transformers shall not be taken into measurement of bus trunking quantity). (a) 1600 Amp TPN Bus Duct | 35.00 | Meter |  | 19000.00 | 665000.00 | 25000.00 | 875000.00 | 25000.00 | 875000.00 | 27000.00 | 945000.00 | 22500.00 | 787500.00 | 665000.00 | DOSHI ELECTRIC ENGG. CO.
3.00 | Laying of one number PVC insulated and PVC sheathed XLPE power cable of 33 KV grade of following size in the existing masonary open duct as required. (a) Above120 sqmm & Upto 400 sq.mm. | 27.00 | Meter |  | 50.00 | 1350.00 | 100.00 | 2700.00 | 100.00 | 2700.00 | 100.00 | 2700.00 | 100.00 | 2700.00 | 1350.00 | DOSHI ELECTRIC ENGG. CO.
4.00 | Supplying and making indoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for following size of 3 core, XLPE aluminium conductor cable of 33 KV grade as required (a) 3Cx185 Sq.mm. | 2.00 | Set |  | 15000.00 | 30000.00 | 4500.00 | 9000.00 | 18000.00 | 36000.00 | 8750.00 | 17500.00 | 23500.00 | 47000.00 | 9000.00 | Choubay And Co.(Agencies) Pvt.Ltd.
5.00 | Earthing with copper earth plate 600mm x 600mm x 3.0mm thick including accessories and providing masonary enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal and salt complete as required. | 2.00 | Set |  | 18000.00 | 36000.00 | 15000.00 | 30000.00 | 16500.00 | 33000.00 | 15750.00 | 31500.00 | 14000.00 | 28000.00 | 28000.00 | Awasthi Electric Works
6.00 | Earthing with GI earth plate 600mm x 600mm x 6.0mm thick including accessories and providing masonary enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal and salt complete as required . | 2.00 | Set |  | 8000.00 | 16000.00 | 4000.00 | 8000.00 | 7000.00 | 14000.00 | 10230.00 | 20460.00 | 9000.00 | 18000.00 | 8000.00 | Choubay And Co.(Agencies) Pvt.Ltd.
7.00 | Providing & fixing of 25mm x 5mm copper strip in 40 mm dia GI Pipe from earth electrode as required. | 50.00 | Meter |  | 1000.00 | 50000.00 | 1400.00 | 70000.00 | 1200.00 | 60000.00 | 1365.00 | 68250.00 | 1750.00 | 87500.00 | 50000.00 | DOSHI ELECTRIC ENGG. CO.
8.00 | Providing & fixing of 25mm x 5mm GI strip in 40 mm dia GI Pipe from earth electrode as required. | 45.00 | Meter |  | 800.00 | 36000.00 | 400.00 | 18000.00 | 580.00 | 26100.00 | 650.00 | 29250.00 | 690.00 | 31050.00 | 18000.00 | Choubay And Co.(Agencies) Pvt.Ltd.
9.00 | Providing & fixing of 25mm x 5mm copper strip on surface or recess for earth connection as required. | 50.00 | Meter |  | 800.00 | 40000.00 | 1200.00 | 60000.00 | 980.00 | 49000.00 | 1100.00 | 55000.00 | 1290.00 | 64500.00 | 40000.00 | DOSHI ELECTRIC ENGG. CO.
10.00 | Providing & fixing of 25mm x 5mm GI strip on surface or recess for earth connection as required. | 60.00 | Meter |  | 100.00 | 6000.00 | 150.00 | 9000.00 | 240.00 | 14400.00 | 250.00 | 15000.00 | 190.00 | 11400.00 | 6000.00 | DOSHI ELECTRIC ENGG. CO.
11.00 | Supplying and fixing of nominal 3.00mm +/- 10% thick, 1000mm wide Antistatic Electric Insulated Synthetic Mat confirming to IS: 15652: 2006 with upto date amendments suitable for 33KV installation alongwith adhesive/ resin, sealing material and similar type of taping on sealing at all joints and corners as per recommendations etc as required. | 20.00 | Sq. meter |  | 800.00 | 16000.00 | 1600.00 | 32000.00 | 1100.00 | 22000.00 | 1575.00 | 31500.00 | 1250.00 | 25000.00 | 16000.00 | DOSHI ELECTRIC ENGG. CO.
| Total in Figures |  |  |  |  | 3896350.00 |  | 4413700.00 |  | 4532200.00 |  | 4177000.00 |  | 4092650.00
Lowest Amount Quoted BY: DOSHI ELECTRIC ENGG. CO.(3896350.00)

## BOQ Summary
BOQ Summary Details Tender Title: SITC of 1000 KVA, 33 KV/0.433 KV 3 Phase Transformer and other allied works at New ATC Power House at CA, Khajuraho Tender ID: 2022_AAI_117681_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | DOSHI ELECTRIC ENGG. CO. | 3896350.00 | L1
| 2 | Awasthi Electric Works | 4092650.00 | L2
| 3 | Mona Generator Services Pvt. Ltd. | 4177000.00 | L3
| 4 | Choubay And Co.(Agencies) Pvt.Ltd. | 4413700.00 | L4
| 5 | Manish Electricals | 4532200.00 | L5