## BoQ1
Government eProcurement System Created By: PADMA P Created Date/Time: 25-Jul-2022 11:50 AM Tender Title: Electrical Works associated with Construction of Satellite Fire Station Tender ID: 2022_AAI_118192_1
Tender Inviting Authority: Asst. General Manager (E-E) - I
Name of Work : Construction of prefabricated satellite fire station near DVOR& on 10 side of runway, store room near the existing fire station and associated works at Calicut International Airport. SH : Electrical works associated with construction of Satellite fire station.
Ref No: AAI/CL/ENGG(E)/147/NIT-05/2022-23 ( E bid Ref : 2022_AAI_118192_1)
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Shantha ELectricals and Engineers Pvt Ltd(GSTN-29AARCS2866G1ZP) |  | M/s LEESHA ELECTRICALS(GSTN-27ABAPW8550C1ZK) |  | surbhi association(GSTN-23AGKPD2522N1ZK)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supplying and Laying of HDPE pipe of 50mm OD of PE 80 PN 6 ISI marked along with all accessories like socket, bend,couplers etc. confirming to IS 4984,complete with fitting and cutting, jointing etc. direct in ground at a depth of 0.8m below the ground level i/c excavation and refilling the trench but excluding sand cushioining and protective etc as required. | 3600.00 | Meter |  | 450.00 | 1620000.00 | 260.00 | 936000.00 | 285.00 | 1026000.00 | 936000.00 | M/s LEESHA ELECTRICALS
2.00 | Supplying of PVC insulated, PVC sheathed, copper conductor Flat Industrial Cable for Submerssible Pumps Power Cable of 1.1 KV grade of following size etc as per IS 694 with upto date amendments etc as required 3 C x 4 sq mm | 60.00 | Meter |  | 150.00 | 9000.00 | 250.00 | 15000.00 | 260.00 | 15600.00 | 9000.00 | Shantha ELectricals and Engineers Pvt Ltd
3.00 | Supplying of XLPE insulated, PVC sheathed, armoured Aluminium conductor Power Cable of 1.1 KV grade of following size etc as per IS 7098 Part-I 1988 with upto date amendments etc as required 4 C x 16 sq mm | 3500.00 | Meter |  | 130.00 | 455000.00 | 260.00 | 910000.00 | 250.00 | 875000.00 | 455000.00 | Shantha ELectricals and Engineers Pvt Ltd
4.00 | Supplying of XLPE insulated, PVC sheathed, armoured Aluminium conductor Power Cable of 1.1 KV grade of following size etc as per IS 7098 Part-I 1988 with upto date amendments etc as required 3.5 C x 35 sq mm | 175.00 | Meter |  | 200.00 | 35000.00 | 235.00 | 41125.00 | 320.00 | 56000.00 | 35000.00 | Shantha ELectricals and Engineers Pvt Ltd
5.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/HUME/STONEWARE/METAL/DWC/HDPE Pipe as required. [Upto 35 Sq. mm] | 3500.00 | Meter |  | 50.00 | 175000.00 | 30.00 | 105000.00 | 45.00 | 157500.00 | 105000.00 | M/s LEESHA ELECTRICALS
6.00 | Supplying and making end termination with brass single compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed/ XLPE aluminium conductor cable of 1.1 KV grade as required. 4 core, 16 sq.mm | 8.00 | Set |  | 550.00 | 4400.00 | 300.00 | 2400.00 | 320.00 | 2560.00 | 2400.00 | M/s LEESHA ELECTRICALS
7.00 | Supplying and making end termination with brass single compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed/ XLPE aluminium conductor cable of 1.1 KV grade as required. 3.5 core, 35 Sq.mm. | 2.00 | Set |  | 750.00 | 1500.00 | 700.00 | 1400.00 | 750.00 | 1500.00 | 1400.00 | M/s LEESHA ELECTRICALS
8.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required. Upto 35 sq. mm (clamped with 1mm thick saddle) | 25.00 | Meter |  | 35.00 | 875.00 | 100.00 | 2500.00 | 90.00 | 2250.00 | 875.00 | Shantha ELectricals and Engineers Pvt Ltd
9.00 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 2.00 | Set |  | 9500.00 | 19000.00 | 8500.00 | 17000.00 | 9500.00 | 19000.00 | 17000.00 | M/s LEESHA ELECTRICALS
10.00 | Supply and fixing of SMC loop in loop out box of inside dimension 240 X 130 X 95 ( equivalent to Sintex make model No.GS-JB-2817) including fixing the box by clamping with a suitable GI pipe in ground ( Minimum Depth 50 cm ) by providing and laying cement concrete (1 cement : 2 coarse sand : 4 graded stone ) base of size 50 cm x 50 cm x 50 cm with suitable 20 A 4 way connector and din rail etc, including making required interconnections as required. | 4.00 | Job |  | 8700.00 | 34800.00 | 1500.00 | 6000.00 | 2500.00 | 10000.00 | 6000.00 | M/s LEESHA ELECTRICALS
11.00 | S&F of Busbar Distribution Box : Supply and fixing of Busbar Distribution Box made out of 14 SWG CRCA sheet steel, of size not less than 700 mm x 480 mm x 210 mm (having IP 65 protection ) having bus bar type power terminals , with proper barrier from each terminal, of current capacity not less than 150 A fixed on the box with suitable supports desirable for connecting up to size 3.5 C x 185 sq.mm armoured Al.conductor cable on required supports from ground by providing suitable foundation along with 2nos of MS Clamps, screws, nuts etc. testing and commissioning etc complete as required. | 1.00 | Job |  | 18000.00 | 18000.00 | 9000.00 | 9000.00 | 20000.00 | 20000.00 | 9000.00 | M/s LEESHA ELECTRICALS
12.00 | S/O LED LIGHT FIXTURES : Supply of LED HighBay light fixtures of wattage not less than 80 W with efficacy minimum 100 lm/w,, CRI ≥ 80,THD ≤10, IP 20 or higher, surge protection ≥ 4 kV, P.F ≥ 0.95, High pressure diecast aluminium/standard alloy housing, warranty period of 5 years from date of completion, total power consumption of not more than 110% of rated power, any of the following make of LED - Nichia/Cree/Osram/Lumiled (Philips)/Sharp/Seoul/Everlite/ Citizen(Japan)/ Bridgelux(USA)/ Samsung and completely complying to the specifications in the tender document | 10.00 | Each |  | 7600.00 | 76000.00 | 6000.00 | 60000.00 | 6200.00 | 62000.00 | 60000.00 | M/s LEESHA ELECTRICALS
13.00 | S/O LED OUTDOOR LIGHT FIXTURES : Supply of LED street light fixtures of wattage less than 40 W with efficacy minimum 110 lm/w,, CRI ≥ 70,THD ≤10, IP 65 or higher, surge protection ≥ 4 kV, P.F ≥ 0.95, High pressure diecast aluminium/standard alloy housing, warranty period of 5 years from date of completion, total power consumption of not more than 110% of rated power, any of the following make of LED - Nichia/Cree/Osram/Lumiled (Philips)/Sharp/Seoul/Everlite/ Citizen(Japan)/ Bridgelux(USA)/ Samsung and completely complying to the specifications in the tender document. | 5.00 | Each |  | 3100.00 | 15500.00 | 3000.00 | 15000.00 | 3200.00 | 16000.00 | 15000.00 | M/s LEESHA ELECTRICALS
14.00 | S/O LED INDOOR LIGHT FIXTURES : Supply of LED recess mounted 2 ft x 2 ft panel light fixtures of wattage 30-35 W with efficacy minimum 100 lm/w,, CRI ≥ 80,THD ≤10, IP 20 or higher, surge protection ≥ 2 kV, P.F ≥ 0.95, High pressure diecast aluminium/standard alloy housing, warranty period of 5 years from date of completion, total power consumption of not more than 110% of rated power, any of the following make of LED - Nichia/Cree/Osram/Lumiled (Philips)/Sharp/Seoul/Everlite/ Citizen(Japan)/ Bridgelux(USA)/ Samsung and completely complying to the specifications in the tender document. | 10.00 | Each |  | 2200.00 | 22000.00 | 2500.00 | 25000.00 | 2850.00 | 28500.00 | 22000.00 | Shantha ELectricals and Engineers Pvt Ltd
15.00 | Wiring for circuit/ submain wiring along with earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed medium class FR PVC conduit as required. 2 X 4 sq. mm + 1 X 4 sq. mm earth wire | 100.00 | Meter |  | 190.00 | 19000.00 | 250.00 | 25000.00 | 265.00 | 26500.00 | 19000.00 | Shantha ELectricals and Engineers Pvt Ltd
16.00 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed medium class FR PVC conduit as required. 2 X 1.5 sq. mm + 1 X 1.5 sq. mm earth wire | 25.00 | Meter |  | 140.00 | 3500.00 | 200.00 | 5000.00 | 215.00 | 5375.00 | 3500.00 | Shantha ELectricals and Engineers Pvt Ltd
17.00 | Supplying and fixing of following sizes of medium class FR PVC conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required. 20 mm | 25.00 | Meter |  | 40.00 | 1000.00 | 50.00 | 1250.00 | 65.00 | 1625.00 | 1000.00 | Shantha ELectricals and Engineers Pvt Ltd
18.00 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor,single core cable in the existing surface/ recessed steel/ PVC conduit as required. 3 x 1.5 sq. mm | 25.00 | Meter |  | 140.00 | 3500.00 | 75.00 | 1875.00 | 95.00 | 2375.00 | 1875.00 | M/s LEESHA ELECTRICALS
19.00 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor,single core cable in the existing surface/ recessed steel/ PVC conduit as required. 3 x 4 sq. mm | 25.00 | Meter |  | 190.00 | 4750.00 | 130.00 | 3250.00 | 160.00 | 4000.00 | 3250.00 | M/s LEESHA ELECTRICALS
20.00 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class FRLS PVC conduit, with modular switch, modular plate, suitable GI/PVC box and earthing the point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable etc. as required. GROUP C | 25.00 | Point |  | 650.00 | 16250.00 | 1000.00 | 25000.00 | 950.00 | 23750.00 | 16250.00 | Shantha ELectricals and Engineers Pvt Ltd
21.00 | Supplying and fixing following way, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator) 8 way (8 + 24), Double door | 1.00 | Each |  | 5900.00 | 5900.00 | 15000.00 | 15000.00 | 11500.00 | 11500.00 | 5900.00 | Shantha ELectricals and Engineers Pvt Ltd
22.00 | Supplying and fixing following rating, four pole, 415 volts, C- curve MCB in the existing MCB DB complete with connections, testing and commissioning etc. as required. 40 A | 1.00 | Each |  | 1900.00 | 1900.00 | 1500.00 | 1500.00 | 1800.00 | 1800.00 | 1500.00 | M/s LEESHA ELECTRICALS
23.00 | Supplying and fixing following rating, four pole, 415 volts, residual current circuit breaker (RCCB), having a sensitivity current 100 mA in the existing MCB DB complete with connections, testing and commissioning etc. as required. 40 A | 1.00 | Each |  | 3200.00 | 3200.00 | 2000.00 | 2000.00 | 3500.00 | 3500.00 | 2000.00 | M/s LEESHA ELECTRICALS
24.00 | Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, 10 kA, “C” curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. Single pole | 20.00 | Each |  | 250.00 | 5000.00 | 300.00 | 6000.00 | 260.00 | 5200.00 | 5000.00 | Shantha ELectricals and Engineers Pvt Ltd
25.00 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing along with existing surface/ recessed conduit/ submain wiring/ cable as required. | 20.00 | Meter |  | 45.00 | 900.00 | 30.00 | 600.00 | 35.00 | 700.00 | 600.00 | M/s LEESHA ELECTRICALS
26.00 | Providing and laying earth connection from earth electrode with 6 SWG dia G.I. Wire in 15 mm dia G.I. pipe from earth electrode including connection with G.I. thimble excavation and re-filling as required. | 225.00 | Meter |  | 110.00 | 24750.00 | 120.00 | 27000.00 | 180.00 | 40500.00 | 24750.00 | Shantha ELectricals and Engineers Pvt Ltd
27.00 | Supplying and fixing following size/ modules, PVC box alongwith modular base & cover plate for modular switches in recess etc as required. 3 Module (100mmX75mm) | 20.00 | Each |  | 240.00 | 4800.00 | 200.00 | 4000.00 | 180.00 | 3600.00 | 3600.00 | surbhi association
28.00 | Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required. 6 pin 15/16 amp socket outlet | 5.00 | Each |  | 220.00 | 1100.00 | 150.00 | 750.00 | 220.00 | 1100.00 | 750.00 | M/s LEESHA ELECTRICALS
29.00 | Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required. 15/16 A Switch | 5.00 | Each |  | 170.00 | 850.00 | 250.00 | 1250.00 | 150.00 | 750.00 | 750.00 | surbhi association
30.00 | Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required. 6 A Switch | 15.00 | Each |  | 95.00 | 1425.00 | 100.00 | 1500.00 | 95.00 | 1425.00 | 1425.00 | Shantha ELectricals and Engineers Pvt Ltd, surbhi association
31.00 | Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required. 3 PIN 6 A socket outlet | 15.00 | Each |  | 160.00 | 2400.00 | 200.00 | 3000.00 | 180.00 | 2700.00 | 2400.00 | Shantha ELectricals and Engineers Pvt Ltd
32.00 | Supplying and fixing of 20 amps, 240 volts, SPN industrial type, socket outlet, with 2 pole and earth, metal enclosed plug top along with 20 amps "C" curve, SP, MCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning etc. as required. | 5.00 | Each |  | 3800.00 | 19000.00 | 1200.00 | 6000.00 | 1500.00 | 7500.00 | 6000.00 | M/s LEESHA ELECTRICALS
33.00 | Supply of 32 A industrial connector 2P +E of IP44 or higher rating, complete with all accessories as required ( Equivalent to Havells Cat no.DHQDA63032/Legrand Cat no.555214). | 1.00 | Each |  | 1100.00 | 1100.00 | 2000.00 | 2000.00 | 3500.00 | 3500.00 | 1100.00 | Shantha ELectricals and Engineers Pvt Ltd
34.00 | Installation, testing and commissioning of pre-wired, LED fitting mentioned in Item No 8, complete with all accessories . directly on false ceiling/ wall, including connection with 1.5 sq. mm FRLS PVC insulated, copper conductor, single core cable and earthing etc. as required. | 15.00 | Each |  | 250.00 | 3750.00 | 1000.00 | 15000.00 | 800.00 | 12000.00 | 3750.00 | Shantha ELectricals and Engineers Pvt Ltd
35.00 | Installation, testing and commissioning of pre-wired High Bay LED fittings of all types, complete with all accessories etc. directly on ceiling /double height truss not less than 8 m , including connection with 1.5 sq. mm RLS PVC insulated, copper conductor, single core cable and earthing etc. as required. | 6.00 | Each |  | 600.00 | 3600.00 | 1000.00 | 6000.00 | 900.00 | 5400.00 | 3600.00 | Shantha ELectricals and Engineers Pvt Ltd
36.00 | Supplying and fixing of suitable dia ( not less than 32 mm) for the item 12 X 2.00 metres long G.I. pipe (medium class) bracket for mounting of LED / fluorescent / HPMV / HPSV street light fitting on pole including bending the pipe to the required shape, 2 nos 40 mm X 3 mm flat iron clamps with nuts, bolts and washer, painting the flat iron with primer and finish paint etc. as required. | 4.00 | Each |  | 3200.00 | 12800.00 | 1500.00 | 6000.00 | 2000.00 | 8000.00 | 6000.00 | M/s LEESHA ELECTRICALS
37.00 | SITC of 1.5 TR split type 5 star AC (inverter type-minimum EER 4.50) consisting of single room unit (evaporator unit) comprising copper coil with cordless remote control and one number outdoor condensing unit (copper coil) with sealed suitable type compressor suitable for operation on 230V, 50Hz. AC supply , working on following refrigerants - R427a/R-410A/R-407C/R-134A/R-404A/R-507A/R-1233zd(E)/R-123ze(E) capable of performing (a) cooling (b) de-humidifying (c) Air-Circulating (d) filtering including fixing the outdoor condenser unit on a raised suitable pedestals duly painted/Metal Stand as per site requirement (Pedestals/Metal Stand included in the scope) and fixing of Evaporator unit including providing and making inter connections between evaporator unit and condensing unit up to a length of 3 mtrs. comprising of the following including first charge of refrigerant, complete as required. The job also includes SITC of suitable stabilizer unit. a) Suitable drain pipe of PVC or as per OEM specification for length upto 10 Metre b) Suitable insulated copper pipe for liquid line or as per OEM specification for length upto 3 Metre. c) Suitable insulated copper pipe for suction or as per OEM specification for length upto 3 Metre d) Suitable FR insulated, PVC sheathed unarmoured multi strand copper cable or as per OEM specification for length upto 3 Metre e) Supply and Fixing of Heavy duty Rigid type PVC pipe / PVC Trunking of suitable size for covering in the liquid line, suction line and multi strand copper cable or as per OEM specification for length upto 3 Metre | 4.00 | Job |  | 57000.00 | 228000.00 | 60000.00 | 240000.00 | 53500.00 | 214000.00 | 214000.00 | surbhi association
38.00 | Providing & laying following size thermally Insulated copper pipe for refrigerant line suitable for the AC unit beyond the standard length received from the factory. 1/4 inch | 15.00 | Meter |  | 350.00 | 5250.00 | 1000.00 | 15000.00 | 1050.00 | 15750.00 | 5250.00 | Shantha ELectricals and Engineers Pvt Ltd
39.00 | Providing & laying 1" Drain pipe for medium duty PVC pipe suitable for the AC unit, beyond the standard length received from the factory. | 5.00 | Meter |  | 280.00 | 1400.00 | 200.00 | 1000.00 | 200.00 | 1000.00 | 1000.00 | M/s LEESHA ELECTRICALS, surbhi association
40.00 | SITC of stand alone type water dispensor unit of minimum 40 ltr/hr capacity with Hot, Normal and Cold water dispensing provision, suitable for working in 220 V 50 Hz Output temperature Cold not more than 18 degree Celcius, Output temperature Hot not more than 85 degree Celcius, with UV Ozone protection including all water connections, electrical cponnections complete as required. | 1.00 | Each |  | 95000.00 | 95000.00 | 25000.00 | 25000.00 | 30000.00 | 30000.00 | 25000.00 | M/s LEESHA ELECTRICALS
41.00 | Supply and Installation of three in one filter 20 inches ( Spun filter, Carbon filter and Iron filter) of any reputed make, for the existing Hot and Cold Dispenser unit along with all piping required for the working of the filter etc complete as required. | 1.00 | Job |  | 19500.00 | 19500.00 | 15000.00 | 15000.00 | 18500.00 | 18500.00 | 15000.00 | M/s LEESHA ELECTRICALS
42.00 | SITC of Open Well submersible pump-motor set, along with all associated accessories, suitable for operation in 415 V 3 phase power supply of 50 Hz with following specifications. Discharge : minimum 1700 LPM Head : minimum 12 meters | 2.00 | Job |  | 35000.00 | 70000.00 | 75000.00 | 150000.00 | 75000.00 | 150000.00 | 70000.00 | Shantha ELectricals and Engineers Pvt Ltd
43.00 | SITC of fully automatic Star Delta Starter set suitable for Open well Submersible pump motor mentioned in the Item No 38. | 2.00 | Job |  | 7800.00 | 15600.00 | 14101.00 | 28202.00 | 18000.00 | 36000.00 | 15600.00 | Shantha ELectricals and Engineers Pvt Ltd
44.00 | SITC of 12 inch Electrical Industrial Gong Bell suitable for operating at a standard voltage of 240 V AC, 50 Hz. | 1.00 | Job |  | 3800.00 | 3800.00 | 10000.00 | 10000.00 | 8511.00 | 8511.00 | 3800.00 | Shantha ELectricals and Engineers Pvt Ltd
| Total in Figures |  |  |  |  | 3065100.00 |  | 2788602.00 |  | 2938471.00
Lowest Amount Quoted BY: M/s LEESHA ELECTRICALS(2788602.00)

## BOQ Summary
BOQ Summary Details Tender Title: Electrical Works associated with Construction of Satellite Fire Station Tender ID: 2022_AAI_118192_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | M/s LEESHA ELECTRICALS | 2788602.00 | L1
| 2 | surbhi association | 2938471.00 | L2
| 3 | Shantha ELectricals and Engineers Pvt Ltd | 3065100.00 | L3