## BoQ1
Government eProcurement System Created By: Amitabh Ranjan Created Date/Time: 05-Aug-2022 01:33 PM Tender Title: Augmentation of Power Supply in Operational Area and Sub-station. Tender ID: 2022_AAI_120087_1
Tender Inviting Authority: <Jt. General Manager, Engg.(Elect), Airports Authority of India, Sri Guru Ram Dass Jee, International Airport, Amritsar - 143101>
Name of Work: <Augmentation of power supply in Operational Area and Sub-station.>
Contract No: <AAI/ASR/ENGG-ELECT/eNIT-02/2022-23>
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | RASS CONTRACTOR AND ENGINEERS(GSTN-09AFIPR1600N1Z7) |  | Power And Instrumentation Guj Ltd(GSTN-24AACCP4292Q1ZW) |  | HIMALAYA GENERATORS(GSTN-09AEDPA0988G1ZL) |  | DOSHI ELECTRIC ENGG. CO.(GSTN-24AAEFD3355K1ZI) |  | shiv electric(GSTN-07AACFS2722H1ZF) |  | Choubay And Co.(Agencies) Pvt.Ltd.(GSTN-09AAACC6073E1ZT) |  | JCC ENGINEERS PRIVATE LIMITED(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply of 1.1 kv grade XPLE insulated and PVC sheathed aluminium conductor armoured cable, confirming to IS:7098 (Part:-l)-1988 with upto date amendments of approved make as required.
1.10 | 3.5 core x 120 sqmm | 400.00 | mtr |  | 900.00 | 360000.00 | 550.00 | 220000.00 | 700.00 | 280000.00 | 1000.00 | 400000.00 | 627.00 | 250800.00 | 535.00 | 214000.00 | 1000.00 | 400000.00 | 214000.00 | Choubay And Co.(Agencies) Pvt.Ltd.
1.20 | 3.5 core x 150 sqmm | 3500.00 | mtr |  | 1000.00 | 3500000.00 | 630.00 | 2205000.00 | 800.00 | 2800000.00 | 1180.00 | 4130000.00 | 693.00 | 2425500.00 | 625.00 | 2187500.00 | 1200.00 | 4200000.00 | 2187500.00 | Choubay And Co.(Agencies) Pvt.Ltd.
1.30 | 3.5 core x 185 sqmm | 1500.00 | mtr |  | 1250.00 | 1875000.00 | 830.00 | 1245000.00 | 1000.00 | 1500000.00 | 1500.00 | 2250000.00 | 861.00 | 1291500.00 | 790.00 | 1185000.00 | 1500.00 | 2250000.00 | 1185000.00 | Choubay And Co.(Agencies) Pvt.Ltd.
1.40 | 3.5 core x 300 sqmm | 2100.00 | mtr |  | 1750.00 | 3675000.00 | 1275.00 | 2677500.00 | 1500.00 | 3150000.00 | 2200.00 | 4620000.00 | 1295.00 | 2719500.00 | 1220.00 | 2562000.00 | 2000.00 | 4200000.00 | 2562000.00 | Choubay And Co.(Agencies) Pvt.Ltd.
1.50 | 3.5 core x 400 sqmm | 500.00 | mtr |  | 2200.00 | 1100000.00 | 1600.00 | 800000.00 | 2000.00 | 1000000.00 | 2900.00 | 1450000.00 | 1656.00 | 828000.00 | 1575.00 | 787500.00 | 2500.00 | 1250000.00 | 787500.00 | Choubay And Co.(Agencies) Pvt.Ltd.
2.00 | Supplying and laying of DWC HDPE pipe (lSI marked) of following sizes along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc.direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc. , complete as required.
2.10 | 90 mm dia (OD-90 mm & ID-76 mm nominal) | 326.00 | mtr |  | 250.00 | 81500.00 | 230.00 | 74980.00 | 225.00 | 73350.00 | 279.00 | 90954.00 | 253.00 | 82478.00 | 230.00 | 74980.00 | 200.00 | 65200.00 | 65200.00 | JCC ENGINEERS PRIVATE LIMITED
2.20 | 120 mm dia (OD-120 mm & ID-103 mm nominal) | 4083.00 | mtr |  | 300.00 | 1224900.00 | 250.00 | 1020750.00 | 375.00 | 1531125.00 | 333.00 | 1359639.00 | 288.00 | 1175904.00 | 255.00 | 1041165.00 | 300.00 | 1224900.00 | 1020750.00 | Power And Instrumentation Guj Ltd
2.30 | 160 mm dia (OD-160 mm & ID-135 mm nominal) | 2575.00 | mtr |  | 450.00 | 1158750.00 | 325.00 | 836875.00 | 500.00 | 1287500.00 | 468.00 | 1205100.00 | 387.00 | 996525.00 | 305.00 | 785375.00 | 400.00 | 1030000.00 | 785375.00 | Choubay And Co.(Agencies) Pvt.Ltd.
2.40 | 200 mm dia (OD-200 mm & ID-175 mm nominal) | 258.00 | mtr |  | 650.00 | 167700.00 | 425.00 | 109650.00 | 750.00 | 193500.00 | 540.00 | 139320.00 | 489.00 | 126162.00 | 370.00 | 95460.00 | 500.00 | 129000.00 | 95460.00 | Choubay And Co.(Agencies) Pvt.Ltd.
3.00 | Providing, laying and fixing G.l. pipe (medium class) of following diameters by proper supports for drain/naala crossing complete in as respect as required.
3.10 | 100 mm dia | 70.00 | mtr |  | 2250.00 | 157500.00 | 1300.00 | 91000.00 | 1450.00 | 101500.00 | 1700.00 | 119000.00 | 1400.00 | 98000.00 | 1200.00 | 84000.00 | 1500.00 | 105000.00 | 84000.00 | Choubay And Co.(Agencies) Pvt.Ltd.
3.20 | 150 mm dia | 108.00 | mtr |  | 3000.00 | 324000.00 | 1925.00 | 207900.00 | 2200.00 | 237600.00 | 2800.00 | 302400.00 | 2080.00 | 224640.00 | 1600.00 | 172800.00 | 2000.00 | 216000.00 | 172800.00 | Choubay And Co.(Agencies) Pvt.Ltd.
4.00 | Supply & laying of GI pipe (medium class) of following diameters in hard soil / surface concrete upto a depth of 40 cms. including excavation and refilling it with 1:2:4 CC to make the surface good etc. as required & as per the direction of Engineer-in-charge.
4.10 | 100 mm dia | 59.00 | mtr |  | 3000.00 | 177000.00 | 1900.00 | 112100.00 | 1750.00 | 103250.00 | 2300.00 | 135700.00 | 1600.00 | 94400.00 | 1400.00 | 82600.00 | 1600.00 | 94400.00 | 82600.00 | Choubay And Co.(Agencies) Pvt.Ltd.
4.20 | 150 mm dia | 64.00 | mtr |  | 3850.00 | 246400.00 | 2450.00 | 156800.00 | 2500.00 | 160000.00 | 3300.00 | 211200.00 | 2280.00 | 145920.00 | 1700.00 | 108800.00 | 2000.00 | 128000.00 | 108800.00 | Choubay And Co.(Agencies) Pvt.Ltd.
5.00 | Supply & Laying of HDPE pipe of following outer/inner dia having 6 KG/cm2 pressure rating through trenchless technology, direct in ground upto the depth of 3 meters including splicing of pipe of size complete as required.
5.10 | 120 mm dia (OD-120 mm & ID-103 mm nominal) | 420.00 | mtr |  | 550.00 | 231000.00 | 1250.00 | 525000.00 | 1350.00 | 567000.00 | 950.00 | 399000.00 | 2000.00 | 840000.00 | 1245.00 | 522900.00 | 1000.00 | 420000.00 | 231000.00 | RASS CONTRACTOR AND ENGINEERS
5.20 | 160 mm dia (OD-160 mm & ID-135 mm nominal) | 410.00 | mtr |  | 750.00 | 307500.00 | 1850.00 | 758500.00 | 1500.00 | 615000.00 | 1200.00 | 492000.00 | 2200.00 | 902000.00 | 1500.00 | 615000.00 | 1600.00 | 656000.00 | 307500.00 | RASS CONTRACTOR AND ENGINEERS
6.00 | Laying of one no. PVC insulated and PVC sheathed / XPLE power cable of 1.1 kv grade of following size in existing RCC/ HUME/ Stoneware/Metal pipe/HDPE etc as required.
6.10 | Above 95 sq. mm and upto 185 sq. mm | 5137.00 | mtr |  | 50.00 | 256850.00 | 75.00 | 385275.00 | 50.00 | 256850.00 | 70.00 | 359590.00 | 100.00 | 513700.00 | 20.00 | 102740.00 | 50.00 | 256850.00 | 102740.00 | Choubay And Co.(Agencies) Pvt.Ltd.
6.20 | Above 185 sq. mm and upto 400 sq. mm | 3436.00 | mtr |  | 65.00 | 223340.00 | 130.00 | 446680.00 | 75.00 | 257700.00 | 90.00 | 309240.00 | 100.00 | 343600.00 | 30.00 | 103080.00 | 100.00 | 343600.00 | 103080.00 | Choubay And Co.(Agencies) Pvt.Ltd.
7.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 kV grade of following size in the existing masonry open duct as required.
7.10 | Above 95 sq. mm and upto 185 sq. mm | 137.00 | mtr |  | 50.00 | 6850.00 | 60.00 | 8220.00 | 50.00 | 6850.00 | 50.00 | 6850.00 | 80.00 | 10960.00 | 20.00 | 2740.00 | 50.00 | 6850.00 | 2740.00 | Choubay And Co.(Agencies) Pvt.Ltd.
7.20 | Above 185 sq. mm and upto 400 sq. mm | 643.00 | mtr |  | 65.00 | 41795.00 | 110.00 | 70730.00 | 75.00 | 48225.00 | 70.00 | 45010.00 | 80.00 | 51440.00 | 24.00 | 15432.00 | 100.00 | 64300.00 | 15432.00 | Choubay And Co.(Agencies) Pvt.Ltd.
8.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 kV grade of following size on wall surface as required.
8.10 | Above 95 sq. mm and upto 185 sq. mm (clamped with 25/40x3mm MS flat clamp) | 20.00 | mtr |  | 50.00 | 1000.00 | 150.00 | 3000.00 | 50.00 | 1000.00 | 370.00 | 7400.00 | 100.00 | 2000.00 | 100.00 | 2000.00 | 100.00 | 2000.00 | 1000.00 | RASS CONTRACTOR AND ENGINEERS, HIMALAYA GENERATORS
8.20 | Above 185 sq. mm and upto 400 sq. mm (clamped with 40x3mm MS flat clamp) | 30.00 | mtr |  | 65.00 | 1950.00 | 175.00 | 5250.00 | 75.00 | 2250.00 | 450.00 | 13500.00 | 100.00 | 3000.00 | 120.00 | 3600.00 | 150.00 | 4500.00 | 1950.00 | RASS CONTRACTOR AND ENGINEERS
9.00 | Laying & fixing of one no. PVC insulated and PVC sheathed / XPLE power cable of 1.1 kv grade of following size on cable tray as required.
9.10 | Above 95 sq. mm and upto 185 sq. mm (clamped with 25/40x3mm MS flat clamp) | 17.00 | mtr |  | 50.00 | 850.00 | 120.00 | 2040.00 | 50.00 | 850.00 | 175.00 | 2975.00 | 100.00 | 1700.00 | 100.00 | 1700.00 | 100.00 | 1700.00 | 850.00 | RASS CONTRACTOR AND ENGINEERS, HIMALAYA GENERATORS
9.20 | Above 185 sq. mm and upto 400 sq. mm (clamped with 40x3mm MS flat clamp) | 96.00 | mtr |  | 65.00 | 6240.00 | 140.00 | 13440.00 | 75.00 | 7200.00 | 210.00 | 20160.00 | 100.00 | 9600.00 | 120.00 | 11520.00 | 150.00 | 14400.00 | 6240.00 | RASS CONTRACTOR AND ENGINEERS
10.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
10.10 | 3½ X 120 sq. mm (45mm) | 2.00 | Job |  | 950.00 | 1900.00 | 490.00 | 980.00 | 1250.00 | 2500.00 | 700.00 | 1400.00 | 1000.00 | 2000.00 | 700.00 | 1400.00 | 500.00 | 1000.00 | 980.00 | Power And Instrumentation Guj Ltd
10.20 | 3½ X 150 sq. mm (50mm) | 6.00 | Job |  | 1250.00 | 7500.00 | 500.00 | 3000.00 | 1350.00 | 8100.00 | 875.00 | 5250.00 | 1200.00 | 7200.00 | 700.00 | 4200.00 | 500.00 | 3000.00 | 3000.00 | JCC ENGINEERS PRIVATE LIMITED, Power And Instrumentation Guj Ltd
10.30 | 3½ X 185 sq. mm (57mm) | 6.00 | Job |  | 1450.00 | 8700.00 | 690.00 | 4140.00 | 1450.00 | 8700.00 | 1050.00 | 6300.00 | 1400.00 | 8400.00 | 800.00 | 4800.00 | 500.00 | 3000.00 | 3000.00 | JCC ENGINEERS PRIVATE LIMITED
10.40 | 3½ X 240 sq. mm (62mm) | 8.00 | Job |  | 1650.00 | 13200.00 | 800.00 | 6400.00 | 1600.00 | 12800.00 | 1225.00 | 9800.00 | 1600.00 | 12800.00 | 1000.00 | 8000.00 | 1000.00 | 8000.00 | 6400.00 | Power And Instrumentation Guj Ltd
10.50 | 3½ X 300 sq. mm (70mm) | 5.00 | Job |  | 2250.00 | 11250.00 | 900.00 | 4500.00 | 2000.00 | 10000.00 | 1400.00 | 7000.00 | 1800.00 | 9000.00 | 1200.00 | 6000.00 | 1000.00 | 5000.00 | 4500.00 | Power And Instrumentation Guj Ltd
10.60 | 3½ X 400 sq. mm (82mm) | 4.00 | Job |  | 3250.00 | 13000.00 | 1200.00 | 4800.00 | 2400.00 | 9600.00 | 1575.00 | 6300.00 | 2000.00 | 8000.00 | 1500.00 | 6000.00 | 1000.00 | 4000.00 | 4000.00 | JCC ENGINEERS PRIVATE LIMITED
11.00 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 kV grade as required.
11.10 | 3½ X 120 sq. mm | 1.00 | Job |  | 4500.00 | 4500.00 | 3200.00 | 3200.00 | 2000.00 | 2000.00 | 3500.00 | 3500.00 | 3800.00 | 3800.00 | 1800.00 | 1800.00 | 2000.00 | 2000.00 | 1800.00 | Choubay And Co.(Agencies) Pvt.Ltd.
11.20 | 3½ X 150 sq. mm | 4.00 | Job |  | 5000.00 | 20000.00 | 3200.00 | 12800.00 | 2500.00 | 10000.00 | 3850.00 | 15400.00 | 3800.00 | 15200.00 | 2000.00 | 8000.00 | 2500.00 | 10000.00 | 8000.00 | Choubay And Co.(Agencies) Pvt.Ltd.
11.30 | 3½ X 185 sq. mm | 3.00 | Job |  | 5500.00 | 16500.00 | 3650.00 | 10950.00 | 3000.00 | 9000.00 | 4200.00 | 12600.00 | 3800.00 | 11400.00 | 2000.00 | 6000.00 | 3000.00 | 9000.00 | 6000.00 | Choubay And Co.(Agencies) Pvt.Ltd.
11.40 | 3½ X 240 sq. mm | 3.00 | Job |  | 6500.00 | 19500.00 | 4400.00 | 13200.00 | 4000.00 | 12000.00 | 4550.00 | 13650.00 | 4000.00 | 12000.00 | 2600.00 | 7800.00 | 3500.00 | 10500.00 | 7800.00 | Choubay And Co.(Agencies) Pvt.Ltd.
11.50 | 3½ X 300 sq. mm | 3.00 | Job |  | 7500.00 | 22500.00 | 5400.00 | 16200.00 | 5000.00 | 15000.00 | 4900.00 | 14700.00 | 4000.00 | 12000.00 | 2750.00 | 8250.00 | 4000.00 | 12000.00 | 8250.00 | Choubay And Co.(Agencies) Pvt.Ltd.
11.60 | 3½ X 400 sq. mm | 1.00 | Job |  | 8500.00 | 8500.00 | 6500.00 | 6500.00 | 6000.00 | 6000.00 | 5250.00 | 5250.00 | 4000.00 | 4000.00 | 3000.00 | 3000.00 | 4500.00 | 4500.00 | 3000.00 | Choubay And Co.(Agencies) Pvt.Ltd.
12.00 | Supplying and making cable route marker with cement concrete1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size) of size 60 cm X 60 cm at the bottom and 50cm X 50 cm at the top with a thickness of 10cm including inscription duly engraved as required. | 12.00 | Job |  | 1250.00 | 15000.00 | 600.00 | 7200.00 | 500.00 | 6000.00 | 525.00 | 6300.00 | 500.00 | 6000.00 | 1000.00 | 12000.00 | 500.00 | 6000.00 | 6000.00 | JCC ENGINEERS PRIVATE LIMITED, HIMALAYA GENERATORS, shiv electric
13.00 | Design, fabrication, supply, installation, testing and commissioning of cubical type, dust & vermin proof, outdoor type, floor mounted electrical Feeder Pillar with IP 54 protection, suitable for 415 V, 3 phase, 50 Hz AC supply system fabricated in compartmentalised design from CRCA sheet steel of 2mm thick for frame work and covers, detachable gland plates of suitable thickness and front hinged door locking arrangment, i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having extendable TPN Aluminum Alloy bus bars of high conductivity, DMC/ SMC bus bar supports and insulators suitable for 1.1 kV. The minimum dimensions of the feeder pillar should be 600 mm (Width) x 300 mm (Depth) x 500 mm (Height). Entire panel shall have a common GI earth bar of size 25mm x 5mm at the rear with 2 Nos. earth studs along with bottom holes (4 nos.) of appropriate size for cable entry. Mounting/Grouting should be done with iron/MS angle with minimum size of 50mm x 50mm x 6mm grouted properly by cement concrete of 1:2:4 ratio up to 0.30 mtr depth and 0.30 mtr above ground level. Wherever directed by Engineer-in-Charge, provision for 02 nos. legs of same size made out of minimum 40 mm dia GI/Al. pipe alongwith breakable coupling to make the feeder pillar frangible has to made. Bus Bar:- 600 Amps of high conductivity Aluminium busbar of minimum size 80 mm x 6 mm x 350 mm for three phase and neutral - 1 Set. Bus bar should have holes with nut bolts for terminating cables of size 3.5x400 sqmm or as directed by Engineer-in-Charge. | 1.00 | Job |  | 195000.00 | 195000.00 | 19000.00 | 19000.00 | 145000.00 | 145000.00 | 28575.00 | 28575.00 | 20000.00 | 20000.00 | 23500.00 | 23500.00 | 15000.00 | 15000.00 | 15000.00 | JCC ENGINEERS PRIVATE LIMITED
14.00 | Design, fabrication, supply, installation, testing and commissioning of cubical type, dust & vermin proof, outdoor type, floor mounted electrical Feeder Pillar with IP 54 protection, suitable for 415 V, 3 phase, 50 Hz AC supply system fabricated in compartmentalised design from CRCA sheet steel of 2mm thick for frame work and covers, detachable gland plates of suitable thickness and front hinged door locking arrangment, i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having extendable TPN Aluminum Alloy bus bars of high conductivity, DMC/ SMC bus bar supports and insulators suitable for 1.1 kV. The minimum dimensions of the feeder pillar should be 600 mm (Width) x 300 mm (Depth) x 500 mm (Height). Entire panel shall have a common GI earth bar of size 25mm x 5mm at the rear with 2 Nos. earth studs along with bottom holes (4 nos.) of appropriate size for cable entry. Mounting/Grouting should be done with iron/MS angle with minimum size of 50mm x 50mm x 6mm grouted properly by cement concrete of 1:2:4 ratio up to 0.30 mtr depth and 0.30 mtr above ground level. Wherever directed by Engineer-in-Charge, provision for 02 nos. legs of same size made out of minimum 40 mm dia GI/Al. pipe alongwith breakable coupling to make the feeder pillar frangible has to made. Bus Bar:- 300 Amps of high conductivity Aluminium busbar of minimum size 50 mm x 5 mm x 350 mm for three phase and neutral - 1 Set. Bus bar should have holes with nut bolts for terminating cables of size 3.5x120/3.5x150/3.5x185 sqmm or as directed by Engineer-in-Charge. | 10.00 | Job |  | 175000.00 | 1750000.00 | 19000.00 | 190000.00 | 85000.00 | 850000.00 | 27370.00 | 273700.00 | 20000.00 | 200000.00 | 19000.00 | 190000.00 | 15000.00 | 150000.00 | 150000.00 | JCC ENGINEERS PRIVATE LIMITED
15.00 | Design, fabrication, supply, installation, testing and commissioning of cubical type, dust & vermin proof, outdoor type, floor mounted electrical Feeder Pillar with IP 54 protection, suitable for 415 V, 3 phase, 50 Hz AC supply system fabricated in compartmentalised design from CRCA sheet steel of 2mm thick for frame work and covers, detachable gland plates of suitable thickness and front hinged door locking arrangment, i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having extendable TPN Aluminum Alloy bus bars of high conductivity, DMC/ SMC bus bar supports and insulators suitable for 1.1 kV. The minimum dimensions of the feeder pillar should be 600 mm (Width) x 300 mm (Depth) x 500 mm (Height). Entire panel shall have a common GI earth bar of size 25mm x 5mm at the rear with 2 Nos. earth studs along with bottom holes (4 nos.) of appropriate size for cable entry. Mounting/Grouting should be done with iron/MS angle with minimum size of 50mm x 50mm x 6mm grouted properly by cement concrete of 1:2:4 ratio up to 0.30 mtr depth and 0.30 mtr above ground level. Wherever directed by Engineer-in-Charge, provision for 02 nos. legs of same size made out of minimum 40 mm dia GI/Al. pipe alongwith breakable coupling to make the feeder pillar frangible has to made. Bus Bar:- 500 Amps of high conductivity Aluminium busbar of minimum size 75 mm x 6 mm x 350 mm for three phase and neutral - 1 Set. Bus bar should have holes with nut bolts for terminating cables of size 3.5x240/3.5x300 sqmm or as directed by Engineer-in-Charge. | 6.00 | Job |  | 165000.00 | 990000.00 | 19000.00 | 114000.00 | 130000.00 | 780000.00 | 28175.00 | 169050.00 | 20000.00 | 120000.00 | 20000.00 | 120000.00 | 15000.00 | 90000.00 | 90000.00 | JCC ENGINEERS PRIVATE LIMITED
16.00 | Design, fabrication, supply, installation, testing and commissioning of cubical type, dust & vermin proof, outdoor type, floor mounted electrical Feeder Pillar with IP 54 protection, suitable for 415 V, 3 phase, 50 Hz AC supply system fabricated in compartmentalised design from CRCA sheet steel of 2mm thick for frame work and covers, detachable gland plates of suitable thickness and front hinged door locking arrangment, i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having extendable TPN Aluminum Alloy bus bars of high conductivity, DMC/ SMC bus bar supports and insulators suitable for 1.1 kV. The minimum dimensions of the feeder pillar should be 1000 mm (Width) x 400 mm (Depth) x 600 mm (Height). Entire panel shall have a common GI earth bar of size 25mm x 5mm at the rear with 2 Nos. earth studs along with bottom holes (4 nos.) of appropriate size for cable entry. Mounting/Grouting should be done with iron/MS angle with minimum size of 50mm x 50mm x 6mm grouted properly by cement concrete of 1:2:4 ratio up to 0.30 mtr depth and 0.30 mtr above ground level. Wherever directed by Engineer-in-Charge, provision for 02 nos. legs of same size made out of minimum 40 mm dia GI/Al. pipe alongwith breakable coupling to make the feeder pillar frangible has to made. Bus Bar:- 400 Amps of high conductivity Aluminium busbar of minimum size 50 mm x 6 mm x 350 mm for three phase and neutral - 1 Set. Bus bar should have holes with nut bolts for terminating cables of size 3.5x150/3.5x185 sqmm or as directed by Engineer-in-Charge. Change-over-Switch: 320A on-load - 1 no. inside the feeder pillar with 2 inputs and 1 output. | 2.00 | Job |  | 145000.00 | 290000.00 | 53000.00 | 106000.00 | 150000.00 | 300000.00 | 104650.00 | 209300.00 | 40000.00 | 80000.00 | 58000.00 | 116000.00 | 75000.00 | 150000.00 | 80000.00 | shiv electric
17.00 | Supply of 3 core x 35 Sqmm. 11 kV(E) grade stranded compact circular aluminium conductor, conductor screen with extruded semi conducting compound, XLPE insulated, insulation screening with extruded semi conducting compound in combination with copper tape, cores laid up, inner sheath of PVC, Galvanized steel flat strip armoured and overall PVC sheathed cable conforming to IS 7098 Part-II, 2011 with the latest amendments and as specified. | 700.00 | mtr |  | 1150.00 | 805000.00 | 500.00 | 350000.00 | 1000.00 | 700000.00 | 810.00 | 567000.00 | 450.00 | 315000.00 | 475.00 | 332500.00 | 750.00 | 525000.00 | 315000.00 | shiv electric
18.00 | Supplying and making straight through cable jointing with heat shrinkable jointing kit complete with all accessories including ferrules suitable for 35 sqmm, 3 core, XLPE aluminium conductor cable of 11 KV grade as required. | 3.00 | Job |  | 35000.00 | 105000.00 | 17000.00 | 51000.00 | 5000.00 | 15000.00 | 8750.00 | 26250.00 | 6000.00 | 18000.00 | 8500.00 | 25500.00 | 10000.00 | 30000.00 | 15000.00 | HIMALAYA GENERATORS
19.00 | Supplying and making indoor cable end termination with heat shrinkable jointing kit complete with all accessories including compression glands (if required) and lugs suitable for 35 sqmm, 3 core, XLPE aluminium conductor cable of 11 kV grade as required. | 1.00 | Job |  | 45000.00 | 45000.00 | 12000.00 | 12000.00 | 4500.00 | 4500.00 | 5250.00 | 5250.00 | 5000.00 | 5000.00 | 4000.00 | 4000.00 | 8000.00 | 8000.00 | 4000.00 | Choubay And Co.(Agencies) Pvt.Ltd.
20.00 | Supplying and laying of DWC HDPE pipe (lSI marked) of following sizes along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc.direct in ground (1.2 mtr below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required. 120 mm dia (OD-120 mm & ID-103 mm nominal) | 391.00 | mtr |  | 550.00 | 215050.00 | 300.00 | 117300.00 | 875.00 | 342125.00 | 410.00 | 160310.00 | 365.00 | 142715.00 | 300.00 | 117300.00 | 300.00 | 117300.00 | 117300.00 | JCC ENGINEERS PRIVATE LIMITED, Power And Instrumentation Guj Ltd, Choubay And Co.(Agencies) Pvt.Ltd.
21.00 | Providing, laying and fixing G.l. pipe (medium class) of following diameters by proper supports for drain/naala crossing complete in as respect as required. 150 mm dia | 14.00 | mtr |  | 3500.00 | 49000.00 | 1875.00 | 26250.00 | 2200.00 | 30800.00 | 4375.00 | 61250.00 | 2100.00 | 29400.00 | 1700.00 | 23800.00 | 2000.00 | 28000.00 | 23800.00 | Choubay And Co.(Agencies) Pvt.Ltd.
22.00 | Supply & Laying of HDPE pipe of following outer/inner dia having 6 KG/cm2 pressure rating through trenchless technology, direct in ground upto the depth of 3 meters including splicing of pipe of size complete as required. 120 mm dia (OD-120 mm & ID-103 mm nominal) | 292.00 | mtr |  | 675.00 | 197100.00 | 1100.00 | 321200.00 | 850.00 | 248200.00 | 1350.00 | 394200.00 | 1200.00 | 350400.00 | 1245.00 | 363540.00 | 1200.00 | 350400.00 | 197100.00 | RASS CONTRACTOR AND ENGINEERS
23.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 11 kV grade of following size in existing RCC/ HUME/ Stoneware/Metal pipe/HDPE etc as required. Upto 120 sqmm | 762.00 | mtr |  | 85.00 | 64770.00 | 75.00 | 57150.00 | 50.00 | 38100.00 | 70.00 | 53340.00 | 100.00 | 76200.00 | 30.00 | 22860.00 | 100.00 | 76200.00 | 22860.00 | Choubay And Co.(Agencies) Pvt.Ltd.
24.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 11 kV grade of following size in existing masonry open duct as required. Upto 120 sqmm | 149.00 | mtr |  | 85.00 | 12665.00 | 60.00 | 8940.00 | 50.00 | 7450.00 | 70.00 | 10430.00 | 100.00 | 14900.00 | 20.00 | 2980.00 | 50.00 | 7450.00 | 2980.00 | Choubay And Co.(Agencies) Pvt.Ltd.
25.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 11 kV grade of following size on cable tray as required. 35 sqmm (clamped with 40x3mm or suitable size MS flat clamp) | 39.00 | mtr |  | 85.00 | 3315.00 | 120.00 | 4680.00 | 50.00 | 1950.00 | 190.00 | 7410.00 | 100.00 | 3900.00 | 80.00 | 3120.00 | 100.00 | 3900.00 | 1950.00 | HIMALAYA GENERATORS
26.00 | Design, fabrication, supply, installation, testing and commissioning of outdoor type IP54 rated dust & vermin proof floor mounted electrical panel, fabricated in compartmentalized design from 2 mm thick CRCA sheet steel, complete with 7 tank process for powder coating in approved shade, with extensible aluminium bus bars with SMC busbar supports, short circuit withstand capacity of minimum 25 kA for 1 sec, copper earth strips of standard size & studs, gland plates of suitable thickness, cable alleys of suitable size for cable routing etc. complete with metering instruments, LED indicating lamps & accessories suitable for operation on 415 V, 50 Hz AC system including control wiring, interlocking arrangement between incomers & buscouplers, protections etc. suitable/compatible with following switchgears & instruments. INCOMERS MCCB FP 250A, 25KA Ics = 100% Icu with built in thermal magnetic release- 3 Nos BUSBARS Extensible TPN aluminium main busbars of minimum 800A and auxiliary busbars of suitable ratings with sleeves, SMC supports at specified intervals etc.- 01 set BUS COUPLERS MCCB FP 250A, 25kA Ics = 100% Icu with built in thermal magnetic release- 2 Nos OUTGOINGS MCCB FP 125A, 25kA Ics = 100% Icu with built in thermal magnetic release- 3 Nos MCCB FP 63A, 25kA Ics = 100% Icu with built in thermal magnetic release- 9 Nos INSTRUMENTATION & METERING All incoming and outgoing supplies should have digital MFM showing voltage & current levels along with selector switches, CTs/PTs of appropriate capacities & ratios, LED indication lamps as per system requirement. Mounting/Grouting of the panel should be done with iron/MS angle of suitable size grouted properly in foundation with cement concrete of 1:2:4 ratio. Wherever directed by Engineer-in-Charge, provision for 04 nos. legs of same size made out of minimum 60 mm dia GI/Al. pipe alongwith breakable coupling to make the feeder pillar frangible has to made. | 1.00 | Job |  | 295000.00 | 295000.00 | 243000.00 | 243000.00 | 775000.00 | 775000.00 | 1126600.00 | 1126600.00 | 500000.00 | 500000.00 | 615000.00 | 615000.00 | 750000.00 | 750000.00 | 243000.00 | Power And Instrumentation Guj Ltd
27.00 | Design, fabrication, supply, installation, testing and commissioning of outdoor type IP54 rated dust & vermin proof floor mounted electrical panel, fabricated in compartmentalized design from 2 mm thick CRCA sheet steel, complete with 7 tank process for powder coating in approved shade, with extensible aluminium bus bars with SMC busbar supports, short circuit withstand capacity of minimum 25 kA for 1 sec, copper earth strips of standard size & studs, gland plates of suitable thickness, cable alleys of suitable size for cable routing etc. complete with metering instruments, LED indicating lamps & accessories suitable for operation on 415 V, 50 Hz AC system including control wiring, interlocking arrangement between incomers & buscouplers, protections etc. suitable/compatible with following switchgears & instruments. INCOMERS MCCB FP 125A, 25KA Ics = 100% Icu with built in thermal magnetic release- 2 Nos BUSBARS Extensible TPN aluminium main busbars of minimum 300A and auxiliary busbars of suitable ratings with sleeves, SMC supports at specified intervals etc.- 01 set BUS COUPLERS MCCB FP 125A, 25kA Ics = 100% Icu with built in thermal magnetic release- 1 Nos OUTGOINGS MCCB FP 100A, 25kA Ics = 100% Icu with built in thermal magnetic release- 2 Nos MCCB FP 63A, 25kA Ics = 100% Icu with built in thermal magnetic release- 2 Nos MCCB FP 25A, 25kA Ics = 100% Icu with built in thermal magnetic release- 2 Nos INSTRUMENTATION & METERING All incoming and outgoing supplies should have digital MFM showing voltage & current levels along with selector switches, CTs/PTs of appropriate capacities & ratios, LED indication lamps as per system requirement. Mounting/Grouting of the panel should be done with iron/MS angle of suitable size grouted properly in foundation with cement concrete of 1:2:4 ratio. Wherever directed by Engineer-in-Charge, provision for 04 nos. legs of same size made out of minimum 60 mm dia GI/Al. pipe alongwith breakable coupling to make the feeder pillar frangible has to made. | 2.00 | Job |  | 265000.00 | 530000.00 | 531000.00 | 1062000.00 | 500000.00 | 1000000.00 | 518800.00 | 1037600.00 | 300000.00 | 600000.00 | 290000.00 | 580000.00 | 375000.00 | 750000.00 | 530000.00 | RASS CONTRACTOR AND ENGINEERS
28.00 | Design, fabrication, supply, installation, testing and commissioning of outdoor type IP54 rated dust & vermin proof floor mounted electrical panel, fabricated in compartmentalized design from 2 mm thick CRCA sheet steel, complete with 7 tank process for powder coating in approved shade, with extensible aluminium bus bars with SMC busbar supports, short circuit withstand capacity of minimum 50 kA for 1 sec, copper earth strips of standard size & studs, gland plates of suitable thickness, cable alleys of suitable size for cable routing etc. complete with metering instruments, LED indicating lamps & accessories suitable for operation on 415 V, 50 Hz AC system including control wiring, interlocking arrangement between incomers & buscouplers, protections etc. suitable/compatible with following switchgears & instruments. INCOMERS MCCB FP 400A, 50KA Ics = 100% Icu with built in thermal magnetic release- 3 Nos BUSBARS Extensible TPN aluminium main busbars of minimum 1600A and auxiliary busbars of suitable ratings with sleeves, SMC supports at specified intervals etc.- 01 set BUS COUPLERS MCCB FP 400A, 50kA Ics = 100% Icu with built in thermal magnetic release- 2 Nos OUTGOINGS MCCB FP 250A, 25kA Ics = 100% Icu with built in thermal magnetic release- 3 Nos MCCB FP 125A, 25kA Ics = 100% Icu with built in thermal magnetic release- 6 Nos INSTRUMENTATION & METERING All incoming and outgoing supplies should have digital MFM showing voltage & current levels along with selector switches, CTs/PTs of appropriate capacities & ratios, LED indication lamps as per system requirement. Mounting/Grouting of the panel should be done with iron/MS angle of suitable size grouted properly in foundation with cement concrete of 1:2:4 ratio. Wherever directed by Engineer-in-Charge, provision for 04 nos. legs of same size made out of minimum 60 mm dia GI/Al. pipe alongwith breakable coupling to make the feeder pillar frangible has to made. | 1.00 | Job |  | 425000.00 | 425000.00 | 612000.00 | 612000.00 | 875000.00 | 875000.00 | 1102500.00 | 1102500.00 | 600000.00 | 600000.00 | 700000.00 | 700000.00 | 800000.00 | 800000.00 | 425000.00 | RASS CONTRACTOR AND ENGINEERS
29.00 | Design, fabrication, supply, installation, testing and commissioning of outdoor type IP54 rated dust & vermin proof floor mounted electrical panel, fabricated in compartmentalized design from 2 mm thick CRCA sheet steel, complete with 7 tank process for powder coating in approved shade, with extensible aluminium bus bars with SMC busbar supports, short circuit withstand capacity of minimum 25 kA for 1 sec, copper earth strips of standard size & studs, gland plates of suitable thickness, cable alleys of suitable size for cable routing etc. complete with metering instruments, LED indicating lamps & accessories suitable for operation on 415 V, 50 Hz AC system including control wiring, interlocking arrangement between incomers & buscouplers, protections etc. suitable/compatible with following switchgears & instruments. INCOMERS MCCB FP 250A, 25KA Ics = 100% Icu with built in thermal magnetic release- 2 Nos BUSBARS Extensible TPN aluminium main busbars of minimum 600A and auxiliary busbars of suitable ratings with sleeves, SMC supports at specified intervals etc.- 01 set BUS COUPLERS MCCB FP 250A, 25kA Ics = 100% Icu with built in thermal magnetic release- 1 Nos OUTGOINGS MCCB FP 125A, 25kA Ics = 100% Icu with built in thermal magnetic release- 2 Nos MCCB FP 63A, 25kA Ics = 100% Icu with built in thermal magnetic release- 4 Nos INSTRUMENTATION & METERING All incoming and outgoing supplies should have digital MFM showing voltage & current levels along with selector switches, CTs/PTs of appropriate capacities & ratios, LED indication lamps as per system requirement. Mounting/Grouting of the panel should be done with iron/MS angle of suitable size grouted properly in foundation with cement concrete of 1:2:4 ratio. Wherever directed by Engineer-in-Charge, provision for 04 nos. legs of same size made out of minimum 60 mm dia GI/Al. pipe alongwith breakable coupling to make the feeder pillar frangible has to made. | 1.00 | Job |  | 325000.00 | 325000.00 | 305000.00 | 305000.00 | 375000.00 | 375000.00 | 577500.00 | 577500.00 | 300000.00 | 300000.00 | 330000.00 | 330000.00 | 400000.00 | 400000.00 | 300000.00 | shiv electric
30.00 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required | 29.00 | Job |  | 8500.00 | 246500.00 | 7000.00 | 203000.00 | 4500.00 | 130500.00 | 11000.00 | 319000.00 | 8000.00 | 232000.00 | 7000.00 | 203000.00 | 7500.00 | 217500.00 | 130500.00 | HIMALAYA GENERATORS
31.00 | Supplying and laying 25 mm X 5 mm G.I strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with G.I. nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of G.I. nut bolt & spring washer spaced at 50mm) | 252.00 | Mtr |  | 325.00 | 81900.00 | 150.00 | 37800.00 | 100.00 | 25200.00 | 400.00 | 100800.00 | 200.00 | 50400.00 | 249.00 | 62748.00 | 150.00 | 37800.00 | 25200.00 | HIMALAYA GENERATORS
32.00 | Providing and fixing 25 mm X 5 mm G.I.strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut,bolt, spring, washer excavation and re-filling etc. as required. | 87.00 | Mtr |  | 700.00 | 60900.00 | 650.00 | 56550.00 | 550.00 | 47850.00 | 1150.00 | 100050.00 | 587.00 | 51069.00 | 700.00 | 60900.00 | 650.00 | 56550.00 | 47850.00 | HIMALAYA GENERATORS
33.00 | Providing and fixing 25 mm X5 mm G.I. strip on surface or in recess for connections etc. as required. | 29.00 | Mtr |  | 425.00 | 12325.00 | 230.00 | 6670.00 | 100.00 | 2900.00 | 300.00 | 8700.00 | 180.00 | 5220.00 | 240.00 | 6960.00 | 200.00 | 5800.00 | 2900.00 | HIMALAYA GENERATORS
| Total in Figures |  |  |  |  | 21985700.00 |  | 15973100.00 |  | 20987025.00 |  | 24515303.00 |  | 16963333.00 |  | 14742850.00 |  | 21709600.00
Comparative Chart(eAuction)
Sl.No | Bidder Name | Auction Start Price | Quoted Rate in Figures and Words
|  |  | Bidder Price | Amount in Words
1 | Power And Instrumentation Guj Ltd | 14742850.00 | 12942850.00 | One Crore Twenty Nine Lakh Fourty Two Thousand Eight Hundred and Fifty
2 | DOSHI ELECTRIC ENGG. CO. | 14742850.00 | Not Quoted | Not Quoted
3 | shiv electric | 14742850.00 | Not Quoted | Not Quoted
4 | Choubay And Co.(Agencies) Pvt.Ltd. | 14742850.00 | Not Quoted | Not Quoted
5 | RASS CONTRACTOR AND ENGINEERS | 14742850.00 | 13042850.00 | One Crore Thirty Lakh Fourty Two Thousand Eight Hundred and Fifty
6 | HIMALAYA GENERATORS | 14742850.00 | Not Quoted | Not Quoted
7 | JCC ENGINEERS PRIVATE LIMITED | 14742850.00 | 13142850.00 | One Crore Thirty One Lakh Fourty Two Thousand Eight Hundred and Fifty
Lowest Amount Quoted BY: Power And Instrumentation Guj Ltd(12942850.00)

## BOQ Summary
BOQ Summary Details Tender Title: Augmentation of Power Supply in Operational Area and Sub-station. Tender ID: 2022_AAI_120087_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Choubay And Co.(Agencies) Pvt.Ltd. | 14742850.00 | L1
| 2 | Power And Instrumentation Guj Ltd | 15973100.00 | L2
| 3 | shiv electric | 16963333.00 | L3
| 4 | HIMALAYA GENERATORS | 20987025.00 | L4
| 5 | JCC ENGINEERS PRIVATE LIMITED | 21709600.00 | L5
| 6 | RASS CONTRACTOR AND ENGINEERS | 21985700.00 | L6
| 7 | DOSHI ELECTRIC ENGG. CO. | 24515303.00 | L7