## BoQ1
Government eProcurement System Created By: Dadan Singh Created Date/Time: 17-Aug-2022 11:59 AM Tender Title: Miscellaneous Maintenance Electrical works related to NITB. SH. Overhauling, Servicing and Testing of Schneider Make ACB installed at NITB at Raja Bhoj Airport, Bhopal for the year 2022-23. Tender ID: 2022_AAI_122389_1
Tender Inviting Authority: AGM(E-E), AAI, R.B. Airport, Bhopal
Name of Work: Miscellaneous Maintenance Electrical works related to NITB. SH: Overhauling, Servicing & Testing of Schneider Make ACB installed at NITB at Raja Bhoj Airport, Bhopal for the year 2022-23.
Contract No: AAI/BPL/ENGG(E)/NIT-10/2022-23
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Manish Electricals(GSTN-23ABLPM9012E1ZW) |  | ARK POWER SOLUTIONS PRIVATE LIMITED(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Servicing and complete Overhauling (Electrical & Mechanical), extensive service along with interfacing of Air Circuit Breaker with existing system including activities like opening, fault finding, servicing, overhauling , Cleaning & reassembly of all moving mechanism of ACB like closing circuit, tripping circuit, spring charging mechanism etc., Check the general condition of the device (accessory cover, trip unit, case cradle, connections), Repairing of ACBs, Cleaning and lubricating all mechanical linkages, Removing all covers and arc extinguishing shields and re-fix, Clean all covers and arc shields, Open/close device manually and electrically, Check the filters cleanliness and the attachment of the arc-chute, Checking/ rectification of auxiliary wiring, Trip unit testing, checking & rectification using test tool and check operation of contacts. Check/ rectification of ground fault protection function (Micro logic 6.0) and calibration of protection relay with secondary injection, operation of position contacts, (CE, CT, CD, EF), safety shutters, Cradle Locking, spring charging motor, indication contacts, (OF / PF / MCH), Re greasing of disconnecting contact clusters of Cradle Measuring of insulation resistance complete etc as required.
1.01 | 4000 Amp ACB | 4.00 | Job |  | 15786.00 | 63144.00 | 10500.00 | 42000.00 | 42000.00 | ARK POWER SOLUTIONS PRIVATE LIMITED
1.02 | 2500 Amp ACB | 5.00 | Job |  | 13786.00 | 68930.00 | 9500.00 | 47500.00 | 47500.00 | ARK POWER SOLUTIONS PRIVATE LIMITED
1.03 | 1250 Amp ACB | 14.00 | Job |  | 11786.00 | 165004.00 | 9500.00 | 133000.00 | 133000.00 | ARK POWER SOLUTIONS PRIVATE LIMITED
1.04 | 800 Amp ACB | 7.00 | Job |  | 10000.00 | 70000.00 | 9500.00 | 66500.00 | 66500.00 | ARK POWER SOLUTIONS PRIVATE LIMITED
2.00 | Providing and fixing 250 Amp, Four pole MCCB, with inbuilt thermal Magnetic release with adjustable thermal setting with inbuilt O/L & S/C protection (Ics = Icu = 50 KA) with set of Rotary operating mechanism and terminal extension spreaders complete etc. as required. Note: MCCB will be fixed in existing panel, nothing will be paid extra for same in this account | 1.00 | Job |  | 22000.00 | 22000.00 | 53000.00 | 53000.00 | 22000.00 | Manish Electricals
3.00 | Providing and fixing 630 Amp, Four pole MCCB, with inbuilt thermal Magnetic release with adjustable thermal setting with inbuilt O/L & S/C protection (Ics = Icu = 50 KA) with set of Rotary operating mechanism and terminal extension spreaders complete etc. as required. Note: MCCB will be fixed in existing panel, nothing will be paid extra for same in this account | 1.00 | Job |  | 32000.00 | 32000.00 | 85000.00 | 85000.00 | 32000.00 | Manish Electricals
| Total in Figures |  |  |  |  | 421078.00 |  | 427000.00
Lowest Amount Quoted BY: Manish Electricals(421078.00)

## BOQ Summary
BOQ Summary Details Tender Title: Miscellaneous Maintenance Electrical works related to NITB. SH. Overhauling, Servicing and Testing of Schneider Make ACB installed at NITB at Raja Bhoj Airport, Bhopal for the year 2022-23. Tender ID: 2022_AAI_122389_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Manish Electricals | 421078.00 | L1
| 2 | ARK POWER SOLUTIONS PRIVATE LIMITED | 427000.00 | L2