## BoQ1
Government eProcurement System Created By: Nirad Patra Created Date/Time: 05-Sep-2022 05:45 PM Tender Title: Expansion of Apron for 4 Nos. of AB 320 Type of Aircraft with new Link Taxiway and allied works at VSS Airport, Jharsuguda. SH Electrical Work GLF works Tender ID: 2022_AAI_123628_1
Tender Inviting Authority: Asst. Gen. Manager (Engg-Elect), VSS Airport, Jharsuguda.
Name of Work: - Expansion of Apron for 4 Nos. of AB-320 Type of Aircraft with new Link Taxiway and allied works at VSS Airport, Jharsuguda. (SH :- Electrical Work(GLF works))
Contract No: - AAI/JSG/AGM(EE)/eNIT-4/2022 ( Tender Id : 2022_AAI_123628_1).
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Youngmen Traders(GSTN-19AEIPB6323B1ZZ) |  | Techno Electricals(GSTN-24AAGFT9086M1ZG) |  | Vardhman Airport Solutions Pvt Ltd(GSTN-07AAECN5914F1ZK) |  | Manish Electricals(GSTN-23ABLPM9012E1ZW)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply of 5 KV grade, multi stranded tinned copper conductor, XLPE insulated,Polyethylene sheathed, single core and with inner and outer semi conductor, underground cable or airfield lighting generally as specified in tender specification of the ollowing sizes as required. a) 6 sq mm | 3260.00 | Mtr | 3933950.00 | 95.00 | 309700.00 | 115.00 | 374900.00 | 105.00 | 342300.00 | 95.00 | 309700.00 | 309700.00 | Youngmen Traders, Manish Electricals
2.00 | Supply of elevated type LED Taxiway Edge light fitting (MIRL fitting) for use as Taxiway / Apron Edge /Turning Pad lights suitable for operation at 2.8 Amps to 6.6 Amps series circuit supply current complete with suitable LEDs, omni-directional lens, lens clamping mechanism, breakable coupling, rings /gaskets, base plate with 06 nos. M-10 stainless steel bolts and including an integrated encapsulated suitable electronic converter with standard secondary lead etc. complete fitting confirming to latest ICAO standards / requirement complete as required & direction of Engineering In-Charge.. | 64.00 | Set | 3933950.00 | 3500.00 | 224000.00 | 4200.00 | 268800.00 | 4200.00 | 268800.00 | 3800.00 | 243200.00 | 224000.00 | Youngmen Traders
3.00 | Supply of 15 Watt 6.6 Amps /6.6 Amps, 5 KV grade 50 Hz Isolating transformer series type encapsulated in neoprene type rubber with primary and secondary two pin leads as specified in technical specification as per site condition & direction of Engineering In-Charge. | 64.00 | Each | 3933950.00 | 2600.00 | 166400.00 | 3000.00 | 192000.00 | 2900.00 | 185600.00 | 2850.00 | 182400.00 | 166400.00 | Youngmen Traders
4.00 | Supply of following size copper conductor two pin secondary leads with one side male connector and other side female connector suitable for airfield lighting system and conforming to particular technical specifications etc. complete as required, as per site condition & direction of Engineering In-Charge. Size : - 2 X 2.5 Sq. MM & minimum 0.3 meter long . | 64.00 | Each | 3933950.00 | 400.00 | 25600.00 | 400.00 | 25600.00 | 180.00 | 11520.00 | 285.00 | 18240.00 | 11520.00 | Vardhman Airport Solutions Pvt Ltd
5.00 | Supplying of following size HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS with upto date amendments ,complete as per site condition & direction of Engineering In-Charge. A) 63 mm dia (OD),PN-8,PE-100. | 2608.00 | Mtr | 3933950.00 | 135.00 | 352080.00 | 132.00 | 344256.00 | 120.00 | 312960.00 | 135.00 | 352080.00 | 312960.00 | Vardhman Airport Solutions Pvt Ltd
6.00 | Laying of following size HDPE pipe at a depth of 0.8Mtr along with all accessories like socket, bend, couplers etc. Complete with fitting and cutting, jointing etc. direct in ground including excavation and making good surface as per site condition & direction of Engineering In-Charge. Size 63 mm dia (OD),PN-8,PE-100. | 2608.00 | Mtr | 3933950.00 | 85.00 | 221680.00 | 115.00 | 299920.00 | 95.00 | 247760.00 | 160.00 | 417280.00 | 221680.00 | Youngmen Traders
7.00 | Supply and drawing of following Size of FRLS PVC insulated multistand Copper Conductor cable in the existing Steel/PVC Conduits/HDPE Pipe for secondary supply of GLF fitting from isolating transformer and making jointing with both end two pin secondary leads as per tender specification, site condition & direction of Engineering In-Charge. (a) Size: 3 x 2.5 sq mm copper conductor cable (3 runs of 2.5 sqmm) | 640.00 | Mtr | 3933950.00 | 95.00 | 60800.00 | 125.00 | 80000.00 | 280.00 | 179200.00 | 140.00 | 89600.00 | 60800.00 | Youngmen Traders
8.00 | Installation, Testing, and Commissioning of elevated type high intensity runway edge /approach light/Taxi light fitting all other accessories complete as required as per site condition & direction of Engineering In-Charge. | 64.00 | Each | 3933950.00 | 200.00 | 12800.00 | 125.00 | 8000.00 | 150.00 | 9600.00 | 250.00 | 16000.00 | 8000.00 | Techno Electricals
9.00 | Supply of C.I isolating transformer housing box, water tight round type, metal container of outside size 330 mm height 450 mm made of 10 mm thick cast iron moulding all round, except the top surface, which is 15 mm thick, cast iron moulding suitable to receive a light fitting base plate on the top and underground housing associated with transformer power cable and having a clear hole at three side surface centre 75 mm above bottom surface suitable to receive of 63 mm dia (outer dia) HDPE/G. I. pipe and including check nuts as required and another hole at 175 mm from the bottom of the CI box to receive one no. 15 mm dia, "B" class, GI pipe and check nut as required. The box should have two SS earth bolts of M10 x 30 mm tapped inside near the hole away from the hole centre and having a drain hole at the bottom suitably tapped to receive 15 mm dia, "B" class GI pipe and having clear opening of 220 mm at the top surface and 6 nos. M10 tapped hole at the hole centre 260 mm to receive fitting base plate and bolts as required as per the drawings.(triple Hole type). | 64.00 | Each | 3933950.00 | 4800.00 | 307200.00 | 5750.00 | 368000.00 | 5200.00 | 332800.00 | 5250.00 | 336000.00 | 307200.00 | Youngmen Traders
10.00 | supply of CI collars of 50 mm height ,330mm dia,10mm thick CI moulding all around except top surface which is 15mm thick with 220mm opening on top & bottom, with 6nos. m-10 tapped hole on top and 6nos. through holes at bottom to pass m-10 bolts with three holes suitable to receive 50 mm dia (outer dia) HDPE/G. I. pipe | 64.00 | Each | 3933950.00 | 2700.00 | 172800.00 | 2400.00 | 153600.00 | 2400.00 | 153600.00 | 2600.00 | 166400.00 | 153600.00 | Techno Electricals, Vardhman Airport Solutions Pvt Ltd
11.00 | Installation of transformer housing box / collar as per site with a 100mm thick base concrete of 1:3:6 & all round concrete of 1:2:4 of 150mm thick along with top sloped as specified i/c providing & fixing 250 mm long 15mm dia "B" class G.l Pipe with check nuts at the bottom surface for drainage of water i/c excavation, alignment & refilling as reqd & as per drawing and specifications, as per site condition as per direction of Engineering In-Charge. | 64.00 | Each | 3933950.00 | 1600.00 | 102400.00 | 2500.00 | 160000.00 | 1800.00 | 115200.00 | 1200.00 | 76800.00 | 76800.00 | Manish Electricals
12.00 | Installation of transformer housing box collar as per site with a 100mm thick base concrete of 1:3:6 & all round concrete of 1:2:4 of 150mm thick along with top sloped as specified i/c excavation, alignment & refilling as reqd & as per drawing and specifications, as per site condition as per direction of Engineering In-Charge. | 64.00 | Each | 3933950.00 | 1200.00 | 76800.00 | 1200.00 | 76800.00 | 300.00 | 19200.00 | 1200.00 | 76800.00 | 19200.00 | Vardhman Airport Solutions Pvt Ltd
13.00 | Making field connections by crimping 6/16 sq. mm plug and receptacle with existing 6/16 sq. mm single core PVC copper conductor cable including filling the gap with water sealant material and applying PVC insulated tape etc. complete as required, as per site condition & direction of Engineering In-Charge. | 64.00 | Set | 3933950.00 | 100.00 | 6400.00 | 120.00 | 7680.00 | 150.00 | 9600.00 | 200.00 | 12800.00 | 6400.00 | Youngmen Traders
14.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 5 KV grade of following size in the existing RCC/ HUME/ METAL/HDPE pipe as required, as per site condition & direction of Engineering In-Charge. A) up to 25 Sq mm. | 2608.00 | Mtr | 3933950.00 | 20.00 | 52160.00 | 19.00 | 49552.00 | 30.00 | 78240.00 | 20.00 | 52160.00 | 49552.00 | Techno Electricals
15.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 5 KV grade of following size on wall surface / trench as required, as per site condition & direction of Engineering In-Charge. A) up to 25 Sq mm. | 25.00 | Mtr | 3933950.00 | 35.00 | 875.00 | 19.00 | 475.00 | 30.00 | 750.00 | 30.00 | 750.00 | 475.00 | Techno Electricals
16.00 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required, as per site condition & direction of Engineering In-Charge. | 8.00 | Each | 3933950.00 | 7000.00 | 56000.00 | 6850.00 | 54800.00 | 7500.00 | 60000.00 | 7000.00 | 56000.00 | 54800.00 | Techno Electricals
17.00 | Supply and laying of 6 SWG dia G.I. wire on surface or in recess for loop earthing as required, as per site condition & direction of Engineering In-Charge. | 2608.00 | Mtr | 3933950.00 | 16.00 | 41728.00 | 22.00 | 57376.00 | 20.00 | 52160.00 | 22.00 | 57376.00 | 41728.00 | Youngmen Traders
18.00 | Design Supply, Installation, Testing and commissioning of indoor type Microprocessor based Constant Current Regulator (CCR) suitable for remote as well as local control operations with 5 position brightness control (6.6A maximum current corresponding to 100% brightness) on input voltage 230/415 V, 50hz., AC supply, Control voltage: 48VDC ,provision for control supply with switchgears, CCR protections, connection/ inter-connection etc. Complete as required as per tender specification & direction of Engineering In-Charge. 20 KW, 6.6A output current. | 1.00 | Job | 3933950.00 | 350000.00 | 350000.00 | 400000.00 | 400000.00 | 440000.00 | 440000.00 | 465000.00 | 465000.00 | 350000.00 | Youngmen Traders
19.00 | Design Supply, Installation, Testing and commissioning of indoor type Microprocessor based Constant Current Regulator (CCR) suitable for remote as well as local control operations with 5 position brightness control (6.6A maximum current corresponding to 100% brightness) on input voltage 230/415 V, 50hz., AC supply, Control voltage: 48VDC ,provision for control supply with switchgears, CCR protections, connection/ inter-connection etc. Complete as required as per tender specification & direction of Engineering In-Charge. 7.5 KW, 6.6A output current. | 1.00 | Job | 3933950.00 | 230000.00 | 230000.00 | 260000.00 | 260000.00 | 320000.00 | 320000.00 | 321000.00 | 321000.00 | 230000.00 | Youngmen Traders
20.00 | Constructing brick masonry chamber of size 1200x1200x1200mm of size in cement mortar 1:4 (1 cement :4 coarse sand) inside cement plaster 15 mm thick with cement mortar 1:3 (1 cement: 3 Coarse sand) finished with floating coat of neat cement foundation concrete 1:3:6(1 cement: 3 coarse sand:6 graded stone aggregate 40 mm nominal size) all complete as per standard design with cover of 75 mm thick ness made by RCC in cement mortar 1:2:4(1 cement: 2 coarse sand:4 graded stone aggregate 40 mm nominal size) in two piece with 12 mm rod handle in order to easy handling and as per Tender specifications and as per directions of Engineer-In-charge. | 10.00 | Job | 3933950.00 | 10000.00 | 100000.00 | 17000.00 | 170000.00 | 14000.00 | 140000.00 | 12500.00 | 125000.00 | 100000.00 | Youngmen Traders
21.00 | SITC of internally illuminated LED based Mandatory / Information /Location/VOR check point Runway / Taxiway guidance age of various sizes made out of 4mm thick glare free poly carbonate sheet at front and body made out of 2.0mm thick powder coated aluminum profile having minimum width of 150mm and supported at back by 50mm dia, 3mm thickness, die cast aluminum pipe at a separation as required, and frangible coupling as required. Light source shall be high luminous, long life typical 50,000 Hrs. type, 0.5 Watts LED's assembled on aluminum PCB. The thickness of the aluminium PCB should be 2mm in order to ensure proper heat dissipation. These aluminium PCB’s should be placed not more than 160mm apart across the length of the board in order to ensure uniform distribution of light across the board. Each board having length from 800mm up to 3000mm should be illuminated by a single converter & by using single isolating transformer of suitable wattage in order to save the capital cost of multiple isolating transformers. Signage shall be suitable for operation on series circuit at variable current from 2.8Amp - 6.6Amp and will give constant brightness for all current variation. All the signage shall have letters and symbols made by computerized cutting of vinyl and pasting on the polycarbonate sheet from inside/outside of the sign face of required color as per ICAO. | 10.00 | Sq Mtr | 3933950.00 | 35000.00 | 350000.00 | 47000.00 | 470000.00 | 35000.00 | 350000.00 | 38750.00 | 387500.00 | 350000.00 | Youngmen Traders, Vardhman Airport Solutions Pvt Ltd
22.00 | Excavation of the cable trenches in hard rock not exceeding 1.5 metres in width, and lift upto 1.5 metres, including getting out the excavated soil and disposal of excavated soil as directed by EIC as per site condition. | 20.00 | CUM | 3933950.00 | 300.00 | 6000.00 | 850.00 | 17000.00 | 700.00 | 14000.00 | 1000.00 | 20000.00 | 6000.00 | Youngmen Traders
| Total in Figures |  |  |  |  | 3225423.00 |  | 3838759.00 |  | 3643290.00 |  | 3782086.00
Lowest Amount Quoted BY: Youngmen Traders(3225423.00)

## BOQ Summary
BOQ Summary Details Tender Title: Expansion of Apron for 4 Nos. of AB 320 Type of Aircraft with new Link Taxiway and allied works at VSS Airport, Jharsuguda. SH Electrical Work GLF works Tender ID: 2022_AAI_123628_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Youngmen Traders | 3225423.00 | L1
| 2 | Vardhman Airport Solutions Pvt Ltd | 3643290.00 | L2
| 3 | Manish Electricals | 3782086.00 | L3
| 4 | Techno Electricals | 3838759.00 | L4