## BoQ1
Government eProcurement System Created By: K SANTHOSH KUMAR Created Date/Time: 16-Sep-2022 02:34 PM Tender Title: AMC of Fire Hydrant with Sprinkler System for 02 Years at NATS Complex Tender ID: 2022_AAI_125742_1
Tender Inviting Authority: Asstt. Gen. Mgr. (E-E), NATS Complex, IGI Airport, New Delhi
Name of Work : AMC of Fire Hydrant with Sprinkler System for 02 years at NATS Complex, IGI Airport, New Delhi (2022-24).
Contract No/Tender ID : 2022_AAI_125742_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | BA-PAN ENGINEERING co.(GSTN-07AYDPS2409Q1ZX) |  | NATIONAL SAFETY ENGINEERS(GSTN-07ADCPT3599E3Z6) |  | ARC SERVICESS(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | FIRE HYDRANT SYSTEM
2.00 | 1. Monthly site visit /check (01 No. Mandatory check per month) by experienced staff for the inspection of entire Fire fighting and sprinkler System including cleaning, oiling and greasing of Pumps, valves, etc. attending all complaints/ breakdown (any number of times) during that Month and also carry out all the checks/preventive maintenance works as per enclosed schedule (Annexure-A) and submitting report of the entire Fire Hydrant with sprinkler System. SPARES/ ACCESSORIES/ MAJOR REPAIRS(if any) (As and when required as per site requirement) | 24.00 | Nos | 100.00 | 23000.00 | 552000.00 | 11900.00 | 285600.00 | 8500.00 | 204000.00 | 204000.00 | ARC SERVICESS
3.00 | 2. Replacement (i/c supply) of following fire fighting component/spares including all accessories such as screwed/welded flanges etc. i/c dismantling of the existing component along with accessories( if any )complete including painting, welding, jointing and neoprene gasket, nuts, bolts, washer etc. complete as required and as per relevant IS.
3.01 | (a) 200 mm dia flanged CI Foot Valve (As per IS 4038). Make : Kirloskar or any make as per Approved Make List. | 4.00 | Nos | 10.00 | 14000.00 | 56000.00 | 11000.00 | 44000.00 | 18500.00 | 74000.00 | 44000.00 | NATIONAL SAFETY ENGINEERS
3.02 | (b) 50 mm dia flanged CI Foot Valve (As per IS 4038). Make : Kirloskar or any make as per Approved Make List. | 2.00 | Nos | 10.00 | 3200.00 | 6400.00 | 1800.00 | 3600.00 | 5600.00 | 11200.00 | 3600.00 | NATIONAL SAFETY ENGINEERS
3.03 | (c) 150 mm dia CI Non Return Valve (CIDF Swing Type, PN 1.0, IS 5312, Part I & II, Bronze to Rubber rings/ SS 410 Hinge Pin construction). Make : Kirloskar or any make as per Approved Make List. | 3.00 | Nos | 10.00 | 16000.00 | 48000.00 | 11000.00 | 33000.00 | 12500.00 | 37500.00 | 33000.00 | NATIONAL SAFETY ENGINEERS
3.04 | (d) 50 mm dia CI Non Return Valve (CIDF Swing Type, PN 1.6, IS 5312, Part I & II, Bronze to Rubber rings/ SS 410 Hinge Pin construction). Make : Kirloskar or any make as per Approved Make List. | 2.00 | Nos | 10.00 | 3200.00 | 6400.00 | 2300.00 | 4600.00 | 4500.00 | 9000.00 | 4600.00 | NATIONAL SAFETY ENGINEERS
3.05 | (e) 100 mm dia CI Non Return Valve (CIDF Swing Type, PN 1.6, IS 5312, Part I & II, Bronze to Rubber rings/ SS 410 Hinge Pin construction). Make : Kirloskar or any make as per Approved Make List. | 2.00 | Nos | 10.00 | 6500.00 | 13000.00 | 5200.00 | 10400.00 | 10500.00 | 21000.00 | 10400.00 | NATIONAL SAFETY ENGINEERS
3.06 | (f) 100 mm dia C I Spindle Sluice Valve (CIDF Non rising Type, PN 1.6, IS 14846, Part I & II, Bronze rings/SS 410 shaft). (ISI Marked). Make : Kirloskar or any make as per Approved Make List. | 2.00 | Nos | 10.00 | 9500.00 | 19000.00 | 10000.00 | 20000.00 | 15600.00 | 31200.00 | 19000.00 | BA-PAN ENGINEERING co.
3.07 | (g) 50 mm dia C I Spindle Sluice Valve (CIDF Non rising Type, PN 1.6, IS 14846, Part I & II, Bronze rings/SS 410 shaft). (ISI Marked). Make : Kirloskar or any make as per Approved Make List. | 2.00 | Nos | 10.00 | 4100.00 | 8200.00 | 3000.00 | 6000.00 | 5600.00 | 11200.00 | 6000.00 | NATIONAL SAFETY ENGINEERS
3.08 | (h) 150 mm dia C I Spindle Sluice Valve (CIDF Non rising Type, PN 1.6, IS 14846, Part I&II, Bronze rings /SS 410 shaft). (ISI Marked). Make : Kirloskar or any make as per Approved Make List. | 2.00 | Nos | 10.00 | 13500.00 | 27000.00 | 12000.00 | 24000.00 | 18500.00 | 37000.00 | 24000.00 | NATIONAL SAFETY ENGINEERS
3.09 | (i) 150 mm dia C I Spindle Sluice Valve (CIDF rising Type, PN 1.6, IS 14846, Part (ISI Marked). Make : Kirloskar or any make as per Approved Make List. | 2.00 | Nos | 10.00 | 14000.00 | 28000.00 | 12000.00 | 24000.00 | 15500.00 | 31000.00 | 24000.00 | NATIONAL SAFETY ENGINEERS
4.00 | 3. Replacement (i/c supply) of the following fire fighting component/spares including all forged fittings and accessories such as screwed/welded flanges, tees, reducers etc. (if any) i/c dismantling of the existing component along with accessories( if any), complete including painting, welding, jointing and Providing of neoprene gaskets, nuts, bolts ,washer etc., if required and as per direction of Engineer In Charge, and making good the same complete as required.
4.01 | (a) Gun metal ball Valve(25 mm dia). Make -ZOLOTO or any make as per Approved Make List. | 10.00 | Nos | 10.00 | 800.00 | 8000.00 | 1000.00 | 10000.00 | 1250.00 | 12500.00 | 8000.00 | BA-PAN ENGINEERING co.
4.02 | (b) Gun metal Single hydrant Valve ( ISI marked, IS 5290). Make -New age/Guards or any make as per Approved Make List. | 6.00 | Nos | 10.00 | 7500.00 | 45000.00 | 4000.00 | 24000.00 | 4850.00 | 29100.00 | 24000.00 | NATIONAL SAFETY ENGINEERS
4.03 | (c) Gun Metal lugs for Hydrant valves. Make -New age/Guards or any make as per Approved Make List. | 10.00 | Nos | 10.00 | 800.00 | 8000.00 | 1000.00 | 10000.00 | 1250.00 | 12500.00 | 8000.00 | BA-PAN ENGINEERING co.
5.00 | 4. Replacement ( i/c supply) of First Aid rubber Hose reel tube, 30 Mtr. Length, ISI mark including dismantling the existing tube Make - New age/Guards or any make as per Approved Make List. | 2.00 | Nos. | 10.00 | 3200.00 | 6400.00 | 3000.00 | 6000.00 | 3250.00 | 6500.00 | 6000.00 | NATIONAL SAFETY ENGINEERS
6.00 | 5. Rewinding of motor of 15 KW, 2900 RPM of jockey pump including overhauling/ servicing, varnishing, baking, applying moisture proof varnish, assembling, testing, decoupling and coupling, loading / unloading and transportation to and from the site complete. ( Old defective winding shall be retained by Agency). | 2.00 | Job | 10.00 | 5000.00 | 10000.00 | 2500.00 | 5000.00 | 12500.00 | 25000.00 | 5000.00 | NATIONAL SAFETY ENGINEERS
7.00 | 6. Providing and fixing of Gun metal female delivery hoss coupling, 63 mm ISI as per IS : 903 i/c dismantling of existing coupling (if any). Make - New age/Guards or any make as per Approved Make List. | 5.00 | Nos | 10.00 | 1400.00 | 7000.00 | 2500.00 | 12500.00 | 1250.00 | 6250.00 | 6250.00 | ARC SERVICESS
8.00 | 7. Providing and fixing of First Aid Hose Reel PVC Nozzle 20 mm i/c dismantling of existing nozzle(if any) .Make -as per Approved Make List. | 10.00 | Nos. | 10.00 | 500.00 | 5000.00 | 350.00 | 3500.00 | 350.00 | 3500.00 | 3500.00 | NATIONAL SAFETY ENGINEERS, ARC SERVICESS
9.00 | 8. Repair of jockey pump motor of flow rate of 3 litre / second, 105 meter head including supply and replacement of bearing of suitable size shaft repair, impeller repair, stud and threading, coupling, oiling, greasing & glandory, including labour charges, loading / unloading, transportaion to & from the site etc. complete. | 2.00 | Job | 10.00 | 13000.00 | 26000.00 | 9000.00 | 18000.00 | 12500.00 | 25000.00 | 18000.00 | NATIONAL SAFETY ENGINEERS
10.00 | 9. Replacement (i/c supply) of two nos. bearing of suitable size (Make-SKF), gland plate,complete housing nut,bolt with gland set of main fire pump (make; kirloskar brothers, type: DSM 125/40) i/c Dismantling, loading and unloading, transportation of pump to and from the site, Servicing/overhauling of pump, allignment with motor on common base plate, installation, testing & commisioning complete as required. | 2.00 | Job | 10.00 | 4000.00 | 8000.00 | 26000.00 | 52000.00 | 12500.00 | 25000.00 | 8000.00 | BA-PAN ENGINEERING co.
11.00 | 10. Replacement (i/c supply) of following works to be carried out at work shop if required after opening of main fire pump mentioned in item no. 9
11.01 | (a) Pump sleeves-2 Nos. | 1.00 | Job | 10.00 | 2300.00 | 2300.00 | 4000.00 | 4000.00 | 780.00 | 780.00 | 780.00 | ARC SERVICESS
11.02 | (b) Mechanical seal -1 No. | 1.00 | Job | 10.00 | 13000.00 | 13000.00 | 6000.00 | 6000.00 | 500.00 | 500.00 | 500.00 | ARC SERVICESS
11.03 | (c) Repairing of pump shaft | 1.00 | Job | 10.00 | 4000.00 | 4000.00 | 2000.00 | 2000.00 | 950.00 | 950.00 | 950.00 | ARC SERVICESS
12.00 | 11. Replacement (i/c supply) of gland plate, complete housing nut bolt with gland dori, gland nut bolt set of main diesel pump (make : Kirloskars brothers, type: DSM 5B i/c Dismantling, loading and unloading, transportation of pump to and from the site, Servicing of pump, allignment with Engine in common base plate, installation testing & commisioning complete as required. | 1.00 | Job | 10.00 | 23000.00 | 23000.00 | 18000.00 | 18000.00 | 12500.00 | 12500.00 | 12500.00 | ARC SERVICESS
13.00 | 12. Replacement (i/c supply) of following works which is to be carried out at work shop if required after opening of pump mentioned in item no. 11
13.01 | (a) 2 nos. bearing of suitable size (Make-SKF)of main diesel pump. | 1.00 | Job | 10.00 | 4000.00 | 4000.00 | 4000.00 | 4000.00 | 780.00 | 780.00 | 780.00 | ARC SERVICESS
14.00 | 13. Painting of existing fire hydrant pipelines inside & outside at NATS Complex with (one or more coats on old work) synthetic enamel paint of approved brand and manufacture of required colour to give an even shade. | 100.00 | Sq.Mtr | 10.00 | 50.00 | 5000.00 | 80.00 | 8000.00 | 25.00 | 2500.00 | 2500.00 | ARC SERVICESS
15.00 | 14. Providing and fixing glazing in internal & external fire hydrant boxes with EPDM rubber/ neoprene gasket etc. complete as per the architectural drawings and the directions of Engineer-In-Charge. With float glass panes of 5.50 mm thickness. | 20.00 | Sq.Mtr | 10.00 | 400.00 | 8000.00 | 500.00 | 10000.00 | 25.00 | 500.00 | 500.00 | ARC SERVICESS
16.00 | 15. Painting of existing external fire hydrants hose pipe cabinet (external side only ) and adjacent hydrant post of 80 -100 mm dia. Upto 01 meter and valve etc. including supporting structure with 02 coat of red oxide primer and 01 coat of enamel paint including scrapping, cleaning etc. complete as required as per site condition. | 10.00 | Job | 10.00 | 2000.00 | 20000.00 | 350.00 | 3500.00 | 450.00 | 4500.00 | 3500.00 | NATIONAL SAFETY ENGINEERS
17.00 | 16. Painting of existing internal fire hydrants hose pipe cabinet (external side only) and adjacent hydrant pipe of 50 -100 mm dia. Upto 01 meter and valve etc. including supporting structure with 02 coat of red oxide primer and 01 coat of enamel paint including scrapping, cleaning etc. complete as required as per site condition. | 30.00 | Job | 10.00 | 2000.00 | 60000.00 | 250.00 | 7500.00 | 450.00 | 13500.00 | 7500.00 | NATIONAL SAFETY ENGINEERS
18.00 | 17. Replacement (i/c supply) of new gland plate, housing nut bolt with gland dori, gland nut bolt set, bearings of jockey pump (make: kirloskars brothers, type: CPHM 32/26 i/c dismantling, loading and unloading, transportation of pump to and from the site, Servicing of pump, allignment with Engine on common base plate, installation, testing & commisioning complete as required. | 2.00 | Job | 10.00 | 2000.00 | 4000.00 | 6500.00 | 13000.00 | 450.00 | 900.00 | 900.00 | ARC SERVICESS
19.00 | 18. Providing and fixing of MS Pipe including all fittings and accessories such as screwed/welded flanges, tees, reducers etc. complete including painting(with one coat of primer & two coats of post office red enamel paint), welding, jointing and neoprene gaskets, nuts, bolts etc. as required i/c dismantling of the existing pipes with accessories (if any) of the following pipes fixed in ceiling, walls, coloumns for all heights with hangers, supports and fasteners all as per direction of Engineer In Charge, including chasing of walls/columns/ceilings etc. and making good the same complete as and when required.
19.01 | (a) 200 mm dia (Heavy class 6 mm thick) ( IS : 3589) | 10.00 | Mtr | 10.00 | 2500.00 | 25000.00 | 3500.00 | 35000.00 | 2450.00 | 24500.00 | 24500.00 | ARC SERVICESS
19.02 | (b) 150 mm dia (Medium Class, IS 1239) | 20.00 | Mtr | 10.00 | 2000.00 | 40000.00 | 2600.00 | 52000.00 | 2000.00 | 40000.00 | 40000.00 | BA-PAN ENGINEERING co., ARC SERVICESS
19.03 | (c) 100 mm dia (Medium Class, IS 1239) | 20.00 | Mtr | 10.00 | 1500.00 | 30000.00 | 1800.00 | 36000.00 | 1550.00 | 31000.00 | 30000.00 | BA-PAN ENGINEERING co.
19.04 | (d) 80 mm dia (Medium Class, IS 1239) | 10.00 | Mtr | 10.00 | 1300.00 | 13000.00 | 1500.00 | 15000.00 | 950.00 | 9500.00 | 9500.00 | ARC SERVICESS
19.05 | (e) 50 mm dia (Medium Class, IS 1239) | 10.00 | Mtr | 10.00 | 800.00 | 8000.00 | 800.00 | 8000.00 | 650.00 | 6500.00 | 6500.00 | ARC SERVICESS
| Total in Figures |  |  |  |  | 1146700.00 |  | 818200.00 |  | 761360.00
Lowest Amount Quoted BY: ARC SERVICESS(761360.00)

## BOQ Summary
BOQ Summary Details Tender Title: AMC of Fire Hydrant with Sprinkler System for 02 Years at NATS Complex Tender ID: 2022_AAI_125742_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | ARC SERVICESS | 761360.00 | L1
| 2 | NATIONAL SAFETY ENGINEERS | 818200.00 | L2
| 3 | BA-PAN ENGINEERING co. | 1146700.00 | L3