## BoQ1
Government eProcurement System Created By: S.THIRVMAL MURUGAN Created Date/Time: 21-Sep-2022 05:07 PM Tender Title: Renovation and Associated Works for Water Supply System at Chennai Airport. Sub Head. SITC of LT Panels and Other Associated Works Tender ID: 2022_AAI_125752_1
Tender Inviting Authority: Asst.Gen.Manager (Engg-Elect)-VI, 1st Floor, Electrical Maintenance Division, Operational Offices, Airport Authority of India, Chennai Airport, Chennai 600016.
Name of Work: Renovation and Associated Works for Water Supply System at Chennai Airport. SH: SITC of LT panels and other associated works.
Contract No: AAI/CHE/AMED-VI/2022-23/01
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Shantha ELectricals and Engineers Pvt Ltd(GSTN-29AARCS2866G1ZP) |  | vk sam engineering(GSTN-33AMZPS4037L1ZA) |  | CHENNAI ENGINEERING SERVICES(GSTN-33AADFC4373K1ZH) |  | TRIGGO TECH ENGINEERING(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SH-I: Supply of LT Panels & Cables
1.01 | Old WTP Feeder Pillar
1.02 | Design, Fabrication and supply of cubical type outdoor LT Panel - tested design as per IEC 61439-1 & 2, IP 54, suitable for 415 V, 3 Phase, 4 wire 50 Hz AC supply, made out of 2 mm thick CRCA sheet steel for frame work, canopy and covers, 1.6mm thick with internal doors, portitions and non load bearing portions, 3 mm thick for gland plates, dust tight, vermin proof, totally enclosed, Form 4b compartmentalised design, floor mounting, free standing, extensible on both sides i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having 600Amps capacity TPN Aluminium bus bars of high conductivity, DMC/SMC bus bar supports with short circuit withstand capacity of 50 KA for 1Sec., bottom base channel of MS section not less than 100 mm x50 mm x 5 mm thick, fabrication shall be done in transportable sections,entire panel shall have a common copper earth bar of size 50mm x 5 mm at the rear with 2 nos earth stud, solid connections from main bus bars to switch gears with required size of Aluminium bus bars and control wiring with 2.5Sq.mm. FRLSH PVC insulated copper conductor cable, cable alleys, complete with all accessories, interconnection, earthing, complete etc. as required and comprising of following switch gears:
1.03 | Incoming
1.04 | Two Nos. 400A, 50 KA, Four Pole MCCB as incomer (Ics=Icu) with inbuilt over current and short circuit protection of Microprocessor based release and provided with three nos. Cast resin suitable rating CTs with Digital Multifunction Meter having RS485 port (EM6400 of Schneider make or equivalent), ON/OFF/TRIP LED Indication Lamps and Phase Indication Lamps alongwith control MCBs as required.
1.05 | Outgoings:
1.06 | Four Nos. 250A, 36 KA, Four Pole MCCB (Ics=Icu) with inbuilt over current and short circuit protection of Microprocessor based release and provided with three nos. Cast resin suitable rating CTs with Digital Multifunction Meter (EM6459 of Schneider make or equivalent), ON/OFF/TRIP LED Indication Lamps alongwith control MCBs as required
1.07 | Two Nos. 100 A, 36KA, Four Pole MCCB (Ics=Icu) with inbuilt over current and short circuit protection of Adustable Thermal and Magnetic Release and provided with three nos. Cast resin suitable rating CTs with Digital Multifunction Meter (EM6459 of Schneider make or equivalent), ON/OFF/TRIP LED Indication Lamps alongwith control MCBs as required.
1.08 | Buscoupler: One No. 400A, 50 KA, Four Pole MCCB as Buscoupler (Ics=Icu) with inbuilt over current and short circuit protection of Microprocessor based release and provided with ON/OFF/TRIP LED Indication Lamps and Phase Indication Lamps alongwith control MCBs as required.
1.09 | Busbar:
1.10 | One Set of TPN Aluminium Bus Bars of minimum of 600 A Capacity with heat shrinkable coloured sleeves and i/c DMC/SMC bus bar cross section, size supports & their spacing etc. for meeting fault level of 50 KA for 1 Sec and 50x5mm Copper earth strip etc. as required.
1.11 | Interlocking: Mechanical interlocking between 2 Incomers & 1 Buscoupler and it shall be ensured that only one supply is available at a time on each section of bus and to eliminate any possibility of accidently approaching two supply at one bus section.
1.12 | All accessories such as auxiliary contactors, auxiliary switches, push buttons MCBs, rotary handles, phase seperators etc., as required.
1.13 | All as above (Sl.No. 1.01 to 1.12) | 1.00 | Job |  | 705000.00 | 705000.00 | 502970.00 | 502970.00 | 646879.00 | 646879.00 | 530474.00 | 530474.00 | 502970.00 | vk sam engineering
2.00 | LT Panel for Old WTP HPS Pump Room
2.01 | Design, Fabrication and supply of cubical type Indoor LT Panel - tested design as per IEC 60439-1 & 2, IP 42, suitable for 415 V, 3 Phase, 4 wire 50 Hz AC supply, made out of 2 mm thick CRCA sheet steel for load bearing portions, 1.6mm thick with doors, covers, portitions, barriers and non load bearing portions, 3 mm thick for gland plates, dust tight, vermin proof, totally enclosed, Form 3b compartmentalised design, floor mounting, free standing, extensible on both sides i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having 400Amps capacity TPN Aluminium bus bars of high conductivity, DMC/SMC bus bar supports with short circuit withstand capacity of 50 KA for 1Sec., bottom base channel of MS section not less than 100 mm x50 mm x 5 mm thick, fabrication shall be done in transportable sections,entire panel shall have a common copper earth bar of size 50mm x 5 mm at the rear with 2 nos earth stud, solid connections from main bus bars to switch gears with required size of Aluminium bus bars and control wiring with 2.5Sq.mm. FRLSH PVC insulated copper conductor cable, cable alleys, complete with all accessories, interconnection, earthing, complete etc. as required and comprising of following switch gears:
2.02 | INCOMERS
2.03 | Two Nos. 250A, 36 KA, Four Pole MCCB as incomer (Ics=Icu) with inbuilt over current and short circuit protection of Microprocessor based release and provided with three nos. Cast resin suitable rating CTs with Digital Multifunction Meter having RS485 port (EM6400 of Schneider make or equivalent), ON/OFF/TRIP LED Indication Lamps and Phase Indication Lamps alongwith control MCBs as required.
2.04 | Outgoings:
2.05 | Three Nos. 160 A, 36KA, Four Pole MCCB (Ics=Icu) with inbuilt over current and short circuit protection of Adustable Thermal and Magnetic Release and provided with three nos. Cast resin suitable rating CTs with Digital Multifunction Meter (EM6459 of Schneider make or equivalent), ON/OFF/TRIP LED Indication Lamps alongwith control MCBs as required.
2.06 | Three Nos. 125 A, 36KA, Four Pole MCCB (Ics=Icu) with inbuilt over current and short circuit protection of Adustable Thermal and Magnetic Release and provided with three nos. Cast resin suitable rating CTs with Digital Multifunction Meter (EM6459 of Schneider make or equivalent), ON/OFF/TRIP LED Indication Lamps alongwith control MCBs as required.
2.07 | Three Nos. 63 A, 25KA, Four Pole MCCB (Ics=Icu) with inbuilt over current and short circuit protection of Adustable Thermal and Magnetic Release and provided with three nos. Cast resin suitable rating CTs with Digital Multifunction Meter (EM6459 of Schneider make or equivalent), ON/OFF/TRIP LED Indication Lamps alongwith control MCBs as required.
2.08 | 2 Nos. (1 Working + 1 Standby) 16A TP MPCB of Rotary type with thermal magnetic based O/L & S/C protection Release with Rotary Handle extendable Outside suitable for 10 HP with star-delta starter (Suitable rated 03 Nos TP contactors for Star-Delta Operation, timer and O/L relay) for water pump motor. Each compartment shall contain auto/manual selector switch and Start/Stop Push Button, Single Phase Preventor with ON/Off/Trip indicating lamps alongwith 1 Set of digital multifunction meter (EM6459 of Schneider make or equivalent) with LCD display including 03 Nos suitable rating CTs with control MCB’s complete as required
2.09 | 2 Nos. 10A TP MPCB of Rotary type with thermal magnetic based O/L & S/C protection Release with Rotary Handle extendable Outside suitable for 5 HP with DOL starter (Suitable rated TP contactor and O/L relay) for water pump motor. Each compartment shall contain auto/manual selector switch and Start/Stop Push Button, Single Phase Preventor with ON/Off/Trip indicating lamps alongwith 1 Set of digital multifunction meter (EM6459 of Schneider make or equivalent)with LCD display including 03 Nos suitable rating CTs with control MCB’s complete as required
2.10 | 4Nos. 32A, 4Pole MCB 'C' Curve with Suitable rating connectors
2.11 | Buscoupler: One No. 250A, 36 KA, Four Pole MCCB as Buscoupler (Ics=Icu) with inbuilt over current and short circuit protection of Microprocessor based release and provided with ON/OFF/TRIP LED Indication Lamps and Phase Indication Lamps alongwith control MCBs as required.
2.12 | Busbar:
2.13 | One Set of TPN Aluminium Bus Bars of minimum of 400 A Capacity with heat shrinkable coloured sleeves and i/c DMC/SMC bus bar cross section, size supports & their spacing etc. and 50x5mm Copper earth strip etc. as required.
2.14 | Interlocking: Mechanical interlocking between 2 Incomers & 1 Buscoupler and it shall be ensured that only one supply is available at a time on each section of bus and to eliminate any possibility of accidently approaching two supply at one bus section
2.15 | All accessories such as auxiliary contactors, auxiliary switches, push buttons MCBs, rotary handles, phase seperators etc., as required.
2.16 | All as above (Sl.No. 2.01 to 2.15) | 1.00 | Job |  | 830000.00 | 830000.00 | 607615.00 | 607615.00 | 659169.00 | 659169.00 | 837300.00 | 837300.00 | 607615.00 | vk sam engineering
3.00 | LT Panel for Old WTP Raw Water Pump Room
3.01 | Design, Fabrication and supply of cubical type Indoor LT Panel - tested design as per IEC 60439-1 & 2, IP 42, suitable for 415 V, 3 Phase, 4 wire 50 Hz AC supply, made out of 2 mm thick CRCA sheet steel for load bearing portions, 1.6mm thick with doors, covers, portitions, barriers and non load bearing portions, 3 mm thick for gland plates, dust tight, vermin proof, totally enclosed, Form 3b compartmentalised design, floor mounting, free standing, extensible on both sides i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having 400Amps capacity TPN Aluminium bus bars of high conductivity, DMC/ SMC bus bar supports with short circuit withstand capacity of 50 KA for 1Sec., bottom base channel of MS section not less than 100 mm x50 mm x 5 mm thick, fabrication shall be done in transportable sections,entire panel shall have a common copper earth bar of size 50mm x 5 mm at the rear with 2 nos earth stud, solid connections from main bus bars to switch gears with required size of Aluminium bus bars and control wiring with 2.5Sq.mm. FRLSH PVC insulated copper conductor cable, cable alleys, complete with all accessories, interconnection, earthing, complete etc. as required and comprising of following switch gears:
3.02 | INCOMERS
3.03 | Two Nos. 250A, 36 KA, Four Pole MCCB as incomer (Ics=Icu) with inbuilt over current and short circuit protection of Microprocessor based release and provided with three nos. Cast resin suitable rating CTs with Digital Multifunction Meter having RS485 port (EM6400 of Schneider make or equivalent), ON/OFF/TRIP LED Indication Lamps and Phase Indication Lamps alongwith control MCBs as required.
3.04 | Outgoings:
3.05 | Two Nos. 160 A, 36KA, Four Pole MCCB (Ics=Icu) with inbuilt over current and short circuit protection of Adustable Thermal and Magnetic Release and provided with three nos. Cast resin suitable rating CTs with Digital Multifunction Meter (EM6459 of Schneider make or equivalent), ON/OFF/TRIP LED Indication Lamps alongwith control MCBs as required.
3.06 | Three Nos. 63 A, 25KA, Four Pole MCCB (Ics=Icu) with inbuilt over current and short circuit protection of Adustable Thermal and Magnetic Release and provided with three nos. Cast resin suitable rating CTs with Digital Multifunction Meter (EM6459 of Schneider make or equivalent), ON/OFF/TRIP LED Indication Lamps alongwith control MCBs as required.
3.07 | 2 Nos. 32A TP MPCB of Rotary type with thermal magnetic based O/L & S/C protection Release with Rotary Handle extendable Outside suitable for 20 HP with star-delta starter (Suitable rated 03 Nos TPN contactors for Star-Delta Operation, timer and O/L relay) for water pump motor. Each compartment shall contain auto/manual selector switch and Start/Stop Push Button, Single Phase Preventor with ON/Off/Trip indicating lamps alongwith 1 Set of digital multifunction meter(EM6459 of Schneider make or equivalent) with LCD display including 03 Nos suitable rating CTs with control MCB’s complete as required
3.08 | 2 Nos. 25A TP MPCB of Rotary type with thermal magnetic based O/L & S/C protection Release with Rotary Handle extendable Outside suitable for 15 HP with star-delta starter (Suitable rated 03 Nos TPN contactors for Star-Delta Operation, timer and O/L relay) for water pump motor. Each compartment shall contain auto/manual selector switch and Start/Stop Push Button, Single Phase Preventor with ON/Off/Trip indicating lamps alongwith 1 Set of digital multifunction meter(EM6459 of Schneider make or equivalent) with LCD display including 03 Nos suitable rating CTs with control MCB’s complete as required
3.09 | 2 Nos. 16A TP MPCB of Rotary type with thermal magnetic based O/L & S/C protection Release with Rotary Handle extendable Outside suitable for 10 HP with star-delta starter (Suitable rated 03 Nos TP contactors for Star-Delta Operation, timer and O/L relay) for water pump motor. Each compartment shall contain auto/manual selector switch and Start/Stop Push Button, Single Phase Preventor with ON/Off/Trip indicating lamps alongwith 1 Set of digital multifunction meter (EM6459 of Schneider make or equivalent) with LCD display including 03 Nos suitable rating CTs with control MCB’s complete as required
3.10 | 2Nos. 32A, 4Pole MCB 'C' Curve with Suitable rating connectors
3.11 | Buscoupler: One No. 250A, 36 KA, Four Pole MCCB as Buscoupler (Ics=Icu) with inbuilt over current and short circuit protection of Microprocessor based release and provided with ON/OFF/TRIP LED Indication Lamps and Phase Indication Lamps alongwith control MCBs as required.
3.12 | Busbar:
3.13 | One Set of TPN Aluminium Bus Bars of minimum of 400 A Capacity with heat shrinkable coloured sleeves and i/c DMC/SMC bus bar cross section, size supports & their spacing etc. and 50x5mm Copper earth strip etc. as required.
3.14 | Interlocking: Mechanical interlocking between 2 Incomers & 1 Buscoupler and it shall be ensured that only one supply is available at a time on each section of bus and to eliminate any possibility of accidently approaching two supply at one bus section
3.15 | All accessories such as auxiliary contactors, auxiliary switches, push buttons MCBs, rotary handles, phase seperators etc., as required.
3.16 | All as above (Sl.No. 3.01 to 3.15) | 1.00 | Job |  | 790000.00 | 790000.00 | 616255.00 | 616255.00 | 697777.00 | 697777.00 | 823910.00 | 823910.00 | 616255.00 | vk sam engineering
4.00 | LT Panel for Old WTP Pump Room
4.01 | Design, Fabrication and supply of cubical type Indoor LT Panel - tested design as per IEC 60439-1 & 2, IP 42, suitable for 415 V, 3 Phase, 4 wire 50 Hz AC supply, made out of 2 mm thick CRCA sheet steel for load bearing portions, 1.6mm thick with doors, covers, portitions, barriers and non load bearing portions, 3 mm thick for gland plates, dust tight, vermin proof, totally enclosed, Form 3b compartmentalised design, floor mounting, free standing, extensible on both sides i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having 250Amps capacity TPN Aluminium bus bars of high conductivity, DMC/SMC bus bar supports with short circuit withstand capacity of 50 KA for 1Sec., bottom base channel of MS section not less than 100 mm x50 mm x 5 mm thick, fabrication shall be done in transportable sections,entire panel shall have a common copper earth bar of size 50mm x 5 mm at the rear with 2 nos earth stud, solid connections from main bus bars to switch gears with required size of Aluminium bus bars and control wiring with 2.5Sq.mm. FRLSH PVC insulated copper conductor cable, cable alleys, complete with all accessories, interconnection, earthing, complete etc. as required and comprising of following switch gears:
4.02 | INCOMER
4.03 | One No. 160A, 36 KA, Four Pole MCCB as incomer (Ics=Icu) with inbuilt over current and short circuit protection of Adustable Thermal and Magnetic Release and provided with three nos. Cast resin suitable rating CTs with Digital Multifunction Meter having RS485 port (EM6400 of Schneider make or equivalent), ON/OFF/TRIP LED Indication Lamps and Phase Indication Lamps alongwith control MCBs as required.
4.04 | Outgoings:
4.05 | One No. 63 A, 25KA, Four Pole MCCB (Ics=Icu) with inbuilt over current and short circuit protection of Adustable Thermal and Magnetic Release and provided with three nos. Cast resin suitable rating CTs with Digital Multifunction Meter (EM6459 of Schneider make or equivalent), ON/OFF/TRIP LED Indication Lamps alongwith control MCBs as required.
4.06 | 4 Nos. 32A TP MPCB of Rotary type with thermal magnetic based O/L & S/C protection Release with Rotary Handle extendable Outside suitable for 20 HP with star-delta starter (Suitable rated 03 Nos TPN contactors for Star-Delta Operation, timer and O/L relay) for water pump motor. Each compartment shall contain auto/manual selector switch and Start/Stop Push Button, Single Phase Preventor with ON/Off/Trip indicating lamps alongwith 1 Set of digital multifunction meter(EM6459 of Schneider make or equivalent) with LCD display including 03 Nos suitable rating CTs with control MCB’s complete as required
4.07 | 2 Nos. 25A TP MPCB of Rotary type with thermal magnetic based O/L & S/C protection Release with Rotary Handle extendable Outside suitable for 15 HP with star-delta starter (Suitable rated 03 Nos TPN contactors for Star-Delta Operation, timer and O/L relay) for water pump motor. Each compartment shall contain auto/manual selector switch and Start/Stop Push Button, Single Phase Preventor with ON/Off/Trip indicating lamps alongwith 1 Set of digital multifunction meter(EM6459 of Schneider make or equivalent) with LCD display including 03 Nos suitable rating CTs with control MCB’s complete as required
4.08 | 3 Nos. 13A TP MPCB of Rotary type with thermal magnetic based O/L & S/C protection Release with Rotary Handle extendable Outside suitable for 7.5 HP with star-delta starter (Suitable rated 03 Nos TPN contactors for Star-Delta Operation, timer and O/L relay) for water pump motor. Each compartment shall contain auto/manual selector switch and Start/Stop Push Button, Single Phase Preventor with ON/Off/Trip indicating lamps alongwith 1 Set of digital multifunction meter(EM6459 of Schneider make or equivalent) with LCD display including 03 Nos suitable rating CTs with control MCB’s complete as required
4.09 | 4 Nos. 10A TP MPCB of Rotary type with thermal magnetic based O/L & S/C protection Release with Rotary Handle extendable Outside suitable for 3 HP with DOL starter (Suitable rated TP contactor and O/L relay) for water pump motor. Each compartment shall contain auto/manual selector switch and Start/Stop Push Button, Single Phase Preventor with ON/Off/Trip indicating lamps alongwith 1 Set of digital multifunction meter (EM6459 of Schneider make or equivalent)with LCD display including 03 Nos suitable rating CTs with control MCB’s complete as required
4.10 | 6 Nos. 2.5A TP MPCB of Rotary type with thermal magnetic based O/L & S/C protection Release with Rotary Handle extendable Outside suitable for 1 HP with DOL starter (Suitable rated TP contactor and O/L relay) for water pump motor. Each compartment shall contain auto/manual selector switch and Start/Stop Push Button, Single Phase Preventor with ON/Off/Trip indicating lamps alongwith 1 Set of digital multifunction meter (EM6459 of Schneider make or equivalent)with LCD display including 03 Nos suitable rating CTs with control MCB’s complete as required
4.11 | 2Nos. 32A, 4Pole MCB 'C' Curve with Suitable rating connectors
4.12 | Busbar:
4.13 | One Set of TPN Aluminium Bus Bars of minimum of 250 A Capacity with heat shrinkable coloured sleeves and i/c DMC/SMC bus bar cross section, size supports & their spacing etc. and 50x5mm Copper earth strip etc. as required.
4.14 | All accessories such as auxiliary contactors, auxiliary switches, push buttons MCBs, rotary handles, phase seperators etc., as required.
4.15 | All as above (Sl.No. 4.01 to 4.14) | 1.00 | Job |  | 950000.00 | 950000.00 | 695815.00 | 695815.00 | 791589.00 | 791589.00 | 1000382.00 | 1000382.00 | 695815.00 | vk sam engineering
5.00 | LT Panel for Cowl Bazaar Pump Room
5.01 | Design, Fabrication and supply of cubical type Indoor LT Panel - tested design as per IEC 60439-1 & 2, IP 42, suitable for 415 V, 3 Phase, 4 wire 50 Hz AC supply, made out of 2 mm thick CRCA sheet steel for load bearing portions, 1.6mm thick with doors, covers, portitions, barriers and non load bearing portions, 3 mm thick for gland plates, dust tight, vermin proof, totally enclosed, Form 3b compartmentalised design, floor mounting, free standing, extensible on both sides i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having 250Amps capacity TPN Aluminium bus bars of high conductivity, DMC/SMC bus bar supports with short circuit withstand capacity of 50 KA for 1Sec., bottom base channel of MS section not less than 100 mm x50 mm x 5 mm thick, fabrication shall be done in transportable sections, entire panel shall have a common copper earth bar of size 25mm x 5 mm at the rear with 2 nos earth stud, solid connections from main bus bars to switch gears with required size of Aluminium bus bars and control wiring with 2.5Sq.mm. FRLSH PVC insulated copper conductor cable, cable alleys, complete with all accessories, interconnection, earthing, complete etc. as required and comprising of following switch gears:
5.02 | INCOMER
5.03 | One No. 160A, 36 KA, Four Pole MCCB as incomer (Ics=Icu) with inbuilt over current and short circuit protection of Adustable Thermal and Magnetic Release and provided with three nos. Cast resin suitable rating CTs with Digital Multifunction Meter having RS485 port (EM6400 of Schneider make or equivalent), ON/OFF/TRIP LED Indication Lamps and Phase Indication Lamps alongwith control MCBs as required.
5.04 | Outgoings:
5.05 | Two Nos. 63 A, 25KA, Four Pole MCCB (Ics=Icu) with inbuilt over current and short circuit protection of Adustable Thermal and Magnetic Release and provided with three nos. Cast resin suitable rating CTs with Digital Multifunction Meter (EM6459 of Schneider make or equivalent), ON/OFF/TRIP LED Indication Lamps alongwith control MCBs as required.
5.06 | 3 Nos. 10A TP MPCB of Rotary type with thermal magnetic based O/L & S/C protection Release with Rotary Handle extendable Outside suitable for 5 HP with DOL starter (Suitable rated TP contactor and O/L relay) for water pump motor. Each compartment shall contain auto/manual selector switch and Start/Stop Push Button, Single Phase Preventor with ON/Off/Trip indicating lamps alongwith 1 Set of digital multifunction meter (EM6459 of Schneider make or equivalent)with LCD display including 03 Nos suitable rating CTs with control MCB’s complete as required
5.07 | 4 Nos. 6.3A TP MPCB of Rotary type with thermal magnetic based O/L & S/C protection Release with Rotary Handle extendable Outside suitable for 3 HP with DOL starter (Suitable rated TP contactor and O/L relay) for water pump motor. Each compartment shall contain auto/manual selector switch and Start/Stop Push Button, Single Phase Preventor with ON/Off/Trip indicating lamps alongwith 1 Set of digital multifunction meter (EM6459 of Schneider make or equivalent)with LCD display including 03 Nos suitable rating CTs with control MCB’s complete as required
5.08 | 1 Nos. 13A TP MPCB of Rotary type with thermal magnetic based O/L & S/C protection Release with Rotary Handle extendable Outside suitable for 7.5 HP with star-delta starter (Suitable rated 03 Nos TPN contactors for Star-Delta Operation, timer and O/L relay) for water pump motor. Each compartment shall contain auto/manual selector switch and Start/Stop Push Button, Single Phase Preventor with ON/Off/Trip indicating lamps alongwith 1 Set of digital multifunction meter(EM6459 of Schneider make or equivalent) with LCD display including 03 Nos suitable rating CTs with control MCB’s complete as required
5.09 | 2Nos. 32A, 4Pole MCB 'C' Curve with Suitable rating connectors
5.10 | Busbar:
5.11 | One Set of TPN Aluminium Bus Bars of minimum of 250 A Capacity with heat shrinkable coloured sleeves and i/c DMC/SMC bus bar cross section, size supports & their spacing etc. and 25x5mm Copper earth strip etc. as required.
5.12 | Interlocking: Mechanical interlocking between Incomer & 1 No. of 63A outgoing MCCB shall be provided.
5.13 | All accessories such as auxiliary contactors, auxiliary switches, push buttons MCBs, rotary handles, phase seperators etc., as required.
5.14 | All as above (Sl.No. 5.01 to 5.13) | 1.00 | Job |  | 458000.00 | 458000.00 | 306535.00 | 306535.00 | 384779.00 | 384779.00 | 498720.00 | 498720.00 | 306535.00 | vk sam engineering
6.00 | i) LT Panel for 25 Pump Room - 1 Job ii) LT Panel for Cargo Well Pump Room - 1 Job iii) LT Panel for Old Fire Pump House - 1 Job
6.01 | Design, Fabrication and supply of cubical type Indoor LT Panel - tested design as per IEC 60439-1 & 2, IP 42, suitable for 415 V, 3 Phase, 4 wire 50 Hz AC supply, made out of 2 mm thick CRCA sheet steel for load bearing portions, 1.6mm thick with doors, covers, portitions, barriers and non load bearing portions, 3 mm thick for gland plates, dust tight, vermin proof, totally enclosed, Form 3b compartmentalised design, floor mounting, free standing, extensible on both sides i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having 250Amps capacity TPN Aluminium bus bars of high conductivity, DMC/SMC bus bar supports with short circuit withstand capacity of 50 KA for 1Sec., bottom base channel of MS section not less than 100 mm x50 mm x 5 mm thick, fabrication shall be done in transportable sections, entire panel shall have a common copper earth bar of size 25mm x 5 mm at the rear with 2 nos earth stud, solid connections from main bus bars to switch gears with required size of Aluminium bus bars and control wiring with 2.5Sq.mm. FRLSH PVC insulated copper conductor cable, cable alleys, complete with all accessories, interconnection, earthing, complete etc. as required and comprising of following switch gears:
6.02 | INCOMER
6.03 | One No. 100A, 36 KA, Four Pole MCCB as incomer (Ics=Icu) with inbuilt over current and short circuit protection of Adustable Thermal and Magnetic Release and provided with three nos. Cast resin suitable rating CTs with Digital Multifunction Meter having RS485 port (EM6400 of Schneider make or equivalent), ON/OFF/TRIP LED Indication Lamps and Phase Indication Lamps alongwith control MCBs as required.
6.04 | Outgoings:
6.05 | One No. 63 A, 25KA, Four Pole MCCB (Ics=Icu) with inbuilt over current and short circuit protection of Adustable Thermal and Magnetic Release and provided with three nos. Cast resin suitable rating CTs with Digital Multifunction Meter (EM6459 of Schneider make or equivalent), ON/OFF/TRIP LED Indication Lamps alongwith control MCBs as required.
6.06 | 3 Nos. 10A TP MPCB of Rotary type with thermal magnetic based O/L & S/C protection Release with Rotary Handle extendable Outside suitable for 5 HP with DOL starter (Suitable rated TP contactor and O/L relay) for water pump motor. Each compartment shall contain auto/manual selector switch and Start/Stop Push Button, Single Phase Preventor with ON/Off/Trip indicating lamps alongwith 1 Set of digital multifunction meter (EM6459 of Schneider make or equivalent)with LCD display including 03 Nos suitable rating CTs with control MCB’s complete as required
6.07 | 4Nos. 32A, 4Pole MCB 'C' Curve with Suitable rating connectors
6.08 | Busbar:
6.09 | One Set of TPN Aluminium Bus Bars of minimum of 150 A Capacity with heat shrinkable coloured sleeves and i/c DMC/SMC bus bar cross section, size supports & their spacing etc. and 25x5mm Copper earth strip etc. as required.
6.10 | All accessories such as auxiliary contactors, auxiliary switches, push buttons MCBs, rotary handles, phase seperators etc., as required.
6.11 | All as above (Sl.No. 6.01 to 6.10) | 3.00 | Job |  | 265000.00 | 795000.00 | 166135.00 | 498405.00 | 196429.00 | 589287.00 | 248480.00 | 745440.00 | 498405.00 | vk sam engineering
7.00 | Runway 25 side Outdoor LT Panel
7.01 | Design, Fabrication and supply of cubical type outdoor LT Panel - tested design as per IEC 60439-1 & 2, IP 54, suitable for 415 V, 3 Phase, 4 wire 50 Hz AC supply, made out of 2 mm thick CRCA sheet steel for frame work, canopy and covers, 1.6mm thick with internal doors, portitions and non load bearing portions, 3 mm thick for gland plates, dust tight, vermin proof, totally enclosed, Form 3b compartmentalised design , floor mounting, free standing, extensible on both sides i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having 150Amps capacity TPN Aluminium bus bars of high conductivity, DMC/SMC bus bar supports with short circuit withstand capacity of 50 KA for 1Sec., bottom base channel of MS section not less than 100 mm x50 mm x 5 mm thick, fabrication shall be done in transportable sections, entire panel shall have a common copper earth bar of size 25mm x 5 mm at the rear with 2 nos earth stud, solid connections from main bus bars to switch gears with required size of Aluminium bus bars and control wiring with 2.5Sq.mm. FRLSH PVC insulated copper conductor cable, cable alleys, complete with all accessories, interconnection, earthing, complete etc. as required and comprising of following switch gears:
7.02 | INCOMER
7.03 | One No. 100A, 36 KA, Four Pole MCCB as incomer (Ics=Icu) with inbuilt over current and short circuit protection of Adustable Thermal and Magnetic Release and provided with three nos. Cast resin suitable rating CTs with Digital Multifunction Meter having RS485 port (EM6400 of Schneider make or equivalent), ON/OFF/TRIP LED Indication Lamps and Phase Indication Lamps alongwith control MCBs as required.
7.04 | Outgoings:
7.05 | 1 No. 10A TP MPCB of Rotary type with thermal magnetic based O/L & S/C protection Release with Rotary Handle extendable Outside suitable for 5 HP with DOL starter (Suitable rated TP contactor and O/L relay) for water pump motor. Each compartment shall contain auto/manual selector switch and Start/ Stop Push Button, Single Phase Preventor with ON/ Off/ Trip indicating lamps alongwith 1 Set of digital multifunction meter (EM6459 of Schneider make or equivalent)with LCD display including 03 Nos suitable rating CTs with control MCB’s complete as required
7.06 | 2 Nos. 6.3A TP MPCB of Rotary type with thermal magnetic based O/L & S/C protection Release with Rotary Handle extendable Outside suitable for 3 HP with DOL starter (Suitable rated TP contactor and O/L relay) for water pump motor. Each compartment shall contain auto/manual selector switch and Start/ Stop Push Button, Single Phase Preventor with ON/ Off/ Trip indicating lamps alongwith 1 Set of digital multifunction meter (EM6459 of Schneider make or equivalent) with LCD display including 03 Nos suitable rating CTs with control MCB’s complete as required
7.07 | Busbar:
7.08 | One Set of TPN Aluminium Bus Bars of minimum of 150 A Capacity with heat shrinkable coloured sleeves and i/c DMC/SMC bus bar cross section, size supports & their spacing etc. and 50x5mm Copper earth strip etc. as required.
7.09 | All accessories such as auxiliary contactors, auxiliary switches, push buttons MCBs, rotary handles, phase seperators etc., as required.
7.10 | Note: Panel Height shall be restricted to maximum 0.7Mtr.
7.11 | All as above (Sl.No.7.01 to 7.10) | 1.00 | Job |  | 230000.00 | 230000.00 | 141895.00 | 141895.00 | 152419.00 | 152419.00 | 249980.00 | 249980.00 | 141895.00 | vk sam engineering
8.00 | LT Panel for Old Pump Room / Cargo Pump Room
8.01 | Design, Fabrication and supply of cubical type Indoor LT Panel - tested design as per IEC 60439-1 & 2, IP 42, suitable for 415 V, 3 Phase, 4 wire 50 Hz AC supply, made out of 2 mm thick CRCA sheet steel for load bearing portions, 1.6mm thick with doors, covers, portitions, barriers and non load bearing portions, 3 mm thick for gland plates, dust tight, vermin proof, totally enclosed, Form 3b compartmentalised design, floor mounting, free standing, extensible on both sides i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having 250Amps capacity TPN Aluminium bus bars of high conductivity, DMC/SMC bus bar supports with short circuit withstand capacity of 50 KA for 1Sec., bottom base channel of MS section not less than 100 mm x50 mm x 5 mm thick, fabrication shall be done in transportable sections, entire panel shall have a common copper earth bar of size 25mm x 5 mm at the rear with 2 nos earth stud, solid connections from main bus bars to switch gears with required size of Aluminium bus bars and control wiring with 2.5Sq.mm. FRLSH PVC insulated copper conductor cable, cable alleys, complete with all accessories, interconnection, earthing, complete etc. as required and comprising of following switch gears:
8.02 | INCOMER
8.03 | One No. 160A, 36 KA, Four Pole MCCB as incomer (Ics=Icu) with inbuilt over current and short circuit protection of Adustable Thermal and Magnetic Release and provided with three nos. Cast resin suitable rating CTs with Digital Multifunction Meter having RS485 port (EM6400 of Schneider make or equivalent), ON/OFF/TRIP LED Indication Lamps and Phase Indication Lamps alongwith control MCBs as required.
8.04 | Outgoings:
8.05 | One No. 125 A, 36KA, Four Pole MCCB (Ics=Icu) with inbuilt over current and short circuit protection of Adustable Thermal and Magnetic Release and provided with three nos. Cast resin suitable rating CTs with Digital Multifunction Meter (EM6459 of Schneider make or equivalent), ON/OFF/TRIP LED Indication Lamps alongwith control MCBs as required.
8.06 | Two Nos. 63 A, 25KA, Four Pole MCCB (Ics=Icu) with inbuilt over current and short circuit protection of Adustable Thermal and Magnetic Release and provided with three nos. Cast resin suitable rating CTs with Digital Multifunction Meter (EM6459 of Schneider make or equivalent), ON/OFF/TRIP LED Indication Lamps alongwith control MCBs as required.
8.07 | 2 Nos. 32A TP MPCB of Rotary type with thermal magnetic based O/L & S/C protection Release with Rotary Handle extendable Outside suitable for 20 HP with star-delta starter (Suitable rated 03 Nos TPN contactors for Star-Delta Operation, timer and O/L relay) for water pump motor. Each compartment shall contain auto/manual selector switch and Start/Stop Push Button, Single Phase Preventor with ON/Off/Trip indicating lamps alongwith 1 Set of digital multifunction meter(EM6459 of Schneider make or equivalent) with LCD display including 03 Nos suitable rating CTs with control MCB’s complete as required
8.08 | 3 Nos. (2 Working + 1 Standby) 16A TP MPCB of Rotary type with thermal magnetic based O/L & S/C protection Release with Rotary Handle extendable Outside suitable for 10 HP with star-delta starter (Suitable rated 03 Nos TP contactors for Star-Delta Operation, timer and O/L relay) for water pump motor. Each compartment shall contain auto/manual selector switch and Start/Stop Push Button, Single Phase Preventor with ON/Off/Trip indicating lamps alongwith 1 Set of digital multifunction meter (EM6459 of Schneider make or equivalent) with LCD display including 03 Nos suitable rating CTs with control MCB’s complete as required
8.09 | 4Nos. 32A, 4Pole MCB 'C' Curve with Suitable rating connectors
8.10 | Busbar:
8.11 | One Set of TPN Aluminium Bus Bars of minimum of 250 A Capacity with heat shrinkable coloured sleeves and i/c DMC/SMC bus bar cross section, size supports & their spacing etc. and 25x5mm Copper earth strip etc. as required.
8.12 | All accessories such as auxiliary contactors, auxiliary switches, push buttons MCBs, rotary handles, phase seperators etc., as required.
8.13 | All as above (Sl.No. 8.01 to 8.12) | 1.00 | Job |  | 470000.00 | 470000.00 | 347335.00 | 347335.00 | 402939.00 | 402939.00 | 543468.00 | 543468.00 | 347335.00 | vk sam engineering
9.00 | LT Panel for New WTP
9.01 | Design, Fabrication and supply of cubical type Indoor LT Panel - tested design as per IEC 60439-1 & 2, IP 42, suitable for 415 V, 3 Phase, 4 wire 50 Hz AC supply, made out of 2 mm thick CRCA sheet steel for load bearing portions, 1.6mm thick with doors, covers, portitions, barriers and non load bearing portions, 3 mm thick for gland plates, dust tight, vermin proof, totally enclosed, Form 3b compartmentalised design, floor mounting, free standing, extensible on both sides i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having 400Amps capacity TPN Aluminium bus bars of high conductivity, DMC/SMC bus bar supports with short circuit withstand capacity of 50 KA for 1Sec., bottom base channel of MS section not less than 100 mm x50 mm x 5 mm thick, fabrication shall be done in transportable sections,entire panel shall have a common copper earth bar of size 25mm x 5 mm at the rear with 2 nos earth stud, solid connections from main bus bars to switch gears with required size of Aluminium bus bars and control wiring with 2.5Sq.mm. FRLSH PVC insulated copper conductor cable, cable alleys, complete with all accessories, interconnection, earthing, complete etc. as required and comprising of following switch gears:
9.02 | INCOMER
9.03 | One No. 250A, 36 KA, Four Pole MCCB as incomer (Ics=Icu) with inbuilt over current and short circuit protection of Adustable Thermal and Magnetic Release and provided with three nos. Cast resin suitable rating CTs with Digital Multifunction Meter having RS485 port (EM6400 of Schneider make or equivalent), ON/OFF/TRIP LED Indication Lamps and Phase Indication Lamps alongwith control MCBs as required.
9.04 | Outgoings:
9.05 | One No. 160 A, 36KA, Four Pole MCCB (Ics=Icu) with inbuilt over current and short circuit protection of Adustable Thermal and Magnetic Release and provided with three nos. Cast resin suitable rating CTs with Digital Multifunction Meter (EM6459 of Schneider make or equivalent), ON/OFF/TRIP LED Indication Lamps alongwith control MCBs as required.
9.06 | Three Nos. 63 A, 25KA, Four Pole MCCB (Ics=Icu) with inbuilt over current and short circuit protection of Adustable Thermal and Magnetic Release and provided with three nos. Cast resin suitable rating CTs with Digital Multifunction Meter (EM6459 of Schneider make or equivalent), ON/OFF/TRIP LED Indication Lamps alongwith control MCBs as required.
9.07 | 2 Nos. 25A TP MPCB of Rotary type with thermal magnetic based O/L & S/C protection Release with Rotary Handle extendable Outside suitable for 15 HP with star-delta starter (Suitable rated 03 Nos TPN contactors for Star-Delta Operation, timer and O/L relay) for water pump motor. Each compartment shall contain auto/manual selector switch and Start/Stop Push Button, Single Phase Preventor with ON/Off/Trip indicating lamps alongwith 1 Set of digital multifunction meter(EM6459 of Schneider make or equivalent) with LCD display including 03 Nos suitable rating CTs with control MCB’s complete as required
9.08 | 1 No. 13A TP MPCB of Rotary type with thermal magnetic based O/L & S/C protection Release with Rotary Handle extendable Outside suitable for 7.5 HP with star-delta starter (Suitable rated 03 Nos TPN contactors for Star-Delta Operation, timer and O/L relay) for water pump motor. Each compartment shall contain auto/manual selector switch and Start/Stop Push Button, Single Phase Preventor with ON/Off/Trip indicating lamps alongwith 1 Set of digital multifunction meter(EM6459 of Schneider make or equivalent) with LCD display including 03 Nos suitable rating CTs with control MCB’s complete as required
9.09 | 2Nos. 32A, 4Pole MCB 'C' Curve with Suitable rating connectors
9.10 | Busbar:
9.11 | One Set of TPN Aluminium Bus Bars of minimum of 400 A Capacity with heat shrinkable coloured sleeves and i/c DMC/SMC bus bar cross section, size supports & their spacing etc. and 25x5mm Copper earth strip etc. as required.
9.12 | All accessories such as auxiliary contactors, auxiliary switches, push buttons MCBs, rotary handles, phase seperators etc., as required.
9.13 | All as above (Sl.No.9.01 to 9.12) | 1.00 | Job |  | 426000.00 | 426000.00 | 308815.00 | 308815.00 | 320469.00 | 320469.00 | 414692.00 | 414692.00 | 308815.00 | vk sam engineering
10.00 | Supply of XLPE insulated and PVC sheathed aluminium conductor armoured power cable of 1.1 KV grade conforming to IS 7098 (Part-I) 1988 as amended upto date and of following size as required.
10.01 | 4C X 35 Sq.mm | 600.00 | Mtr |  | 280.00 | 168000.00 | 210.00 | 126000.00 | 259.00 | 155400.00 | 307.00 | 184200.00 | 126000.00 | vk sam engineering
10.02 | 3.5C X 120 Sq.mm | 200.00 | Mtr |  | 545.00 | 109000.00 | 525.00 | 105000.00 | 659.00 | 131800.00 | 714.00 | 142800.00 | 105000.00 | vk sam engineering
11.00 | Supply of nominal 2.0 mm thick (Width 1 Mtr) PVC synthetic, electric insulated mats conforming to IS 15652-2006 having Dielectric strength of 30 KV, no adverse effect of mineral oil, high insulation resistance (Minimum 1,00,000 M Ω on wet condition with 5 KV meggar) etc., as required. | 60.00 | Sq.Mtr |  | 950.00 | 57000.00 | 650.00 | 39000.00 | 499.00 | 29940.00 | 1970.00 | 118200.00 | 29940.00 | CHENNAI ENGINEERING SERVICES
12.00 | Supply of XLPE insulated and PVC sheathed copper conductor armoured power cable of 1.1 KV grade conforming to IS 7098 (Part-I) 1988 as amended upto date and of following size as required.
12.01 | 4C X 6 Sq.mm | 100.00 | Mtr |  | 310.00 | 31000.00 | 290.00 | 29000.00 | 359.00 | 35900.00 | 315.00 | 31500.00 | 29000.00 | vk sam engineering
13.00 | Installation, Testing, commissioning of LT Panels, Laying of Cables and Associated Works.
14.00 | Installation, Testing and Commissioning of 415V, 600 Amps Bus bar rating, Old WTP outdoor Feeder Pillar mentioned at SH-I SOQ Item No.1 including provision of supporting "C" channel size 100 x 50 x 6 mm thick, supporting MS Angles and Civil foundation etc. complete as required. Civil foundation alongwith MS angle/channel supports shall be got approved by Engineer-In-Charge prior execution of work. | 1.00 | Job |  | 22000.00 | 22000.00 | 7500.00 | 7500.00 | 29999.00 | 29999.00 | 7500.00 | 7500.00 | 7500.00 | vk sam engineering, TRIGGO TECH ENGINEERING
15.00 | Installation, Testing and Commissioning of 415V, 400 Amps Bus bar rating LT Panel for Old WTP Pump Room mentioned at SH-I SOQ Item No.2 including provision of supporting "C" channel size 100 x 50 x 6 mm thick, supporting MS Angles and Civil foundation etc. complete as required. Civil foundation alongwith MS angle/channel supports shall be got approved by Engineer-In-Charge prior execution of work. | 1.00 | Job |  | 25000.00 | 25000.00 | 6000.00 | 6000.00 | 39999.00 | 39999.00 | 7500.00 | 7500.00 | 6000.00 | vk sam engineering
16.00 | Installation, Testing and Commissioning of 415V, 400 Amps Bus bar rating LT Panel for Old WTP Raw Water Pump Room mentioned at SH-I SOQ Item No.3 including provision of supporting "C" channel size 100 x 50 x 6 mm thick, supporting MS Angles and Civil foundation etc. complete as required. Civil foundation alongwith MS angle/channel supports shall be got approved by Engineer-In-Charge prior execution of work. | 1.00 | Job |  | 23000.00 | 23000.00 | 4500.00 | 4500.00 | 39999.00 | 39999.00 | 7500.00 | 7500.00 | 4500.00 | vk sam engineering
17.00 | Installation, Testing and Commissioning of 415V, 250 Amps Bus bar rating LT Panel for Old WTP Pump Room mentioned at SH-I SOQ Item No.4 including provision of supporting "C" channel size 100 x 50 x 6 mm thick, supporting MS Angles and Civil foundation etc. complete as required. Civil foundation alongwith MS angle/channel supports shall be got approved by Engineer-In-Charge prior execution of work. | 1.00 | Job |  | 25000.00 | 25000.00 | 4500.00 | 4500.00 | 49999.00 | 49999.00 | 7500.00 | 7500.00 | 4500.00 | vk sam engineering
18.00 | Installation, Testing and Commissioning of 415V, 250 Amps Bus bar rating LT Panel for Cowl Bazaar Pump Room mentioned at SH-I SOQ Item No.5 including provision of supporting "C" channel size 100 x 50 x 6 mm thick, supporting MS Angles and Civil foundation etc. complete as required. Civil foundation alongwith MS angle/channel supports shall be got approved by Engineer-In-Charge prior execution of work. | 1.00 | Job |  | 20000.00 | 20000.00 | 4500.00 | 4500.00 | 19999.00 | 19999.00 | 7500.00 | 7500.00 | 4500.00 | vk sam engineering
19.00 | Installation, Testing and Commissioning of 415V, 150 Amps Bus bar rating LT Panel for 25 Pump Room mentioned at SH-I SOQ Item No.6 including provision of supporting "C" channel size 100 x 50 x 6 mm thick, supporting MS Angles and Civil foundation etc. complete as required. Civil foundation alongwith MS angle/channel supports shall be got approved by Engineer-In-Charge prior execution of work. | 3.00 | Job |  | 18000.00 | 54000.00 | 3500.00 | 10500.00 | 9999.00 | 29997.00 | 7500.00 | 22500.00 | 10500.00 | vk sam engineering
20.00 | Installation, Testing and Commissioning of 415V, 150 Amps Bus bar rating Runway 25 side Outdoor LT Panel mentioned at SH-I SOQ Item No.7 including provision of supporting "C" channel size 100 x 50 x 6 mm thick, supporting MS Angles and Civil foundation etc. complete as required. Civil foundation alongwith MS angle/channel supports shall be got approved by Engineer-In-Charge prior execution of work. | 1.00 | Job |  | 15000.00 | 15000.00 | 5500.00 | 5500.00 | 9999.00 | 9999.00 | 7500.00 | 7500.00 | 5500.00 | vk sam engineering
21.00 | Installation, Testing and Commissioning of 415V, 250 Amps Bus bar rating LT Panel for Old Pump Room / Cargo Pump Room mentioned at SH-I SOQ Item No.8 including provision of supporting "C" channel size 100 x 50 x 6 mm thick, supporting MS Angles and Civil foundation etc. complete as required. Civil foundation alongwith MS angle/channel supports shall be got approved by Engineer-In-Charge prior execution of work. | 1.00 | Job |  | 15000.00 | 15000.00 | 4500.00 | 4500.00 | 19999.00 | 19999.00 | 7500.00 | 7500.00 | 4500.00 | vk sam engineering
22.00 | Installation, Testing and Commissioning of 415V, 400 Amps Bus bar rating LT Panel for New WTP mentioned at SH-I SOQ Item No.9 including provision of supporting "C" channel size 100 x 50 x 6 mm thick, supporting MS Angles and Civil foundation etc. complete as required. Civil foundation alongwith MS angle/channel supports shall be got approved by Engineer-In-Charge prior execution of work. | 1.00 | Job |  | 10000.00 | 10000.00 | 4500.00 | 4500.00 | 19999.00 | 19999.00 | 7500.00 | 7500.00 | 4500.00 | vk sam engineering
23.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required.
23.01 | Upto 35 sq. mm (clamped with 1mm thick saddle) | 60.00 | Mtr |  | 70.00 | 4200.00 | 55.00 | 3300.00 | 39.00 | 2340.00 | 85.00 | 5100.00 | 2340.00 | CHENNAI ENGINEERING SERVICES
23.02 | Above 95 sq. mm and upto 185 sq. mm (clamped with 25x3mm MS flat clamp) | 120.00 | Mtr |  | 130.00 | 15600.00 | 90.00 | 10800.00 | 119.00 | 14280.00 | 120.00 | 14400.00 | 10800.00 | vk sam engineering
24.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 11 KV grade of following size in the existing RCC/ HUME/ METAL/HDPE pipe as required.
24.01 | Upto 120 sq. mm | 220.00 | Mtr |  | 120.00 | 26400.00 | 60.00 | 13200.00 | 69.00 | 15180.00 | 125.00 | 27500.00 | 13200.00 | vk sam engineering
25.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required.
25.01 | Upto 35 sq. mm (clamped with 1mm thick saddle) | 60.00 | Mtr |  | 75.00 | 4500.00 | 45.00 | 2700.00 | 29.00 | 1740.00 | 85.00 | 5100.00 | 1740.00 | CHENNAI ENGINEERING SERVICES
25.02 | Above 185 sq. mm and upto 400 sq. mm (clamped with 40x3mm MS flat clamp) | 80.00 | Mtr |  | 160.00 | 12800.00 | 110.00 | 8800.00 | 149.00 | 11920.00 | 120.00 | 9600.00 | 8800.00 | vk sam engineering
26.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required.
26.01 | Above 95 sq. mm and upto 185 sq. mm | 10.00 | Mtr |  | 170.00 | 1700.00 | 45.00 | 450.00 | 59.00 | 590.00 | 85.00 | 850.00 | 450.00 | vk sam engineering
26.02 | Above 185 sq. mm and upto 400 sq. mm | 10.00 | Mtr |  | 250.00 | 2500.00 | 80.00 | 800.00 | 109.00 | 1090.00 | 180.00 | 1800.00 | 800.00 | vk sam engineering
27.00 | Supply, Installation, Testing and Commissioning of Four Pole On Load Change Over Switch of 400 Amps rating of Outdoor type with MS Enclosure with Canopy in the Existing Wall, including providing Handle, providing LED Display for Inputs and Output, suitable Bus Links for both at Input & Output Side, grouting, earthing, providing MS angle supports/civil foundation etc., complete as required. | 1.00 | Job |  | 69600.00 | 69600.00 | 37000.00 | 37000.00 | 49999.00 | 49999.00 | 39316.00 | 39316.00 | 37000.00 | vk sam engineering
28.00 | Supply, Installation, Testing and Commissioning of Four Pole On Load Change Over Switch of 250 Amps rating of Indoor type with MS Enclosure in the Existing Wall, including providing Handle, providing LED Display for Inputs and Output, suitable Bus Links for both at Input & Output Side, grouting, earthing, providing MS angle supports/civil foundation etc., complete as required. | 1.00 | Job |  | 54000.00 | 54000.00 | 20000.00 | 20000.00 | 39999.00 | 39999.00 | 27685.00 | 27685.00 | 20000.00 | vk sam engineering
29.00 | Supply, Installation, Testing and Commissioning of Four Pole On Load Change Over Switch of 160 Amps rating of Indoor type with MS Enclosure in the Existing Wall, including providing Handle, providing LED Display for Inputs and Output, suitable Bus Links for both at Input & Output Side, grouting, earthing, providing MS angle supports/civil foundation etc., complete as required. | 1.00 | Job |  | 43000.00 | 43000.00 | 12000.00 | 12000.00 | 24999.00 | 24999.00 | 20019.00 | 20019.00 | 12000.00 | vk sam engineering
30.00 | Supply, Installation, Testing and Commissioning of Four Pole On Load Change Over Switch of 63 Amps rating of Indoor type with MS Enclosure in the Existing Wall, including providing Handle, providing LED Display for Inputs and Output, suitable Bus Links for both at Input & Output Side, grouting, earthing, providing MS angle supports/civil foundation etc., complete as required. | 1.00 | Job |  | 33600.00 | 33600.00 | 8500.00 | 8500.00 | 14999.00 | 14999.00 | 12859.00 | 12859.00 | 8500.00 | vk sam engineering
31.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
31.01 | 3½ X 300 sq. mm (70mm) | 4.00 | Set |  | 2900.00 | 11600.00 | 1100.00 | 4400.00 | 1499.00 | 5996.00 | 4184.00 | 16736.00 | 4400.00 | vk sam engineering
31.02 | 3½ X 120 sq. mm (45mm) | 22.00 | Set |  | 1800.00 | 39600.00 | 550.00 | 12100.00 | 799.00 | 17578.00 | 2154.00 | 47388.00 | 12100.00 | vk sam engineering
31.03 | 4 X 35 sq. mm (32mm) | 14.00 | Set |  | 750.00 | 10500.00 | 350.00 | 4900.00 | 399.00 | 5586.00 | 1130.00 | 15820.00 | 4900.00 | vk sam engineering
31.04 | 4 X 6 sq. mm (25mm) | 6.00 | Set |  | 600.00 | 3600.00 | 175.00 | 1050.00 | 199.00 | 1194.00 | 699.00 | 4194.00 | 1050.00 | vk sam engineering
32.00 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed /XLPE aluminium conductor cable of 1.1 KV grade as required.
32.01 | 3½ X 300 sq. mm | 2.00 | Set |  | 4800.00 | 9600.00 | 5500.00 | 11000.00 | 7999.00 | 15998.00 | 9472.00 | 18944.00 | 9600.00 | Shantha ELectricals and Engineers Pvt Ltd
33.00 | Supplying and laying of following size DWC HDPE pipe ISI marked of rating PN-6, PE-63 along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc. direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc. , complete as required.
33.01 | 90 mm dia (OD-90 mm & ID-76 mm nominal) | 200.00 | Mtr |  | 295.00 | 59000.00 | 300.00 | 60000.00 | 299.00 | 59800.00 | 772.00 | 154400.00 | 59000.00 | Shantha ELectricals and Engineers Pvt Ltd
34.00 | Supplying and laying of following size DWC HDPE pipe ISI marked of rating PN-6, PE-63 along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc. direct in concreted portion (75 cm below ground level) including Concrete cutting, excavation and refilling the trench but excluding sand cushioning and protective covering etc. , complete as required.
34.02 | 90 mm dia (OD-90 mm & ID-76 mm nominal) | 40.00 | Mtr |  | 350.00 | 14000.00 | 1240.00 | 49600.00 | 399.00 | 15960.00 | 817.00 | 32680.00 | 14000.00 | Shantha ELectricals and Engineers Pvt Ltd
35.00 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray cable tray with perforation not more than 17.5%, in convenient sections, joined with connectors, suitable supporting MS angles, including G.I. bolts & nuts, etc as required.
35.01 | 300 mm width X 50 mm depth X 1.6 mm thickness | 100.00 | Mtr |  | 1350.00 | 135000.00 | 960.00 | 96000.00 | 899.00 | 89900.00 | 818.00 | 81800.00 | 81800.00 | TRIGGO TECH ENGINEERING
36.00 | Supply and Installation of various Mild Steel structure fabricated using single section MS Channel/angle/flat/bar etc including cutting, welding, drilling, fixing in position using appropriate fasteners, grinding, painting with approved steel primer and two coats enamel paint etc. complete as required. | 1000.00 | Kg |  | 190.00 | 190000.00 | 140.00 | 140000.00 | 99.00 | 99000.00 | 133.00 | 133000.00 | 99000.00 | CHENNAI ENGINEERING SERVICES
37.00 | Providing and fixing 25 mm X 5 mm GI strip in 40 mm dia 'B' Class G.I. pipe from earth electrode including connection with brass nut, bolt, spring, washer and brassing i/c excavation of bituminous/ concrete / pavement & excavation of Soil to the depth of 0.30 Mtrs from ground, refilling the Soil and with 1:2:4 concrete on top for 0.15 Mtrs after laying Pipe and making good the same to original surface etc. complete as required. | 30.00 | Mtr |  | 320.00 | 9600.00 | 715.00 | 21450.00 | 499.00 | 14970.00 | 14750.00 | 442500.00 | 9600.00 | Shantha ELectricals and Engineers Pvt Ltd
38.00 | Providing and fixing 25 mm X 5 mm GI strip in recess including cutting of concrete floor and finishing to original floor and connection with brass nut, bolt, spring, washer and brassing etc. as required. | 20.00 | Mtr |  | 350.00 | 7000.00 | 320.00 | 6400.00 | 349.00 | 6980.00 | 374.00 | 7480.00 | 6400.00 | vk sam engineering
39.00 | Providing and fixing earth bus of 25 mm X 5 mm GI strip on surface/recess in ground including connection with brass nut, bolt, spring, washer and brassing for connections etc. as required. | 200.00 | Mtr |  | 220.00 | 44000.00 | 225.00 | 45000.00 | 229.00 | 45800.00 | 374.00 | 74800.00 | 44000.00 | Shantha ELectricals and Engineers Pvt Ltd
40.00 | Providing of earth pits using Copper bonded Earth electrode of 17.2 mm dia, 3 Metres installed vertically as per the site conditions complete and top cover dully backfilled with backfill earth enhancing compound of 25 kgs. along with required masonary chamber, CI Cover outer size of 450mm X 450mm X 10mm including excavation & refilling etc as required. | 22.00 | Set |  | 14000.00 | 308000.00 | 6800.00 | 149600.00 | 19999.00 | 439978.00 | 13485.00 | 296670.00 | 149600.00 | vk sam engineering
41.00 | Supply and laying of 100 mm dia 'B' Class GI Pipe in cement concrete/bitumen for cable crossing/laying by cutting the bitumen/concrete/pavement , excavation upto maximum depth of 150mm and width 120 mm for laying the pipe, threading, cutting, joining of pipe & filling the gaps with bitumen mix/concrete of ratio 1:3:6 and making good the surface matching with original finish and disposal of left out excavated materials as required | 24.00 | Mtr |  | 2500.00 | 60000.00 | 2250.00 | 54000.00 | 2499.00 | 59976.00 | 1114.00 | 26736.00 | 26736.00 | TRIGGO TECH ENGINEERING
42.00 | Fixing of nominal 2 mm (Width 1 Mtr) thick PVC synthetic, electric insulated mats conforming to IS 15652-2006 along with suitable adhensive/ chemibond, i/c providing water proofing of floor, (chipping of floor if required) sealing of all joints and edges, providing reflective tap of 4cm all around the insulation mat etc., as required. | 60.00 | Sq.Mtr. |  | 300.00 | 18000.00 | 100.00 | 6000.00 | 99.00 | 5940.00 | 3375.00 | 202500.00 | 5940.00 | CHENNAI ENGINEERING SERVICES
43.00 | Supply, Installation, Testing and Commissioning of dewatering submersible system consisting of 2 Pumps i.e. 1working +1Standby of rating 1.5 KW/2 HP (Make: Grundfos Model: DPK.10.50.15.5.0D), suitable for 415 V, 50 HZ, AC power supply, non-sealed construction with discharge of 15 Cum/Hr @ 12 Meter Head Insulation class 'F’, non-clog, pump housing cast iron with all metal surfaces with cataphoresis coating/CED coated, suitable for intermittent operation in submerged condition, particle handling size of 10mm, CONTROL PANEL 2P 3PH 8A AUTO GIDPC, 2 Nos. cable water /level switch and all other standard accessories required to commission the system including power and control cabling i.e. from control panel to both pumps which are apart approximately 30Mtrs., Floor mounting ring stand, discharge elbow including gaskets nut bolts, screws, washer etc. as per OEM specifications complete as required. | 1.00 | Set |  | 45000.00 | 45000.00 | 202500.00 | 202500.00 | 249999.00 | 249999.00 | 83200.00 | 83200.00 | 45000.00 | Shantha ELectricals and Engineers Pvt Ltd
44.00 | Supply and laying of 80mm dia UPVC pipeline in surface or recess with associated pipe line accessories like flange, butterfly valve, gasket, reducer, elbow, Tee, MTA and FTA etc., complete as required. (Note: Linear measurement will be carried out considering pipe and other pipe line accessories). | 76.00 | Mtr |  | 3200.00 | 243200.00 | 1560.00 | 118560.00 | 999.00 | 75924.00 | 8878.00 | 674728.00 | 75924.00 | CHENNAI ENGINEERING SERVICES
45.00 | Supply, Installation, Testing and Commissioning of 160 A 4P MCCB (Ics=Icu) with inbuilt O/L and S/C fault protection with thermal magnetic release, with enclosure including providing Handle, with all accessories, with all accessories, interconnection, connection, earthing, etc. complete as required. | 1.00 | Job |  | 18000.00 | 18000.00 | 12000.00 | 12000.00 | 24999.00 | 24999.00 | 19949.00 | 19949.00 | 12000.00 | vk sam engineering
46.00 | Providing and laying cement concrete in retaining walls, return walls, walls (any thickness) including attached pilasters, columns, piers, abutments, pillars, posts, struts, buttresses, string or lacing courses, parapets, coping,bed blocks, anchor blocks, plain window sills, fillets, sunken floor,etc., up to floor five level, excluding the cost of centering, shuttering and finishing.
46.01 | Cement concrete in 1:3:6 (1 cement: 3 coarse sand : 6 graded stone aggregate 20mm nominal size) | 2.00 | Cum |  | 28500.00 | 57000.00 | 10500.00 | 21000.00 | 8999.00 | 17998.00 | 11898.00 | 23796.00 | 17998.00 | CHENNAI ENGINEERING SERVICES
46.02 | Cement mortar in 1:6 (1 cement: 6 coarse sand ) | 2.00 | Cum |  | 6500.00 | 13000.00 | 7500.00 | 15000.00 | 3999.00 | 7998.00 | 5713.00 | 11426.00 | 7998.00 | CHENNAI ENGINEERING SERVICES
46.03 | Brick work with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in foundation and plinth in with Cement mortar 1:6 (1 cement : 6 coarse sand). | 2.00 | Cum |  | 9800.00 | 19600.00 | 9500.00 | 19000.00 | 5999.00 | 11998.00 | 7938.00 | 15876.00 | 11998.00 | CHENNAI ENGINEERING SERVICES
46.04 | Cement plaster of 15 mm on the rough side of single or half brick wall of mix with 1:6 (1 cement: 6 coarse sand). | 10.00 | Sq Mtr |  | 370.00 | 3700.00 | 450.00 | 4500.00 | 329.00 | 3290.00 | 652.00 | 6520.00 | 3290.00 | CHENNAI ENGINEERING SERVICES
46.05 | Steel Rod for RCC Slabs | 200.00 | Kgs |  | 110.00 | 22000.00 | 115.00 | 23000.00 | 79.00 | 15800.00 | 143.00 | 28600.00 | 15800.00 | CHENNAI ENGINEERING SERVICES
47.00 | Dismantling of existing LT panel and Associated Works
47.01 | Dismantling of existing LT panel available at following locations including disconnection & dismantling of control and power cabling, earthing etc, dis-assembling the Panel from the PCC/metal structure alongwith shifting and transporting of LT Panel to Old Water Treatment Plant etc and handing over the same to AAI, complete as arequired and as per the instructions of the Engineer-In-Charge.
47.02 | Old WTP Feeder Pillar | 1.00 | Job |  | 6000.00 | 6000.00 | 3000.00 | 3000.00 | 5999.00 | 5999.00 | 12500.00 | 12500.00 | 3000.00 | vk sam engineering
47.03 | LT Panel for Old WTP Raw Water Pump Room | 1.00 | Job |  | 6000.00 | 6000.00 | 2500.00 | 2500.00 | 5999.00 | 5999.00 | 7500.00 | 7500.00 | 2500.00 | vk sam engineering
47.04 | LT Panel for Old WTP Pump Room | 1.00 | Job |  | 5000.00 | 5000.00 | 2500.00 | 2500.00 | 14999.00 | 14999.00 | 7500.00 | 7500.00 | 2500.00 | vk sam engineering
47.05 | LT Panel for Cowl Bazaar Pump Room | 1.00 | Job |  | 5000.00 | 5000.00 | 3500.00 | 3500.00 | 16999.00 | 16999.00 | 7500.00 | 7500.00 | 3500.00 | vk sam engineering
47.06 | i) LT Panel for 25 Pump Room - 1 Job ii) LT Panel for Cargo Well Pump Room - 1 Job iii) LT Panel for Old Fire Pump House - 1 Job | 3.00 | Job |  | 5000.00 | 15000.00 | 2500.00 | 7500.00 | 13999.00 | 41997.00 | 6550.00 | 19650.00 | 7500.00 | vk sam engineering
47.07 | Runway 25 side Outdoor LT Panel | 1.00 | Job |  | 5000.00 | 5000.00 | 3000.00 | 3000.00 | 19999.00 | 19999.00 | 7500.00 | 7500.00 | 3000.00 | vk sam engineering
47.08 | LT Panel for Old Pump Room / Cargo Pump Room | 1.00 | Job |  | 5000.00 | 5000.00 | 3000.00 | 3000.00 | 13999.00 | 13999.00 | 7500.00 | 7500.00 | 3000.00 | vk sam engineering
| Total in Figures |  |  |  |  | 7883900.00 |  | 5596250.00 |  | 6848125.00 |  | 8857188.00
Lowest Amount Quoted BY: vk sam engineering(5596250.00)

## BOQ Summary
BOQ Summary Details Tender Title: Renovation and Associated Works for Water Supply System at Chennai Airport. Sub Head. SITC of LT Panels and Other Associated Works Tender ID: 2022_AAI_125752_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | vk sam engineering | 5596250.00 | L1
| 2 | CHENNAI ENGINEERING SERVICES | 6848125.00 | L2
| 3 | Shantha ELectricals and Engineers Pvt Ltd | 7883900.00 | L3
| 4 | TRIGGO TECH ENGINEERING | 8857188.00 | L4