## BoQ1
Government eProcurement System Created By: Ashvin Kumar Singh Created Date/Time: 18-Oct-2022 04:40 PM Tender Title: Replacement of defective Fire hydrant line of City side / Air side at Chandigarh International Airport Mohali. Tender ID: 2022_AAI_129726_1
Tender Inviting Authority: Asstt. General Manager (Engg- Elect.), Chandigarh International Airport Ltd.(CHIAL), Mohali (PB)
Name of Work: Replacement of defective Fire hydrant line of City side / Air side at Chandigarh International Airport Mohali.
Contract No: 0172-2242404, 0172-2242434
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Modern Agencies(GSTN-04AAWFM7893FIZL)
[5 empty] | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Providing, laying, jointing testing and commissioning of following size of MS heavy (Class C) pipes conforming to IS-1239 including cutting , threading, welding,painting,providing PCC block support at required interval etc. with all accessories like all fittings (standard MS fitting with welded joint shall be used on the pipes) including tees, elbows, reducers, union, flanges, rubber gaskets, nut, bolts and washer etc., and shall be painted with one coat of Red Oxide Primer immediately after bringing the pipes to site and shall be painted with one coat of red oxide primer after erection & proper hydraulic testing and two or more coats of Synthetic Enamel Paint of approved shade on finishing. Prior to application of primer the surface should be cleaned for any dirt, rusts, rough substance etc. All pipe includes cost of supporting blocks / fixing pipe on wall / floor /ceiling with clamps, hangers (using anchor fasteners), MS angles/ channels of suitable size/specification. a) 150 mm | 395.00 | Mtr | 100.00 | 2200.00 | 869000.00 | 869000.00 | Modern Agencies
2.00 | Providing, fixing and jointing including testing C- class heavy duty mild steel pipes conforming to IS-1239, including cutting, welding, fittings viz bends, tees, reducers, flanges, nut-bolts, gasket complete and laying in ground including excavation, providing PCC block support at interval and giving suitable treatment for corrosion by way of min. 4mm thick corrosion protection tape which shall be wrapped comprising of coal tar/ asphalt component supported on fabric of organic/ inorganic fibre as per IS-10221, re-filling the trench etc.as required and as per enclosed specification. a) 150 mm dia | 90.00 | Mtr | 100.00 | 2600.00 | 234000.00 | 234000.00 | Modern Agencies
3.00 | Providing, laying, jointing testing and commissioning of following size of MS heavy (Class C) pipes conforming to IS-1239 including cutting , threading, welding,painting, etc. with all accessories like all fittings (standard MS fitting with welded joint shall be used on the pipes) including tees, elbows, reducers, union, flanges, rubber gaskets, nut, bolts and washer etc., and laying of pipe in existing trench, providing PCC block supports at regular interval and shall be provided with protection against corrosion by application of 4mm thick layer of anti-corrosive protection tape which shall be wrapped comprising of coal tar over the pipe, with overlap of 25mm minimum as per IS-10221. Prior to wrapping of anti-corroisive protection tape the surface should be cleaned for any dirt, rusts, rough substance etc. All pipe includes cost of laying of pipe in existing trench, supporting blocks, wrapping of anti-corroisive protection tape of suitable size/specification. a) 150 mm | 30.00 | Mtr | 10.00 | 2400.00 | 72000.00 | 72000.00 | Modern Agencies
4.00 | Providing, laying, jointing testing and commissioning of following size of MS heavy (Class C) pipes conforming to IS-1239 including cutting , threading, welding,painting,providing PCC block support at required interval etc. with all accessories like all fittings (standard MS fitting with welded joint shall be used on the pipes) including tees, elbows, reducers, union, flanges, rubber gaskets, nut, bolts and washer etc., and shall be painted with one coat of Red Oxide Primer immediately after bringing the pipes to site and shall be painted with one coat of red oxide primer after erection & proper hydraulic testing and two or more coats of Synthetic Enamel Paint of approved shade on finishing. Prior to application of primer the surface should be cleaned for any dirt, rusts, rough substance etc. All pipe includes cost of supporting blocks / fixing pipe on wall / floor /ceiling with clamps, hangers (using anchor fasteners), MS angles/ channels of suitable size/specification. a) 100 mm | 20.00 | Mtr | 100.00 | 1700.00 | 34000.00 | 34000.00 | Modern Agencies
5.00 | Excavating, Cutting, Dismantling, Shifting & re-fixing of Existing double headed external yard hydrant comprising of 100mm dia. stand pipe with bend, flange, 63mm dia. Gun Metal landing valve (ISI marked) conforming to IS-5290 (Type -B) with blank Gun-Metal cap & chain, cast iron wheel, complete as required and as per the site conditions. | 11.00 | Job | 100.00 | 1800.00 | 19800.00 | 19800.00 | Modern Agencies
6.00 | Cutting of pavment of concrete surface of minimum size 9m X 0.5m X 0.5m (Length x Breadth x Depth)by using Hilti machine/breaker and Diamond Cutter including removal of dismantled material and making good the damages with 1:2:4 (1 cement : 2 coarse sand and 4 stone aggregate 20 mm nominal size) Grade of pavement as required. | 3.00 | Job | 100.00 | 14000.00 | 42000.00 | 42000.00 | Modern Agencies
7.00 | Excavating, Cutting,dismantling, Shifting & re-fixing of Existing Fire Hose Cabinet outdoor type of size 0.750Mx 0.600Mx 0.250M near External Hydrant. A brick pedestal shall be constructed for supporting the hose box.The Job includes Excavating, Cutting,dismantling, Shifting & re-fixing of Existing Fire Hose Cabinet with brick pedestal as required and as per the site conditions. | 11.00 | Job | 100.00 | 2200.00 | 24200.00 | 24200.00 | Modern Agencies
| Total in Figures |  |  |  |  | 1295000.00
Lowest Amount Quoted BY: Modern Agencies(1295000.00)

## BOQ Summary
BOQ Summary Details Tender Title: Replacement of defective Fire hydrant line of City side / Air side at Chandigarh International Airport Mohali. Tender ID: 2022_AAI_129726_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Modern Agencies | 1295000.00 | L1