## BoQ1
Government eProcurement System Created By: SUJATHA R Created Date/Time: 01-Nov-2022 04:46 PM Tender Title: Replacement of AHUs (Phase-I, 8 Nos.) of ATS Complex, Southern Region, Chennai Airport. SH Replacement of AHUs at ATC Control Tower and Automation Area Tender ID: 2022_AAI_130554_1
Tender Inviting Authority: Asst. General Manager (Engg-Electrical), AAI, RHQ SR, Chennai Airport, Chennai - 600027
Name of Work: Replacement of AHUs (Phase-I, 8 Nos) of ATS Complex, Southern Region, Chennai Airport. SH: Replacement of AHUs at ATC Control Tower & Automation Area.
Contract No: 2022_AAI_130554_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Item Code | VOLTAS LIMITED(GSTN-33AAACV2809DIZT) |  | SNOWMEX ENGINEERS LIMITED(GSTN-07AAMCS8717P1ZF)
[5 empty] | Rate Without Tax | Rate With Tax | Rate Without Tax | Rate With Tax | L1 Rate Without Tax | L1 Bidder Without Tax | L1 Rate With Tax | L1 Bidder With Tax
1.00 | Dismantling the existing air handling units of following capacity i/c motor, blower, cooling coil, electrical panel, Chilled water pipelines at Inlet & Outlet of AHUs upto 3-way mixing valve, etc with all associated accessories and handing over of all dismantled items to AAI stores, including transportatioin, etc complete as required.
1.10 | 9.27 TR capacity at ATC control tower | 2.00 | Jobs | Item No.1 | 21220.00 | 25040.00 | 24000.00 | 28320.00 | 21220.00 | VOLTAS LIMITED | 25040.00 | VOLTAS LIMITED
1.20 | 28 TR capacity at Second floor & Third floor | 1.00 | Jobs | Item No.2 | 16850.00 | 19883.00 | 16800.00 | 19824.00 | 16800.00 | SNOWMEX ENGINEERS LIMITED | 19824.00 | SNOWMEX ENGINEERS LIMITED
2.00 | Supply of factory built floor mounted chilled water double skin type Air Handling Units made of 25mm thick panels consisting pre plasticised G.I casing of thickness 0.8mm outside layer and 0.8mm inside layer with polyurethene foam(PUF) insulation having 38 kg/cu.M density, factory injected between them by injection moulding machine, complete with blower section with Backward curve blower, blower suitable for static pressure as detailed below, PVC drift eliminators, cooling coil section with aluminium finned copper tubes (tube thickness not less than 0.5mm) cooling coil, filter sections with 50mm thick metal viscous /washable synthetic type air pre-filters, belt drive package with TEFC drive motor of efficiency class IE5 suitable for 415 ± 10% volts, 50Hz, 3 phase, AC Supply, suitably designed for variable frequency drive applications, drain connections, stainless steel (18G) drain pan with PUF insulation, LED light with door switch, Provision to install UVGI lamps between cooling coil and blower, PCC cubicals to position the base frame of AHUs, necessary vibration isolation arrangement etc., complete as per specification and of following capacities:
2.10 | a)10 TR Capacity, 5,600 CFM b)K.Calorie per hour-30,000 c)C.M Hr.- 9,515 d)Rows deep-4 e)Static pressure -55mmWC f) Pre-Filter: Having Filtration standard-90% efficiency down to 10 Microns g) MERV-13 Box type filter - 6 nos having size 540x540x300D each & to be fixed on the existing frame in the supply air Plenum. h) Supply blower - 1 No | 2.00 | set | Item No.3 | 470120.00 | 554742.00 | 420000.00 | 495600.00 | 420000.00 | SNOWMEX ENGINEERS LIMITED | 495600.00 | SNOWMEX ENGINEERS LIMITED
2.20 | a)30 TR Capacity, 16,800CFM b)K.Calorie per hour-90,000 c)C.M Hr.- 28,544 d)Rows deep-4 e)Static pressure -75mmWC f) Pre-Filter: Having Filtration standard-90% efficiency down to 10 Microns g) MERV-13 Box type filter - 9 nos having size 540x540x300D each suitable for 2000CFM & to be fixed on the existing frame in the supply air Plenum. h) Supply blower - 1 No | 1.00 | set | Item No.4 | 549850.00 | 648823.00 | 567000.00 | 669060.00 | 549850.00 | VOLTAS LIMITED | 648823.00 | VOLTAS LIMITED
3.00 | Installation, Testing & Commissioning of above air handling units at following locations for successful operation i/c refixing of dismantled UV lamp system, etc complete as required. Note: Since the location of item no 3.1 (i.e. 10 TR AHUs) is 30mtr hight from ground level and narrow passage to shift the materail to AHU room, the agencies are requested to inspect the site before qouting their rates.
3.10 | 10 TR & 5,600 CFM Capacity at ATC Control Tower (Fifth floor) | 2.00 | Jobs | Item No.5 | 23720.00 | 27990.00 | 16000.00 | 18880.00 | 16000.00 | SNOWMEX ENGINEERS LIMITED | 18880.00 | SNOWMEX ENGINEERS LIMITED
3.20 | 30 TR & 16,800 CFM Capacity at Third floor of ATS Complex | 1.00 | Jobs | Item No.6 | 24960.00 | 29453.00 | 9500.00 | 11210.00 | 9500.00 | SNOWMEX ENGINEERS LIMITED | 11210.00 | SNOWMEX ENGINEERS LIMITED
4.00 | The associated works complete to enable the commissioning of AHUs as required as below: a) Necessary modification in the existing GI ducting to made suit the mouth connection with the new AHU including supply & fixing of necessary thermal & acoustic insulation as required b) Necessary modification in the existing MS Chilled water pipeline including supply & fabrication of required new MS 'C' class pipes, 2 nos drain valves, supports, insulation with PUF sections, vapour barrier, GI wire mesh, sand cement plastering, Coloring, etc between butterfly valves & AHU. c) Necessary modification in the existing drain water piping for trouble free draining of condensate water including fabricating, supplying, fixing a 'U' trap with both side flanges (easy removal for cleaning) at the drain outlet of AHU. d) Termination of existing power cable, earth wires, control cables, etc
4.10 | 10 TR & 5,600 CFM Capacity at ATC Control Tower (Fifth floor) | 2.00 | Jobs | Item No.7 | 125600.00 | 148208.00 | 130000.00 | 153400.00 | 125600.00 | VOLTAS LIMITED | 148208.00 | VOLTAS LIMITED
4.20 | 30 TR & 16,800 CFM Capacity at Third floor of ATS Complex | 1.00 | Jobs | Item No.8 | 96280.00 | 113610.00 | 75000.00 | 88500.00 | 75000.00 | SNOWMEX ENGINEERS LIMITED | 88500.00 | SNOWMEX ENGINEERS LIMITED
5.00 | Supply, installation, testing and commissioning of variable frequency drive (VFD) starter panels with Star-Delta bypass facility near the AHUs constructed out of 2mm thick CRCA sheet duly powder coated as per specifications. The panel shall have hinged door with ON-OFF interlocks. The panel shall be complete with incoming MCCB/MCB, suitable connectioins, LED indicating lamps, Auto Manual switch, remote start / stop contacts, Ammeter with selector switch, Voltmeter with selector switch, necessary provision for Fire Damper controls & BMS controls, providing Connectors for power and control cables, earthing connectors, printed wiring diagram of starter panel, etc. as required complete as per specifications for following capacity AHUs.
5.10 | 10 TR & 5,600 CFM Capacity AHU at ATC Control Tower (Fifth floor) | 2.00 | Jobs | Item No.9 | 130460.00 | 153943.00 | 120000.00 | 141600.00 | 120000.00 | SNOWMEX ENGINEERS LIMITED | 141600.00 | SNOWMEX ENGINEERS LIMITED
5.20 | 30 TR & 16,800 CFM Capacity AHU at Third floor of ATS Complex | 2.00 | Jobs | Item No.10 | 179080.00 | 211314.00 | 144000.00 | 169920.00 | 144000.00 | SNOWMEX ENGINEERS LIMITED | 169920.00 | SNOWMEX ENGINEERS LIMITED
6.00 | Supply of following size butterfly valve wafer type with matching flanges, bolt nuts and insulation for chilled water header pipes in the AHU rooms.
6.10 | 100 mm dia | 2.00 | Set | Item No.11 | 7420.00 | 8756.00 | 6400.00 | 7552.00 | 6400.00 | SNOWMEX ENGINEERS LIMITED | 7552.00 | SNOWMEX ENGINEERS LIMITED
7.00 | Fixing of following size butterfly valves wafer type with matching flanges, bolt nuts, insulation, etc after made cutting in the existing chilled water header pipes of AHU rooms including removal of existing insulation etc complete as required.
7.10 | 100 mm dia | 2.00 | Jobs | Item No.12 | 10660.00 | 12579.00 | 4800.00 | 5664.00 | 4800.00 | SNOWMEX ENGINEERS LIMITED | 5664.00 | SNOWMEX ENGINEERS LIMITED
8.00 | Supply of following size butterfly valve wafer type with matching flanges, bolt nuts and insulation for supply & return chilled water pipes of AHUs.
8.10 | 80 mm dia | 2.00 | Jobs | Item No.13 | 5620.00 | 6632.00 | 6400.00 | 7552.00 | 5620.00 | VOLTAS LIMITED | 6632.00 | VOLTAS LIMITED
8.20 | 50 mm dia | 4.00 | Jobs | Item No.14 | 9880.00 | 11658.00 | 8400.00 | 9912.00 | 8400.00 | SNOWMEX ENGINEERS LIMITED | 9912.00 | SNOWMEX ENGINEERS LIMITED
9.00 | Fixing of following size butterfly valve wafer type with matching flanges, bolt nuts, insulation, etc after made cutting in the existing supply & return chilled water pipes of AHUs including removal of existing insulation etc complete as required.
9.10 | 80 mm dia | 2.00 | Jobs | Item No.15 | 8980.00 | 10596.00 | 3900.00 | 4602.00 | 3900.00 | SNOWMEX ENGINEERS LIMITED | 4602.00 | SNOWMEX ENGINEERS LIMITED
9.20 | 50 mm dia | 4.00 | Jobs | Item No.16 | 11720.00 | 13830.00 | 6200.00 | 7316.00 | 6200.00 | SNOWMEX ENGINEERS LIMITED | 7316.00 | SNOWMEX ENGINEERS LIMITED
10.00 | Supply of following size balancing valve with matching flanges and insulation
10.10 | 80 mm dia | 1.00 | Set | Item No.17 | 13870.00 | 16367.00 | 9500.00 | 11210.00 | 9500.00 | SNOWMEX ENGINEERS LIMITED | 11210.00 | SNOWMEX ENGINEERS LIMITED
10.20 | 50 mm dia | 2.00 | Set | Item No.18 | 21780.00 | 25700.00 | 15200.00 | 17936.00 | 15200.00 | SNOWMEX ENGINEERS LIMITED | 17936.00 | SNOWMEX ENGINEERS LIMITED
11.00 | Fixing of following size balancing valve with matching flanges and insulation
11.10 | 80 mm dia | 1.00 | Jobs | Item No.19 | 3620.00 | 4272.00 | 2500.00 | 2950.00 | 2500.00 | SNOWMEX ENGINEERS LIMITED | 2950.00 | SNOWMEX ENGINEERS LIMITED
11.20 | 50 mm dia | 2.00 | Jobs | Item No.20 | 5240.00 | 6183.00 | 4000.00 | 4720.00 | 4000.00 | SNOWMEX ENGINEERS LIMITED | 4720.00 | SNOWMEX ENGINEERS LIMITED
12.00 | Supply of following size MS " Y" Strainer with matching flanges and insulation
12.10 | 80 mm dia | 1.00 | Set | Item No.21 | 6300.00 | 7434.00 | 4300.00 | 5074.00 | 4300.00 | SNOWMEX ENGINEERS LIMITED | 5074.00 | SNOWMEX ENGINEERS LIMITED
12.20 | 50 mm dia | 2.00 | Set | Item No.22 | 8440.00 | 9959.00 | 6800.00 | 8024.00 | 6800.00 | SNOWMEX ENGINEERS LIMITED | 8024.00 | SNOWMEX ENGINEERS LIMITED
13.00 | Fixing of following size MS " Y" Strainer with matching flanges and insulation
13.10 | 80 mm dia | 1.00 | Jobs | Item No.23 | 3620.00 | 4272.00 | 2400.00 | 2832.00 | 2400.00 | SNOWMEX ENGINEERS LIMITED | 2832.00 | SNOWMEX ENGINEERS LIMITED
13.20 | 50 mm dia | 2.00 | Jobs | Item No.24 | 5240.00 | 6183.00 | 3600.00 | 4248.00 | 3600.00 | SNOWMEX ENGINEERS LIMITED | 4248.00 | SNOWMEX ENGINEERS LIMITED
14.00 | Supply of following size 3-way Modulating valve with actuator, matching flanges, insulation. Thermostat with temperature adjustment, necessary wiring for normal working, etc complete as required.
14.10 | 80 mm dia | 1.00 | Set | Item No.25 | 66000.00 | 77880.00 | 28000.00 | 33040.00 | 28000.00 | SNOWMEX ENGINEERS LIMITED | 33040.00 | SNOWMEX ENGINEERS LIMITED
14.20 | 50 mm dia | 2.00 | Set | Item No.26 | 53200.00 | 62776.00 | 48000.00 | 56640.00 | 48000.00 | SNOWMEX ENGINEERS LIMITED | 56640.00 | SNOWMEX ENGINEERS LIMITED
15.00 | ITC of following size 3-way Modulating valve with actuator, matching flanges, insulation. Thermostat with temperature adjustment, necessary wiring for normal working, etc complete as required.
15.10 | 80 mm dia | 1.00 | Jobs | Item No.27 | 6120.00 | 7222.00 | 2750.00 | 3245.00 | 2750.00 | SNOWMEX ENGINEERS LIMITED | 3245.00 | SNOWMEX ENGINEERS LIMITED
15.20 | 50 mm dia | 2.00 | Jobs | Item No.28 | 9360.00 | 11045.00 | 4700.00 | 5546.00 | 4700.00 | SNOWMEX ENGINEERS LIMITED | 5546.00 | SNOWMEX ENGINEERS LIMITED
16.00 | Supply of 25 mm ball valve with MS pipe nipple for AHU Chilled water Header lines | 6.00 | Set | Item No.29 | 7680.00 | 9062.00 | 3900.00 | 4602.00 | 3900.00 | SNOWMEX ENGINEERS LIMITED | 4602.00 | SNOWMEX ENGINEERS LIMITED
17.00 | Fixing of 25 mm ball valve with MS pipe nipple for AHU Chilled water Header lines | 6.00 | Jobs | Item No.30 | 5520.00 | 6514.00 | 1200.00 | 1416.00 | 1200.00 | SNOWMEX ENGINEERS LIMITED | 1416.00 | SNOWMEX ENGINEERS LIMITED
18.00 | Supply of industrial type Thermometer with adopter for AHU chilled water line,etc complete as required. | 6.00 | Nos | Item No.31 | 6420.00 | 7576.00 | 5700.00 | 6726.00 | 5700.00 | SNOWMEX ENGINEERS LIMITED | 6726.00 | SNOWMEX ENGINEERS LIMITED
19.00 | Fixing of industrial type Thermometer with adopter for AHU chilled water line,etc complete as required. | 6.00 | Jobs | Item No.32 | 4020.00 | 4744.00 | 5700.00 | 6726.00 | 4020.00 | VOLTAS LIMITED | 4744.00 | VOLTAS LIMITED
20.00 | Supply of dial type Pressure gauges having 150mm dia for AHUs including forged ball valves and pipe stem,etc complete as required. | 6.00 | Set | Item No.33 | 9960.00 | 11753.00 | 5700.00 | 6726.00 | 5700.00 | SNOWMEX ENGINEERS LIMITED | 6726.00 | SNOWMEX ENGINEERS LIMITED
21.00 | Fixing of dial type Pressure gauges having 150mm dia for AHUs including forged ball valves and pipe stem,etc complete as required. | 6.00 | Jobs | Item No.34 | 4020.00 | 4744.00 | 5700.00 | 6726.00 | 4020.00 | VOLTAS LIMITED | 4744.00 | VOLTAS LIMITED
22.00 | Supply of Canvass Connection between AHU & Duct made of fire retardant type cloth etc complete as required. | 4.00 | Nos | Item No.35 | 9000.00 | 10620.00 | 8000.00 | 9440.00 | 8000.00 | SNOWMEX ENGINEERS LIMITED | 9440.00 | SNOWMEX ENGINEERS LIMITED
23.00 | Fixing of Canvass Connection between AHU & Duct made of fire retardant type cloth etc complete as required. | 4.00 | Jobs | Item No.36 | 6760.00 | 7977.00 | 4000.00 | 4720.00 | 4000.00 | SNOWMEX ENGINEERS LIMITED | 4720.00 | SNOWMEX ENGINEERS LIMITED
24.00 | Supply of Opposed blade G.I Construction box type factory fabricated duct Volume Control Damper made of 18 SWG thick GI Sheet complete with nuts, bolts, screw, linkage, flanges, etc duct lever and quadrants etc complete as required. | 2.79 | Sqm | Item No.37 | 17465.40 | 20609.40 | 21762.00 | 25679.00 | 17465.40 | VOLTAS LIMITED | 20609.40 | VOLTAS LIMITED
25.00 | ITC of Opposed blade G.I Construction box type factory fabricated duct Volume Control Damper made of 16 SWG thick GI Sheet complete with nuts, bolts, screw, linkage, flanges, etc duct lever and quadrants etc complete as required. | 2.79 | Sqm | Item No.38 | 4715.10 | 5564.10 | 5580.00 | 6584.00 | 4715.10 | VOLTAS LIMITED | 5564.10 | VOLTAS LIMITED
| Total in Figures |  |  |  | 1970770.50 | 2325513.50 | 1757392.00 | 2073722.00

## BOQ Summary
BOQ Summary Details Tender Title: Replacement of AHUs (Phase-I, 8 Nos.) of ATS Complex, Southern Region, Chennai Airport. SH Replacement of AHUs at ATC Control Tower and Automation Area Tender ID: 2022_AAI_130554_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | SNOWMEX ENGINEERS LIMITED | 2073722.00 | L1
| 2 | VOLTAS LIMITED | 2325513.50 | L2