## BoQ1
Government eProcurement System Created By: RAMESH BABU K Created Date/Time: 28-Dec-2022 10:31 AM Tender Title: Replacement of Existing Conventional Column light fittings with RGB LED fittings at CIA SH Provision of Facade lighting at T1 and T4 terminal Tender ID: 2022_AAI_130580_1
Tender Inviting Authority: Jt. General Manager (Engg-Elect)-II, Electrical Maintenance Division-II, Operational Offices, Airports Authority of India, Chennai Airport
Name of Work:Replacement of Existing Conventional Column light fittings with RGB LED fittings at CIA. SH: Provsision of Façade lighting at T1 and T4 Terminal.
Contract No:
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | SABHARI ELECTRICALS(GSTN-NA) |  | AMAR ELECTRIC CO(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SH: -I SITC of Light Fittings and Controller
1.01 | Design and Supply,installation, testing and commissioining of BIS registered RGBW ( neutral white) LED LINEAR GRAZING (LINEAR WALL WASHER) for FACADE lighting with housing material of extruded aluminum with die-cast aluminum end caps, powder-coated finish, system wattage not exceeding 45W at full load and system lumen output of shall be 1800 lumens and with all LEDs ON. Fixture shall be available with high power LED and architectural optics with choice of beam angles such as narrow,medium,wide and Elliptical as per site requirement . The luminaire shall be capable of producing dynamic colour changing light with 16 millions colours as light fixture shall be programmable using required bit control DMX protocol/Ethernet based control The luminaries shall be with Anti-aging and anti-UV high optical efficiency and lens shall be made up by of UL/VDE /PMMA lens approved PC for each LED and clear tempered glass for better illumination. Luminaire should have IP67 rated male/female connectors for DMX through wiring. Fixture shall be suitable to operate at ambient temperature range of -10°C to +50°C. Fixture shall have input voltage for 24 V DC. Lifetime of LED should be at least 50,000 burning hours at L70 at 50 degree centigrade and shall be IP 66 and Ik06 rated. Lumainaire shll be conforming to BIS 10322 and shall be complete with all necessary accessories required for proper working of fixture including weather proof connection cables,water proof connectors, supply and fixing external driver of suitable wattage by considering one driver for every six lumainaire,. as per technical specifications and junction for making control cable and power conection to the fittings etc as required.LOCATION : Terminal building T1 & T4 Canopy Roof at 25m height | 1080.00 | Each |  | 33300.00 | 35964000.00 | 33755.00 | 36455400.00 | 35964000.00 | SABHARI ELECTRICALS
1.02 | Design, Supply,installation,testing and commissioning of BIS registered RGBW(neutral white) LED LINEAR GRAZING (LINEAR WALL WASHER) luminaire for FACADE LIGHTING with housing material of extruded aluminum with die-cast aluminum end caps, powder-coated finish, system wattage not exceeding 24W and at full load,system lumen output of shall be 1100 lumens with all LEDs ON . Fixture shall be available with high power LED and architectural optics with choice of beam angles such narrow,medium,wide, or ellptical as per site requirement. The luminaire shall be capable of producing dynamic colour changing light with 16 millions colours as light fixture shall be programmable using required bit control DMX protocol/Ethernet based control. The luminaries shall be with Anti-aging and anti-UV high optical efficiency and lens shall be made UL/VDE/PMMA lens approved PC for each LED and clear tempered glass for better illumination. Luminaire should have IP67 rated male/female connectors for DMX through wiring. Fixture shall suitable to operate at ambient temperature range of -10°C to 50°C and shall be IP 66 and IK 06 rated. . Lifetime should be at least 50,000 burning hours at L70 at 50 degree centigrade. Luminaire shll be conforming to BIS 10322 and shall be complete with all necessary accessories required for proper working of fixture including weather proof connection cables,water proof connectors, supply and fixing external driver of suitable wattage by considering one driver for every five luminaire,. as per technical specifications and junction for making control cable and power conection to the fittings etc as required. The bidder shall submit the Catalogues with all details LM 79, and LM 80 reports is mandatory as per direction of E.I.C and technical specification. Location: Terminal Building T1 & T4 Deparature shed at 4metre height | 260.00 | Each |  | 22000.00 | 5720000.00 | 30100.00 | 7826000.00 | 5720000.00 | SABHARI ELECTRICALS
1.03 | Design ,Supply,installation,testing and commissioning of BIS registered RGBW (neutral white) LED flood light luminaire for facade lighting. The luminaire housing material shall be extruded aluminum with die-cast aluminum end caps, powder-coated finish, system wattage not exceeding 50W at full load and system lumen output of shall be 2300 lumens with all LEDs ON. Fixture shall be available with architectural optics with choice of beam angles of such as narrow, medium,wide or elliptical beam as per site reequirement. The luminaire shall be capable of producing dynamic colour changing light with 16 million colours as light fixture shall be programmable using required bit control DMX protocol/Ethernet based control. The luminaries shall be with Anti-aging and anti-UV high optical efficiency and lens shall be UL/VDE/ PMMA lens of approved PC for each LED and clear tempered glass for better illumination. Luminaire should have IP67 rated male/female connectors for DMX through wiring. Fixture shall be suitable to operate at an ambient temperature range of -10°C to 50°C and shall be IP 66 and IK 06 rated. Fixture shall complete with driver and capable of operating at line voltage with out any separate power from 100 – 270V AC with power factor >0.9. Lifetime should be at least 50,000 burning hours at L70 at 50 degree centigrade with total IP66 protection. The lumainaire shall complete with integral driver and capable of operating at line voltage from 90V-305V. Lumainaire shll be conforming to BIS 10322 and shall be complete with all necessary accessories required for proper working of fixture including weather proof connection cables,water proof connectors etc as required. Location: Vechicular Lane Concrete V column at 10 metre height. | 72.00 | Each |  | 40000.00 | 2880000.00 | 55355.00 | 3985560.00 | 2880000.00 | SABHARI ELECTRICALS
1.04 | Design, Supply,installation,testing and commissioning of BIS registered RGBW(neutral white) LED flood light luminaire for facade lighting. The luminaire housing material shall be extruded aluminum with die-cast aluminum end caps, powder-coated finish. system wattage not exceeding 150W at full load and system lumen output of shall be 5500 lumens with all LEDs ON . Fixture shall be available with architectural optics with choice of beam angles of such narrow,medium,wide, or ellptical as per site requirement. . Luminaire should have IP67 rated male/female connectors for DMX through wiring. Fixture shall be suitable to operate at an ambient temperature range of -10°C to 50°C and shall be IP 66 and IK 06 rated. Fixture shall complete with driver and capable of operating at line voltage with out any separate power from 100 – 270V AC with power factor >0.9. Lifetime should be at least 50,000 burning hours at L70 at 50 degree centigrade with and shall be IP66 and IK 06 rated. The lumainaire shall complete with integral driver and capable of operating at line voltage from 90V-305V . Lumainaire shll be conforming to BIS 10322 and shall be complete with all necessary accessories required for proper working of fixture including weather proof connection cables,water proof connectors etc as required. Location: Terminal Building T1 & T4 Metal V column at 30m height | 64.00 | Each |  | 74000.00 | 4736000.00 | 83300.00 | 5331200.00 | 4736000.00 | SABHARI ELECTRICALS
1.05 | Design,Supply,installation,testing and commissioning of compact DMX signal amplifier that takes the incoming DMX512/RDM signal and amplify the signal and supporting bi-directional communications for discovery, addressing and DMX control of light fixtures. This unit takes the incoming DMX/RDM signal and splits the signal into six separate output channels allowing for expanding the number of devices controlled from 32 to 6 X 32. The output terminals are electronically isolated from the input & RDM-through port and share a common ground reference. All six output ports have an independent output driver to boost the DMX/RDM signal. Operating temperature shall be -10° to 50°C. The maximum power consumption shall be 4.5W and input voltage shall be 12-24V DC. | 30.00 | Each |  | 370.00 | 11100.00 | 75000.00 | 2250000.00 | 11100.00 | SABHARI ELECTRICALS
1.06 | Design,Supply,installation,Testing and commissioning of splitter with input voltage range 190-240V AC, power consumption less than 15W made up of with CRCA sheet with powder coated, Ingress protection rating IP20. This unit takes DMX signal from DMX controller and split the signal in to 8 seperate output channels. The ouput terminals of splitters are optically isolated from the input.Splitters should be capable to amplify the DMX signal.Operating temperature shall be -10° to 50°C. | 10.00 | Each |  | 370.00 | 3700.00 | 2000.00 | 20000.00 | 3700.00 | SABHARI ELECTRICALS
1.07 | Design,Supply,installation,testing and commissioning of Content program controller specifically designed for author, configure, and control, intrigate LED light shows in multiple zones with features as follows and as techncial specificattions and as per direction of E.I.C. • Input Power: 100 – 240 VAC or DC supply auto-switching •Operating Temperature - 0 to 50 Centigrade • Minimum supported LED nodes up to 10000 • Network Data compatibility Ethernet protocol. • The software composer required to create light shows for DMX controller/DMX programming. • Connector/Cable: (2) RJ45 ports, shielded Cat. 6 or better data cable of required length to be included for comunication . • Work as stand alone or computer driven controller. • Environment: Dry indoor location. •Ethernet keypad module for the DMX controller for selecting multible scene. •Ethernet Compact keypad that triggers the controller•Secure Digital SD card drive for flexible show •USB 2.0 interface for downloading shows and configuring from attached PC. • All others items required for sucesssful functioning of DMXcontroller shall be considered and included in the quoted rate. | 2.00 | Job |  | 450000.00 | 900000.00 | 625000.00 | 1250000.00 | 900000.00 | SABHARI ELECTRICALS
2.00 | Sub Head - II (Electrical Works)
2.01 | Supply of following size of 1.1kv grade multistrand Copper conductor XLPE insulated and PVC sheathed armoured cable as per IS : 7098 (part1)1988 with up to date amendments.
2.02 | (a) 4 x 4 Sq. mm. | 2800.00 | Metre |  | 530.00 | 1484000.00 | 200.00 | 560000.00 | 560000.00 | AMAR ELECTRIC CO
2.03 | (b) 3 x 2.5 Sq. mm. | 2200.00 | Metre |  | 370.00 | 814000.00 | 130.00 | 286000.00 | 286000.00 | AMAR ELECTRIC CO
2.04 | (c) 3 x 1.5 Sq. mm. | 1300.00 | Metre |  | 300.00 | 390000.00 | 95.00 | 123500.00 | 123500.00 | AMAR ELECTRIC CO
2.05 | Supply of following size of 1.1kv grade multistrand aluminium conductor XLPE insulated and PVC sheathed armoured cable as per IS : 7098 (part1)1988 with up to date amendments. 4C x 25 Sq. mm. | 660.00 | Metre |  | 485.00 | 320100.00 | 235.00 | 155100.00 | 155100.00 | AMAR ELECTRIC CO
2.06 | Fabrication, Supply, installation, Testing & Commissioning of Indoor wall mounted/floor mounted panel made up of CRCA sheet steel,IP42, Cubicle type, including providing and fixing 200A Aluminium Bus bar with all accessories suitable for opeation at 433 V, 3 Phase, 4 wire, 50HZ, A.C Powr supply System,compartmentalized and i/c providing and fixing following switch gears and accessories therin complete with connections,interconnections with suitble size of AL strips /bars/copper wires i/c powder coated with approved colour,complee with all accessories, interconnection, earthing, painting coating, earth studs cable Entry provision etc., as required as per technical specification. a) 160A, 35 KA, 4P MCCB with Thermal magnetic releases with spreader links,door interlock assembly and rotary handle,as incomer with R,Y,B,ON,OFF,TRIP indication LED lamps, rasin cast CT's with multifunction meter-as incomer - 1 set. b) 63A, 25KA, 4P MCCB with thermal magnetic releases,with rotary handle as outgoing - 6 Sets | 2.00 | Job |  | 360000.00 | 720000.00 | 265000.00 | 530000.00 | 530000.00 | AMAR ELECTRIC CO
2.07 | Fabrication, Supply, Testing & commissioning of 4way(4+12)ways surface/ recess mounting,, double door, 415 V, TPN MCB distribution board of sheet steel, dust protected, duly powder coating, inclusive of suitable Size bus bar, common neutral link, earth bar, din bar for mounting MCB's including Supply, fabrication of suitbale size and height of stand for mounting the Distribution board and consisting following incoming/outgoing . a) 4 way (4+ 12), Double door b) 63Amps , 4 pole MCB - 01 No c) 10 A - 32A SP MCB "C " Series - 12 Nos. | 4.00 | Job |  | 16500.00 | 66000.00 | 25000.00 | 100000.00 | 66000.00 | SABHARI ELECTRICALS
2.08 | Fabrication, Supply, Testing & commissioning of 12way(4+36)ways surface/ recess mounting, vertical type, double door, 415 V, TPN MCB distribution board of sheet steel, dust protected, duly powder coating , inclusive of suitable Size bus bar, common neutral link, earth bar, din bar for mounting MCB's including Supply, fabrication of suitbale size and height of stand for mounting the Distribution board and consisting following incoming/outgoing. a) 100A 25KA, MCCB - 1No as incomer. b) 20A, TP MCB - 12 Nos as outgoings | 4.00 | Job |  | 39990.00 | 159960.00 | 75000.00 | 300000.00 | 159960.00 | SABHARI ELECTRICALS
2.09 | Supplying and fixing following 4way, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder coating including earthing etc as required ( i/c the following MCB’s a) 4 way (MCB + 12), Double door b) 63amps Four Pole MCB c) 10 A - 32A SP MCB | 2.00 | Job |  | 29000.00 | 58000.00 | 20000.00 | 40000.00 | 40000.00 | AMAR ELECTRIC CO
2.10 | Supply , Installation, Testing and Commisioning of 3 Phase 75KVA servo stabilizer with Input voltage range 360 Volt to 460 volt and output voltage 415V+/- 1%, 50HZ, digital micro controller based with correction speed 16.6V to 70V/Sec, Manual/Autoreset with Time delay, with protection features as per OEM standard,IP 20 Protection, Metering, Rugged AC step synchronized motor, Indoor, Floor mounted, efficiency more than 95% etc as required. | 2.00 | Job |  | 230000.00 | 460000.00 | 200000.00 | 400000.00 | 400000.00 | AMAR ELECTRIC CO
2.11 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray (galvanization thickness not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.l. suspenders including G.l. bolts & nuts, etc. as required.
2.12 | a) 100 mm width X 50 mm depth X 1.6 mm thickness | 1340.00 | Meter |  | 350.00 | 469000.00 | 420.00 | 562800.00 | 469000.00 | SABHARI ELECTRICALS
2.13 | b) 150 mm width X 50 mm depth X 1.6 mm thickness | 250.00 | Meter |  | 410.00 | 102500.00 | 500.00 | 125000.00 | 102500.00 | SABHARI ELECTRICALS
2.14 | c) 225 mm width X 50 mm depth X 1.6 mm thickness | 570.00 | Meter |  | 480.00 | 273600.00 | 600.00 | 342000.00 | 273600.00 | SABHARI ELECTRICALS
2.15 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required.
2.16 | a) upto 35 sq. mm (clamped with 1mm thick MS flat clamp) | 6660.00 | Meter |  | 140.00 | 932400.00 | 330.00 | 2197800.00 | 932400.00 | SABHARI ELECTRICALS
2.17 | b) Above 35 sq. mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp) | 160.00 | Meter |  | 148.00 | 23680.00 | 690.00 | 110400.00 | 23680.00 | SABHARI ELECTRICALS
2.18 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required.
2.19 | a) Upto 35 sq. mm (clamped with 1mm thick saddle). | 150.00 | Meter |  | 325.00 | 48750.00 | 320.00 | 48000.00 | 48000.00 | AMAR ELECTRIC CO
2.20 | b) Above 35 sq. mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp) | 150.00 | Meter |  | 410.00 | 61500.00 | 600.00 | 90000.00 | 61500.00 | SABHARI ELECTRICALS
2.21 | Supplying and making end termination with brass compression gland and copper lugs for following size of PVC insulated and PVC sheathed / XLPE Copper conductor cable of 1.1 KV grade as required. a) 4C x 10 Sq.mm (25mm) | 202.00 | sets |  | 325.00 | 65650.00 | 810.00 | 163620.00 | 65650.00 | SABHARI ELECTRICALS
2.22 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
2.23 | a) 4 CX 25 sq. mm (28mm) | 16.00 | Sets |  | 230.00 | 3680.00 | 950.00 | 15200.00 | 3680.00 | SABHARI ELECTRICALS
2.24 | b) 3½ X 50 sq. mm (35mm) | 8.00 | Sets |  | 190.00 | 1520.00 | 1500.00 | 12000.00 | 1520.00 | SABHARI ELECTRICALS
2.25 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 meter long etc.(with charcoal/ coke and salt ) as required. | 4.00 | sets |  | 7400.00 | 29600.00 | 35000.00 | 140000.00 | 29600.00 | SABHARI ELECTRICALS
2.26 | Providing and Laying 4.00 mm dia copper wire on existing tray for loop earthing as required. | 1320.00 | Meter |  | 185.00 | 244200.00 | 150.00 | 198000.00 | 198000.00 | AMAR ELECTRIC CO
2.27 | Providing and Laying 2.00 mm dia copper wire on existing tray for loop earthing as required. | 3000.00 | Meter |  | 80.00 | 240000.00 | 50.00 | 150000.00 | 150000.00 | AMAR ELECTRIC CO
2.28 | Providing and fixing 25mm x 3mm copper strip in 40 mm dia G.I.Pipe from earth electrode including connection with brass nut, bolt, spring , washer etc as required. | 60.00 | Meter |  | 125.00 | 7500.00 | 1200.00 | 72000.00 | 7500.00 | SABHARI ELECTRICALS
2.29 | Supply and Fixing 140 x 140 x 95 mm SMC Junction Box with 32 Amps three Phase Connector Block in existing Pipe Structure etc., including all the fixing arrangements as required. | 80.00 | Each |  | 945.00 | 75600.00 | 1500.00 | 120000.00 | 75600.00 | SABHARI ELECTRICALS
2.30 | Dismantling of existing 150watts CDMT fittings and handed over to AAI as per direction of Engineer - in - Charge | 70.00 | Each |  | 1000.00 | 70000.00 | 500.00 | 35000.00 | 35000.00 | AMAR ELECTRIC CO
3.00 | Sub Head - III : Routine Preventive Maintainance contract
3.01 | Preventive Quarterly Maintenance for Façade Lighting System Comprising of all items installed in domestic terminal building and international terminal building as per Specifications & Schedule of Work, including providing Services with corrective maintenance resolution, cleaning and proper angle adjustment of fitting ,Special Occasion Programming etc. as & when decided by Engineer-in-Charge, with dedicated Call Center facility 12 x 7 hours with dedicated E-mail ID, telephone No. or with any other quick response facilites for quick responce and effective routine maintenance as per OEM standard and as per Special terms and conditions and direction of Engineer-in-charge.
3.02 | 1st Year | 1.00 | Year |  | 300000.00 | 300000.00 | 300000.00 | 300000.00 | 300000.00 | AMAR ELECTRIC CO, SABHARI ELECTRICALS
3.03 | 2nd Year | 1.00 | Year |  | 324000.00 | 324000.00 | 450000.00 | 450000.00 | 324000.00 | SABHARI ELECTRICALS
3.04 | 3rd Year | 1.00 | Year |  | 348000.00 | 348000.00 | 600000.00 | 600000.00 | 348000.00 | SABHARI ELECTRICALS
3.05 | 4th Year | 1.00 | Year |  | 372000.00 | 372000.00 | 700000.00 | 700000.00 | 372000.00 | SABHARI ELECTRICALS
3.06 | 5th Year | 1.00 | Year |  | 396000.00 | 396000.00 | 800000.00 | 800000.00 | 396000.00 | SABHARI ELECTRICALS
| Total in Figures |  |  |  |  | 59076040.00 |  | 66844580.00
Comparative Chart(eAuction)
Sl.No | Bidder Name | Auction Start Price | Quoted Rate in Figures and Words
|  |  | Bidder Price | Amount in Words
1 | SABHARI ELECTRICALS | 59076040.00 | 23476040.00 | Two Crore Thirty Four Lakh Seventy Six Thousand Fourty
2 | AMAR ELECTRIC CO | 59076040.00 | 23276040.00 | Two Crore Thirty Two Lakh Seventy Six Thousand Fourty
Lowest Amount Quoted BY: AMAR ELECTRIC CO(23276040.00)

## BOQ Summary
BOQ Summary Details Tender Title: Replacement of Existing Conventional Column light fittings with RGB LED fittings at CIA SH Provision of Facade lighting at T1 and T4 terminal Tender ID: 2022_AAI_130580_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | SABHARI ELECTRICALS | 59076040.00 | L1
| 2 | AMAR ELECTRIC CO | 66844580.00 | L2