## BoQ1
Government eProcurement System Created By: Ravindra singh Mehrok Created Date/Time: 07-Dec-2022 11:41 AM Tender Title: Replacement of Old Transformers at CA, Vadodara. Tender ID: 2022_AAI_132953_1
Tender Inviting Authority: Asst.Gen. Manager(E-E), AAI, CA, Vadodara
Name of Work: - Replacement of Old Transformers at CA, Vadodara.
Contract No: AAI / BO / E-E / NIT- 06 / Transformers / 2022-23
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Awasthi Electric Works(GSTN-09ABAPA1866D1Z5) |  | VIJAYPOWER GENERATORS LIMITED(GSTN-07AAACV0191N1Z4) |  | TEXMACO RAIL AND ENGINEERING LIMITED(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supplying, Installation, Testing & commissioning of 1600 KVA (Oil type Distribution transformer) 11KV / .433KV, Dyn11, 3phase 50Hz, IP 55, copper wound, Oil type step down transformer ONAN Mineral oil as per IS:335 i/c oil complete with all modern fittings as required including lifting lugs, Roller type bi-directional wheels,cable end box on HV side suitable for 3C X 240 Sqmm XLPE cable of 11KV grade including Cable termination to transformer and suitable busduct (2500Amps.) connection arrangement on LV side including Bus Duct modification (adding or/ and subtracting of Bus Duct) as per site condition, disconnecting chamber on both sides, winding temprature indication with alarm trip contacts, bucholz relay, earthing terminals, diagram and rating plates, explosion vent, OFF load tap changer (+7.5% to -7.5%) @ of 2.5% steps etc. complete as required. First filling of filtered dehyderated transformer oil and with topping quantities of oil to be supplied separately. Testing of oil before and after commissioning & also if filteration required is included in the scope. Losses, % Impedance and all other parameters complied with as per IS :1180 with upto date amendments, tender specifications etc complete as per site requirement.The warrantee of equipment shall be one year from certified date of the work completion. | 2.00 | Job |  | 3115000.00 | 6230000.00 | 3228000.00 | 6456000.00 | 4555555.00 | 9111110.00 | 6230000.00 | Awasthi Electric Works
2.00 | Dismantling, loading, unloading and Transportation of 1500 KVA, 11 KV/433 volt Distribution Transformer (oil type) along with all accessories within Vadodara Airport premises , location as per instruction by EIC, including hiring charges of heavy T & P such as crane/hydra, lorry etc. along with labour and incidental charges and local taxes etc (if any) complete as per site requirement. | 2.00 | Job |  | 20000.00 | 40000.00 | 18000.00 | 36000.00 | 99999.00 | 199998.00 | 36000.00 | VIJAYPOWER GENERATORS LIMITED
| Total in Figures |  |  |  |  | 6270000.00 |  | 6492000.00 |  | 9311108.00
Lowest Amount Quoted BY: Awasthi Electric Works(6270000.00)

## BOQ Summary
BOQ Summary Details Tender Title: Replacement of Old Transformers at CA, Vadodara. Tender ID: 2022_AAI_132953_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Awasthi Electric Works | 6270000.00 | L1
| 2 | VIJAYPOWER GENERATORS LIMITED | 6492000.00 | L2
| 3 | TEXMACO RAIL AND ENGINEERING LIMITED | 9311108.00 | L3