## BoQ1
Government eProcurement System Created By: SOLOMON PRABHAKAR Created Date/Time: 15-Dec-2022 01:24 PM Tender Title: Provision of UPS back up for GLF System at Hubballi Airport. SH SITC of 2 x 225 KVA Modular UPS System including AICMC for Five Years. Tender ID: 2022_AAI_133642_1
Tender Inviting Authority: ASST GENERAL MANAGER (ENGG-ELECTRICAL), AAI, HUBBALLI AIRPORT
Name of Work: Provision of UPS back up for GLF System at Hubballi Airport. SH: SITC of 2 x 225 KVA Modular UPS System including AICMC for Five Years.
Contract No: 2022_AAI_133642_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | RS Power Systems Pvt. Ltd.(GSTN-08AAICR2572F1ZA) |  | Novateur Electrical and Digital Systems Private Limited(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SH: I SITC of UPS SYSTEM : Supply, installation, Testing and commissioning of 2 x 225 kVA Modular UPS in 250 kVA frame (expandable up to 250 kW capacity in future with adding 1 more 25 kW Power module) and having provision of UPS to run in load sharing mode, battery management features integrated with main UPS controller, three phase input and three phase output, Each UPS shall have 9 no's of 25 kW Power modules, with built in PRS configurations N+1 (200 kW+25 kW) and Hot Swappable Modular UPS, minimum 30 mints backup battery for 200 kVA load @ 0.8 PF, Minimum VAH 1,72,000 in dual string with separate battery isolator for each sting (SMF battery of reputed approved make ), Input pf 0.99, Input THDi < 3%, with Efficiency > 96 % and output power factor Unity (225 kVA = 225 kW), and including all accessories like Top closed MS Rack for Housing the Batteries, Battery breaker, Battery inter connecting Cables, Battery Interlinks and DC cable between UPS and battery Bank for max recommended length of 12 meter (Per Run) as required. The system shall be true double conversion Online technology DSP based UPS system and also UPS shall be with automatic & manual bypass switch complete as required asper technical specifications. | 1.00 | Job |  | 8395200.00 | 8395200.00 | 3790000.00 | 3790000.00 | 3790000.00 | Novateur Electrical and Digital Systems Private Limited
2.00 | SH:II CMC of UPS Comprehensive Maintenance Contract of 2 x 225 kVA Modular UPS in 250 kVA frame (expandable up to 250 kW capacity in future with adding 1 more 25 kW Power module) for five years after completion of Two years of DLP , Comprehensive Maintenance Contract for Preventive and periodic servicing and replacement of defective parts (Excluding battery) asper OEM recommendation etc. complete as required to keep the system serviceable condition including unlimited breakdown calls during CMC period complete as required asper technical specification.
2.10 | First Year (after completion of DLP) Rate for First year after DLP = 4.76% of SH-I i.e., SITC cost of UPS SH-I Sl No.1 | 1.00 | Year |  | 399611.52 | 399611.52 | 180404.00 | 180404.00 | 180404.00 | Novateur Electrical and Digital Systems Private Limited
2.20 | Second Year (after completion of DLP) Rate for Second year after DLP = 6% escalation of SH-II Sl No.2.1 | 1.00 | Year |  | 423588.21 | 423588.21 | 191228.24 | 191228.24 | 191228.24 | Novateur Electrical and Digital Systems Private Limited
2.30 | Third Year (after completion of DLP) Rate for Third Year after DLP = 6% escalation of SH-II Sl No.2.2 | 1.00 | Year |  | 449003.50 | 449003.50 | 202701.93 | 202701.93 | 202701.93 | Novateur Electrical and Digital Systems Private Limited
2.40 | Fourth Year (after completion of DLP) Rate for Fourth Year after DLP = 6% escalation of SH-II Sl No.2.3 | 1.00 | Year |  | 475943.71 | 475943.71 | 214864.05 | 214864.05 | 214864.05 | Novateur Electrical and Digital Systems Private Limited
2.50 | Fifth Year (after completion of DLP) Rate for Fifth year after DLP = 6% escalation of SH-II Sl No.2.4 | 1.00 | Year |  | 504500.33 | 504500.33 | 227755.89 | 227755.89 | 227755.89 | Novateur Electrical and Digital Systems Private Limited
| Total in Figures |  |  |  |  | 10647847.27 |  | 4806954.11
Lowest Amount Quoted BY: Novateur Electrical and Digital Systems Private Limited(4806954.11)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of UPS back up for GLF System at Hubballi Airport. SH SITC of 2 x 225 KVA Modular UPS System including AICMC for Five Years. Tender ID: 2022_AAI_133642_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Novateur Electrical and Digital Systems Private Limited | 4806954.11 | L1
| 2 | RS Power Systems Pvt. Ltd. | 10647847.27 | L2