## BoQ1
Government eProcurement System Created By: Nirad Patra Created Date/Time: 13-Jan-2023 12:12 PM Tender Title: SITC of Clean agent fire suppression system (Novec 1230), Fire detection and alarm system, Auto dialer and other related electrical works for various CNS sites at VSS Airport, Jharsuguda. Tender ID: 2022_AAI_134682_1
Tender Inviting Authority: Asst. Gen. Manager (Engg-Elect), VSS Airport, Jharsuguda.
Name of Work: -SITC of Clean agent fire suppression system (Novec 1230), Fire detection & alarm system, Auto dialler and other related electrical works for various CNS sites at VSS Airport, Jharsuguda.
Contract No: - AAI/JSG/AGM(EE)/eNIT-12/2022 ( Tender Id : 2022_AAI_134682_1)
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Newage Fire Protection Engineers Pvt. Ltd.(GSTN-27AACCN9026C1ZN) |  | BA-PAN ENGINEERING co.(GSTN-07AYDPS2409Q1ZX) |  | CENTRE TAP ENGINEERING(GSTN-24AGPPP8172K1ZP) |  | Nexus Fire And Security Systems(GSTN-07AAKFN7125K1ZY) |  | FIRESTOP SALES AND SERVICES(GSTN-21AADFF1504B1ZJ) |  | DISCERN ENGINEERING PRIVATE LIMITED(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply, Installation, Testing & Commissioning of automatic fire gas (NOVAC 1230, AT 7% design concentration, flooding system comprising of the following as per NFPA 2001 & Uptodate Amendments standards complete as per tender specification, as per site requirment & as per direction of Engineer Incharge.
1.10 | Seamless storage 34 L cylinder of Novac 1230 agent complete with valve assembly, pressure gauge and pressure switch and other standard accessories. | 4.00 | Nos | 3933950.00 | 101779.00 | 407116.00 | 72000.00 | 288000.00 | 80000.00 | 320000.00 | 71760.00 | 287040.00 | 80850.00 | 323400.00 | 166134.00 | 664536.00 | 287040.00 | Nexus Fire And Security Systems
1.20 | Seamless storage 80 L cylinder of Novac 1230 agent complete with valve assembly, pressure gauge and pressure switch and other standard accessories. | 4.00 | Nos | 3933950.00 | 120604.00 | 482416.00 | 122000.00 | 488000.00 | 110000.00 | 440000.00 | 88205.00 | 352820.00 | 89425.00 | 357700.00 | 136172.00 | 544688.00 | 352820.00 | Nexus Fire And Security Systems
1.30 | Seamless storage 120L cylinder of Novac 1230 agent complete with valve assembly, pressure gauge and pressure switch and other standard accessories. | 1.00 | Nos | 3933950.00 | 133257.00 | 133257.00 | 140000.00 | 140000.00 | 116400.00 | 116400.00 | 91005.00 | 91005.00 | 101675.00 | 101675.00 | 150259.00 | 150259.00 | 91005.00 | Nexus Fire And Security Systems
2.00 | Supply, filling & handing over of clean, odourless, colour less, UL listed and suitable for fire class - A, B & C fire suppression agent (Novec 1230 fire suppresion fluid) for item no 1. etc. complete as per tender specification, as per site requirment & as per direction of Engineer Incharge. | 373.00 | Kgs | 3933950.00 | 2855.00 | 1064915.00 | 3200.00 | 1193600.00 | 3500.00 | 1305500.00 | 2365.00 | 882145.00 | 4663.00 | 1739299.00 | 3815.00 | 1422995.00 | 882145.00 | Nexus Fire And Security Systems
3.00 | Supply, Installation, Testing & Commissioning of Control head suitable for operating electrically from fire detection and control panel with all accessories. Suitable for auto opration of NOVAC1230 System complete as per site requirment & as per direction of Engineer Incharge. | 9.00 | Nos | 3933950.00 | 34718.00 | 312462.00 | 41000.00 | 369000.00 | 19400.00 | 174600.00 | 30820.00 | 277380.00 | 19600.00 | 176400.00 | 45195.00 | 406755.00 | 174600.00 | CENTRE TAP ENGINEERING
4.00 | Supply, Installation, Testing & Commissioning of Manually operated actuator to operate the gas manually from the cylinder with all accessories complete as per tender specification, as per site requirment & as per direction of Engineer Incharge. | 9.00 | Nos | 3933950.00 | 2315.00 | 20835.00 | 13000.00 | 117000.00 | 3686.00 | 33174.00 | 2900.00 | 26100.00 | 14700.00 | 132300.00 | 12737.00 | 114633.00 | 20835.00 | Newage Fire Protection Engineers Pvt. Ltd.
5.00 | Supply, Installation, Testing & Commissioning of Pneumatic actuator valve 1.2bar-6bar 24V or 230V AC for triggering the cylinder assembly complete as requirement complete as per tender specification, as per site requirment & as per direction of Engineer Incharge. | 9.00 | Nos | 3933950.00 | 6172.00 | 55548.00 | 13000.00 | 117000.00 | 4850.00 | 43650.00 | 22655.00 | 203895.00 | 4410.00 | 39690.00 | 43961.00 | 395649.00 | 39690.00 | FIRESTOP SALES AND SERVICES
6.00 | Supply, Installation, Testing & Commissioning of Directional Valve 1/2"-4" 24V as per requirement complete as per tender specification, as per site requirment & as per direction of Engineer Incharge. | 13.00 | Nos | 3933950.00 | 186303.00 | 2421939.00 | 23000.00 | 299000.00 | 38800.00 | 504400.00 | 55200.00 | 717600.00 | 47040.00 | 611520.00 | 181954.00 | 2365402.00 | 299000.00 | BA-PAN ENGINEERING co.
7.00 | Supply, Installation, Testing & Commissioning of High pressure flexible rubber discharge hose with braided reinforcement complete as per tender specification, as per site requirment & as per direction of Engineer Incharge. | 9.00 | Nos | 3933950.00 | 10493.00 | 94437.00 | 7200.00 | 64800.00 | 5820.00 | 52380.00 | 10506.00 | 94554.00 | 6738.00 | 60642.00 | 17022.00 | 153198.00 | 52380.00 | CENTRE TAP ENGINEERING
8.00 | Supply, Installation, Testing & Commissioning of Discharge nozzles designed to provide the proper flow and distribution of gas to flood hazard area at - 360 degrees/as per tender specification, as per site requirment & as per direction of Engineer Incharge. | 32.00 | Nos | 3933950.00 | 3704.00 | 118528.00 | 4000.00 | 128000.00 | 4365.00 | 139680.00 | 4082.00 | 130624.00 | 2817.00 | 90144.00 | 11152.00 | 356864.00 | 90144.00 | FIRESTOP SALES AND SERVICES
9.00 | Supply, Installation, Testing & Commissioning of Gas discharge pressure switch to trip A.C., electrical equip. etc for NOVAC 1230 System complete as per tender specification, as per site requirment & as per direction of Engineer Incharge. | 9.00 | Nos | 3933950.00 | 11573.00 | 104157.00 | 14000.00 | 126000.00 | 12125.00 | 109125.00 | 11615.00 | 104535.00 | 8820.00 | 79380.00 | 20543.00 | 184887.00 | 79380.00 | FIRESTOP SALES AND SERVICES
10.00 | Supply, Installation, Testing & Commissioning of Manifold check valve to permit removal of individual FM storage cylinders as per requirement for NOVAC 1230 System complete as per tender specification, as per site requirment & as per direction of Engineer Incharge. | 9.00 | Nos | 3933950.00 | 12344.00 | 111096.00 | 21000.00 | 189000.00 | 4559.00 | 41031.00 | 11902.00 | 107118.00 | 9800.00 | 88200.00 | 18195.00 | 163755.00 | 41031.00 | CENTRE TAP ENGINEERING
11.00 | Supply, Installation, Testing & Commissioning of Manual gas release station having manual break glass push button type call points with auxiliary contacts, hammer etc for NOVAC 1230 System complete as per tender specification, as per site requirment & as per direction of Engineer Incharge. | 17.00 | Nos | 3933950.00 | 1408.00 | 23936.00 | 2200.00 | 37400.00 | 2910.00 | 49470.00 | 1000.00 | 17000.00 | 2646.00 | 44982.00 | 2172.00 | 36924.00 | 17000.00 | Nexus Fire And Security Systems
12.00 | Supply, Installation, Testing & Commissioning of Manual gas abort station having manual break glass push button type call points with auxiliary contacts, hammer gland etc for NOVAC 1230 System complete as per tender specification, as per site requirment & as per direction of Engineer Incharge. | 17.00 | Nos | 3933950.00 | 1408.00 | 23936.00 | 2200.00 | 37400.00 | 2910.00 | 49470.00 | 1000.00 | 17000.00 | 2646.00 | 44982.00 | 2172.00 | 36924.00 | 17000.00 | Nexus Fire And Security Systems
13.00 | Design, Supply, Installation, Testing & Commissioning of Fire Alarm Gas release panel with built in time relay, auto/manual selector switch, housed in a suitable 16 SWG M.S. Sheet panel for succesful auto operation of NOVAC 1230 System during fire condition. The control panel shall have the arrangement for Audio / Visual indications by dual lamps LED's for fire and fault in each zone with lamp test facility. The control panel shall be provided with standby power supply of 2 x 12 volts, 7 AH sealed maintenance free batteries complete with circuit wiring etc., as per IS : 2189 & uptodate Amendment and have Provision for testing each circuit separately including resetting complete as per tender specification, as per site requirment & as per direction of Engineer Incharge. | 17.00 | Nos | 3933950.00 | 35860.00 | 609620.00 | 14000.00 | 238000.00 | 19400.00 | 329800.00 | 15444.00 | 262548.00 | 11956.00 | 203252.00 | 52398.00 | 890766.00 | 203252.00 | FIRESTOP SALES AND SERVICES
14.00 | Supplying, installation , testing and commissioning of conventional , optical / ionisation type smoke detector, conforming to UL/LPCB/FMI/EN-54, with all accessories viz : indicator, base, base box etc. to be installed on ceiling / false ceiling etc. complete as per site requirment & as per direction of Engineer Incharge. | 32.00 | Nos | 3933950.00 | 1408.00 | 45056.00 | 1000.00 | 32000.00 | 1940.00 | 62080.00 | 1228.50 | 39312.00 | 1039.00 | 33248.00 | 1963.00 | 62816.00 | 32000.00 | BA-PAN ENGINEERING co.
15.00 | Providing and fixing of Class-C heavy duty M.S. seamless pipe ASTM A-106(Sch 40) complete with all fittings painting with one coat of red oxide and 2 coats of enamel paint; piping to be fixed on ceiling with MS suspended supports, clamps anchor fastners, cutting chases / holes in valve ceiling and making good the same as required for the 50 mm sizes (Make : Maharashtra seamless / Tata) complete as per site requirment & as per direction of Engineer Incharge. | 234.00 | Mtr | 3933950.00 | 934.00 | 218556.00 | 1300.00 | 304200.00 | 1455.00 | 340470.00 | 1700.00 | 397800.00 | 1240.00 | 290160.00 | 1451.00 | 339534.00 | 218556.00 | Newage Fire Protection Engineers Pvt. Ltd.
16.00 | Supply and laying of PVC insulated, PVC sheathed, FRLS armored copper conductor of cable as per IS 1554- Part- I of size 2x1.5 sq. mm complete as per site requirment & as per direction of Engineer Incharge. | 700.00 | Mtr | 3933950.00 | 136.00 | 95200.00 | 190.00 | 133000.00 | 116.40 | 81480.00 | 112.00 | 78400.00 | 121.52 | 85064.00 | 132.00 | 92400.00 | 78400.00 | Nexus Fire And Security Systems
17.00 | Supplying, installation , testing and commissioning automatic telephone dialer module along with SIM card (Recharged till defect liability period) operating on GSM mobile sets, compitable to conventinal type fire control panel, capable of delivering pre recorded voice to preset telephone no in case of fire thorugh mobile net work etc. complete as per site requirment & as per direction of Engineer Incharge. | 14.00 | Nos | 3933950.00 | 18458.00 | 258412.00 | 9000.00 | 126000.00 | 14550.00 | 203700.00 | 5733.00 | 80262.00 | 5292.00 | 74088.00 | 10556.00 | 147784.00 | 74088.00 | FIRESTOP SALES AND SERVICES
18.00 | Supplying and fixing 20 amps, 240 volts, SPN industrial type, socket outlet, with 2 pole and earth, metal enclosed plug top alongwith 20 amps “C” curve, SP, MCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning etc. complete as per site requirment & as per direction of Engineer Incharge. | 68.00 | Nos | 3933950.00 | 6422.00 | 436696.00 | 1300.00 | 88400.00 | 727.50 | 49470.00 | 1697.00 | 115396.00 | 2450.00 | 166600.00 | 3218.00 | 218824.00 | 49470.00 | CENTRE TAP ENGINEERING
19.00 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt complete as per site requirment & as per direction of Engineer Incharge. | 4.00 | Set. | 3933950.00 | 26145.00 | 104580.00 | 13000.00 | 52000.00 | 19400.00 | 77600.00 | 26320.00 | 105280.00 | 22932.00 | 91728.00 | 10663.00 | 42652.00 | 42652.00 | DISCERN ENGINEERING PRIVATE LIMITED
21.00 | Supplying and laying 6 SWG G.I. wire at 0.50 metre below ground level for conductor earth electrode, including connection/ termination with GI thimble etc. complete as per site requirment & as per direction of Engineer Incharge. | 50.00 | Mtr | 3933950.00 | 616.00 | 30800.00 | 80.00 | 4000.00 | 194.00 | 9700.00 | 110.00 | 5500.00 | 137.00 | 6850.00 | 594.00 | 29700.00 | 4000.00 | BA-PAN ENGINEERING co.
22.00 | Providing and fixing 25 mm X 5 mm copper strip in 40 mm dia G.I. pipe from earth electrode including connection with brass nut, bolt, spring, washer excavation and re-filling etc. complete as per site requirment & as per direction of Engineer Incharge. | 50.00 | Mtr | 3933950.00 | 3116.00 | 155800.00 | 1400.00 | 70000.00 | 485.00 | 24250.00 | 1747.00 | 87350.00 | 2038.00 | 101900.00 | 1220.00 | 61000.00 | 24250.00 | CENTRE TAP ENGINEERING
23.00 | Supply and Installation of Numeric Make 2 KVA UPS,output volatge 230V, 50Hz suitable to operate on 170 to 250 V input Voltage with 6 nos. Sealed Maintenace Free 12V, 26/28 AH battery complete as per site requirment & as per direction of Engineer Incharge. | 1.00 | Nos. | 3933950.00 | 49290.00 | 49290.00 | 45000.00 | 45000.00 | 36860.00 | 36860.00 | 63414.00 | 63414.00 | 39690.00 | 39690.00 | 10261.00 | 10261.00 | 10261.00 | DISCERN ENGINEERING PRIVATE LIMITED
24.00 | Supply and Installation of Vertical air terminal 1 Mtrs.long made with solid 16 mm. dia. Copper rod tappered to 10mm dia complete as per site requirment & as per direction of Engineer Incharge. | 2.00 | Nos. | 3933950.00 | 7915.00 | 15830.00 | 5000.00 | 10000.00 | 5820.00 | 11640.00 | 4563.00 | 9126.00 | 2920.00 | 5840.00 | 3616.00 | 7232.00 | 5840.00 | FIRESTOP SALES AND SERVICES
25.00 | Supply and Erection of 7 mtr high mast made with suitable size GI pipe along with two sets of guy wire sets. Foundation base plate foundation bolts etc. and other mounting accessories etc. complete as per site requirment & as per direction of Engineer Incharge. | 2.00 | Nos. | 3933950.00 | 79435.00 | 158870.00 | 14000.00 | 28000.00 | 65960.00 | 131920.00 | 14157.00 | 28314.00 | 16248.00 | 32496.00 | 56796.00 | 113592.00 | 28000.00 | BA-PAN ENGINEERING co.
26.00 | Supply, Insttallation Testing and Commissioning of 14 Ltr. RO Purifier minimum 12Ltr./Hr. Filteration Capacity with 40 Ltr. Water cooler minimum 5Ltr./Min. water flow rate complete as per site requirment & as per direction of Engineer Incharge. | 3.00 | Set. | 3933950.00 | 82150.00 | 246450.00 | 63000.00 | 189000.00 | 29100.00 | 87300.00 | 15795.00 | 47385.00 | 56840.00 | 170520.00 | 33813.00 | 101439.00 | 47385.00 | Nexus Fire And Security Systems
27.00 | Supply, Insttallation Testing and Commissioning of 25 Ltr. Stroage 5star rated Water Geyser complete as per site requirment & as per direction of Engineer Incharge. | 2.00 | Nos. | 3933950.00 | 23516.00 | 47032.00 | 23000.00 | 46000.00 | 14550.00 | 29100.00 | 14040.00 | 28080.00 | 8232.00 | 16464.00 | 17201.00 | 34402.00 | 16464.00 | FIRESTOP SALES AND SERVICES
| Total in Figures |  |  |  |  | 7846770.00 |  | 4959800.00 |  | 4854250.00 |  | 4656983.00 |  | 5208214.00 |  | 9149871.00
Lowest Amount Quoted BY: Nexus Fire And Security Systems(4656983.00)

## BOQ Summary
BOQ Summary Details Tender Title: SITC of Clean agent fire suppression system (Novec 1230), Fire detection and alarm system, Auto dialer and other related electrical works for various CNS sites at VSS Airport, Jharsuguda. Tender ID: 2022_AAI_134682_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Nexus Fire And Security Systems | 4656983.00 | L1
| 2 | CENTRE TAP ENGINEERING | 4854250.00 | L2
| 3 | BA-PAN ENGINEERING co. | 4959800.00 | L3
| 4 | FIRESTOP SALES AND SERVICES | 5208214.00 | L4
| 5 | Newage Fire Protection Engineers Pvt. Ltd. | 7846770.00 | L5
| 6 | DISCERN ENGINEERING PRIVATE LIMITED | 9149871.00 | L6