## BoQ1
Government eProcurement System Created By: Krishna Kumar Soni Created Date/Time: 26-Dec-2022 03:09 PM Tender Title: Construction of DVOR building, approach path and other allied civil works. SH Electrical work at S.V. Airport, Raipur. Tender ID: 2022_AAI_135525_1
Tender Inviting Authority: Sr. Manager (E-E), Airports Authority of India, S.V. Airport, Raipur
Name of Work: Construction of DVOR building, approach path and other allied civil works. SH: Electrical work at S.V. Airport, Raipur.
Contract No: 2022_AAI_135525
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Awasthi Electric Works(GSTN-09ABAPA1866D1Z5) |  | Manish Electricals(GSTN-23ABLPM9012E1ZW)
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SH-I: LT Panel & SPDs
2.00 | Design, fabrication, supply, installation, testing and commissioning of vermin & dust proof, front operated cubicle type floor mounted, OUTDOOR double door type LT panel board made out of 2.0 mm thick for body & doors and all partitions shall be of 1.6 mm thick CRCA sheet, totally enclosed type, IP 54 ,duly rust inhibited, stove enameled, powder coated paint , fully compartmentalized complete with double hinged front door with lockable arrangement with name plates, heavy duty rubber gaskets, removable gland plates made out of 3 mm thick sheet steel, 02nos earth stud, MS angle iron channel, internal wiring with 1.5 sqmm FR copper wires/cable, connection, interconnection, mechanical interlocking between 2 incomers and Bus coupler including necessary civil works(if required) like PCC, brick work etc. complete as required. | 1.00 | Job | 183201.00 | 285000.00 | 285000.00 | 190000.00 | 190000.00 | 190000.00 | Manish Electricals
3.00 | Incomer
4.00 | 3 Nos. 160 A, four pole Thermal Magnetic release variable range, Moulded Case Circuit Breaker with extended rotary handle and all accessories including providing spreader terminals and auxiliary contacts (Ics=100% Icu value 25 KA ).
5.00 | a) 9 Nos. Phase indication LED lamps with 2Amp MCB, 03 Sets ON/OFF' indicating light with 2A MCB, 03 Nos Multifunction meter, class 0.5 with LCD Display shown V, A, Hz & PF.
6.00 | Bus Bar
7.00 | 400 Amps FP bus bar of high conductivity electrolytic quality aluminium alloy.
8.00 | Bus Coupler
9.00 | 1 No. 160 A, MCCB and 1 No. 160 A, Manual change over with extended rotary handle and all accessories including providing spreader terminals indication LED lamps with 2Amp MCB, ON/OFF etc. complate as required.
10.00 | Out Going
11.00 | 4 Nos. 100 A, four pole Thermal Magnetic release variable range, Moulded Case Circuit Breaker with extended rotary handle and all accessories including providing spreader terminals and auxiliary contacts (Ics=100% Icu value 25 KA).
12.00 | Note: Output of each changeover should be distributed to 2 Nos O/Gs with suitable subsections/compartments for MCCBs, bubars, metering, cable alleys etc.
13.00 | Design, fabrication, supply, installation, testing and commissioning of dust, damp and vermin proof cubicle free floor, indoor type factory built sheet steel enclosed modular bolted construction, suitable for operation on 415 ±10% volts, 50 Hz AC 3 phase 4 wire supply system fabricated out of CRCA sheet steel of 2.0 mm thick for frame work and 2.0 mm thick for doors/ covers, 3mm thick for gland plates i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having TPN Aluminium bus bars of high conductivity, DMC/SMC bus bar supports, bottom base channel of section not less than ISMC 75mm, entire panel shall have a common copper earth bar of suitable size with 2 nos earth studs, including control wiring with 1.5 sqmm. PVC insulated FRLS copper conductor Single Core cable for voltage & 2.5 sq.mm for current circuits, cable alleys, cable gland plates, danger notice plates, etc. necessary metering protections & indications and mounted with the following switch gears. | 1.00 | Job | 352834.00 | 400000.00 | 400000.00 | 340000.00 | 340000.00 | 340000.00 | Manish Electricals
14.00 | INCOMER i) 3 No. 100 Amps. 4P , MCCB '36KA, (Ics = Icu= 36KA) with thermal magnetic release having O/L & S/C protection equipped with extendable rotary Handle and extendable terminals with the following: ii) 6 Nos. Phase indication LED lamps with 2Amp MCB, 02 Sets ON/OFF' indicating light with 2A MCB, 02 Nos Multifunction meter, class 0.5 with LCD Display shown V, A, Hz & PF. iii) 1 No. for each incomer pre-wired Primary protection (Class B / Type 2) surge protection device (SPD) having 100KA , 10/350 micro seconds neutral to earth, 50 KA, 10/350 micro seconds line to neutral with limiting voltage less than 1.5 KV on the mains power entry point at the incomers. The enclosure shall have IP:55 weather proof with cable gland. The three phase SPD shall have the followings. i) Line protected : Line-Neutral and Neutral to earth + Line to Line +Line to Ground (4 modes). ii) Nominal Operating Voltage : 220/240 V AC iii) Input power Frequency : 47-60 Hz iv) Protection : Transverse and common mode v) Response Time : <100 ns vi) Surge rating : 10/350 us pulse response vii) Voltage Protection Level : < 1.5 KV viii) Approval and Testing : Listed with UL-1449-3/IEC - 61643 - 62305 as applicable.
15.00 | AUTO TRANSFER SWITCH i) 1 No. 4 pole, 100 Amps. Open execution type with complete protection.
16.00 | BUS-BAR : TPN aluminium main bus bars of minimum of 300 Amp capacity with heat shrinkable coloured sleeves and i/c DMC/SMC bus bars supports at required intervals complete.
17.00 | OUT GOING: i) 3 No. 63 Amps. 4P, MCCB '36KA, (Ics = Icu= 36KA) with thermal magnetic release having O/L & S/C protection equipped with extendable Rotary handle. ii) 1 No. 100Amps. 4P, MCCB '36KA, (Ics = Icu= 36KA) with thermal magnetic release having O/L & S/C protection equipped with extendable Rotary handle with the following: 4 Set of ON‐OFF indication lamps (LED type) with 2 Amp control MCBs. iii) 04 Nos 32 A, 10 kA, DP MCB
18.00 | Power Quality Analyzer & DATA LOGGER: Microprocessor based Multi channel Power Quality Analyzer and Data Logger device for electrical parameters measuring and monitoring on the data logger display as well as data archiving (storage) having inbuilt real time clock with power from a lithium-type battery
19.00 | Computer Set FOR DATA RECORD: 64 bit, Window 10 loaded with user friendly programs, 54.6 CM screen Monitor,CPU HP280Pro G6 Microtower PC , UPS Luminous 600VA, with Key board and Mouse all accessories having Intel Core i5 (10th Gen) or equivalent processor, HDD (1TB), RAM (8 GB), Graphic Card (1 GB) including Corporate office Computer Wooden Table Polished with office Chair-CBL003 etc. complete as required (HP or equivalent)
20.00 | The panel shall have suitable DIN bar provision for fixing the Surge Protection Device of min. 4 modules
21.00 | SH-II: Internal Electrical Works
22.00 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable etc. as required.
23.00 | Group C | 15.00 | Each | 1535.00 | 900.00 | 13500.00 | 1400.00 | 21000.00 | 13500.00 | Awasthi Electric Works
24.00 | Wiring for twin control light point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, 2 way modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable etc. as required. | 15.00 | Each | 1618.00 | 1450.00 | 21750.00 | 1500.00 | 22500.00 | 21750.00 | Awasthi Electric Works
25.00 | Wiring for light/ power plug with 2X4 sq. mm FRLS PVC insulated copper conductor single core cable in surface/ recessed medium class PVC conduit alongwith 1 No. 4 sq. mm FRLS PVC insulated copper conductor single core cable for loop earthing as required. | 60.00 | Meter | 373.00 | 175.00 | 10500.00 | 350.00 | 21000.00 | 10500.00 | Awasthi Electric Works
26.00 | Wiring for light/ power plug with 2X2.5 sq. mm FRLS PVC insulated copper conductor single core cable in surface/ recessed medium class PVC conduit alongwith 1 No. 2.5 sq. mm FRLS PVC insulated copper conductor single core cable for loop earthing as required. | 522.00 | Meter | 302.00 | 150.00 | 78300.00 | 200.00 | 104400.00 | 78300.00 | Awasthi Electric Works
27.00 | Wiring for light/ power plug with 4X4 sq. mm FRLS PVC insulated copper conductor single core cable in surface/ recessed medium class PVC conduit alongwith 2 Nos. 4 sq. mm FRLS PVC insulated copper conductor single core cable for loop earthing as required. | 100.00 | Meter | 553.00 | 340.00 | 34000.00 | 540.00 | 54000.00 | 34000.00 | Awasthi Electric Works
28.00 | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 3 pin 5/6 amps modular socket outlet and 5/6 amps modular switch, connection etc. as required. | 20.00 | Each | 545.00 | 299.00 | 5980.00 | 490.00 | 9800.00 | 5980.00 | Awasthi Electric Works
29.00 | Supplying and fixing suitable size GI Modular box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 5/6 & 15/16 A modular socket outlet and 15/16 A modular switch, connections etc. as required. | 20.00 | Each | 706.00 | 700.00 | 14000.00 | 600.00 | 12000.00 | 12000.00 | Manish Electricals
30.00 | Supply of 9 W LED Inverter/ rechargeable bulb With Auto-Charge Technology having Emergency time backup of not less than 4 Hours at min. of 50% illumination, suitable for 230 V, 50 Hz Single phase supply complete as required. (Similar to Make- Havells or equivalent). | 2.00 | Each | 483.00 | 435.00 | 870.00 | 525.00 | 1050.00 | 870.00 | Awasthi Electric Works
31.00 | Supply of 1200mm sweep. 5 star electrical ceiling fan without regulator complete with down rod. Canopies ,ball bearing , motor blades, capacitor etc. and suitable for use on 230volts. 50Hz single phase AC supply as required. (Similar to Make- Havells or equivalent). | 5.00 | Each | 3493.00 | 2870.00 | 14350.00 | 3200.00 | 16000.00 | 14350.00 | Awasthi Electric Works
32.00 | Supply of single phase, 300mm dia. 900 RPM sweep Heavy Exhaust fan having thermal overload protection, with Louver and shutter/safety Guard from foreign objects, etc. complete as required suitable for use on 230 volts, 50 Hz, single phase, A.C. supply. (Similar to Make- Havells or equivalent). | 4.00 | Each | 2969.00 | 2750.00 | 11000.00 | 2700.00 | 10800.00 | 10800.00 | Manish Electricals
33.00 | Supply of indoor surface/recesss mounting 20 W (nominal capacity), efficiency of LED light fitting (Efficacy) not less than 110 lumens/Watt, CRI (Colour Rendering Index) is minimum 80, THD should not less than 10% complete with LED tube rod, accessories etc and suitable for use on 140 to 270 volts, 50 Hz, single phase, A.C. supply as required (Similar to Make- Havells or equivalent). | 17.00 | Each | 277.00 | 325.00 | 5525.00 | 300.00 | 5100.00 | 5100.00 | Manish Electricals
34.00 | Supply of 30 W (nominal capacity) LED integral Flood Light type light fitting having pressure die cast housing with toughened glass, individual LEDs with secondary optics, IP 66, inbuilt convertor, accessories etc and suitable for use on 230 volts, 50 Hz, single phase, A.C. supply as required (Similar to Make- Havells or equivalent). | 8.00 | Each | 1997.00 | 2950.00 | 23600.00 | 1800.00 | 14400.00 | 14400.00 | Manish Electricals
35.00 | Installation, testing and commissioning of wall bracket /ceiling fittings of all sizes and shapes containing upto two GLS/CFL/ LED lamps per fitting/wall fan, complete with all accessories including connections etc. as required. | 30.00 | Each | 102.00 | 125.00 | 3750.00 | 80.00 | 2400.00 | 2400.00 | Manish Electricals
36.00 | Installation of exhaust fan Upto 300 mm sweep in the existing opening, including making good the damage, connection, testing, commissioning etc. as required. | 4.00 | Each | 372.00 | 400.00 | 1600.00 | 300.00 | 1200.00 | 1200.00 | Manish Electricals
37.00 | Supplying and fixing 3 pin 16 A Switch with socket in IP 66 enclosure suitable for outdoor installation on surface including connections etc. as required. | 2.00 | Each | 2707.00 | 3300.00 | 6600.00 | 300.00 | 600.00 | 600.00 | Manish Electricals
38.00 | Supply of Extention Board 4 X5/15 Amp. With individual switch socket with 30 meter using 3C x 1.5 sqmm copper conductor Armoured PVC sheathed cable. | 2.00 | Each | 5953.00 | 3400.00 | 6800.00 | 4800.00 | 9600.00 | 6800.00 | Awasthi Electric Works
39.00 | SH-III: Distribution Boards & MCBs
40.00 | Supplying and fixing of , Double door horizontal type PPI, three pole and neutral, sheet steel, MCB distribution board, 415 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator)
41.00 | 8 way Double door | 1.00 | Each | 2498.00 | 5600.00 | 5600.00 | 2000.00 | 2000.00 | 2000.00 | Manish Electricals
42.00 | 6 way (4 + 18) , Double door | 1.00 | Each | 5553.00 | 4500.00 | 4500.00 | 5000.00 | 5000.00 | 4500.00 | Awasthi Electric Works
43.00 | 12 way (8 + 36) , Double door | 1.00 | Each | 10291.00 | 6500.00 | 6500.00 | 9000.00 | 9000.00 | 6500.00 | Awasthi Electric Works
44.00 | Supplying and fixing 5 A to 32 A rating, 240/415 V, 10 kA, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.
45.00 | Single pole | 50.00 | Each | 329.00 | 200.00 | 10000.00 | 210.00 | 10500.00 | 10000.00 | Awasthi Electric Works
46.00 | Supplying and fixing of Four Pole 63 amps rating, 415 volts, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. | 2.00 | Each | 2673.00 | 1350.00 | 2700.00 | 1900.00 | 3800.00 | 2700.00 | Awasthi Electric Works
47.00 | Supplying and fixing of 63 A rating, (Three phase and neutral), 415 volts, residual current circuit breaker (RCCB), having a sensitivity current 300 milli amperes in the existing MCB DB complete with connections, testing and commissioning etc. as required. | 2.00 | Each | 4886.00 | 2750.00 | 5500.00 | 3800.00 | 7600.00 | 5500.00 | Awasthi Electric Works
48.00 | SH-IV: CABLE LAYING WORK
49.00 | Supply of aluminium conductor XLPE insulated, PVC sheathed, armoured power cable of 1.1 KV grade conforming to IS-7098 Part 1(1988) amended up to date.
50.00 | 3.5 X 150 Sq mm | 1000.00 | Meter | 979.00 | 620.00 | 620000.00 | 875.00 | 875000.00 | 620000.00 | Awasthi Electric Works
51.00 | Supply of copper conductor XLPE insulated, PVC sheathed, FRLSZH at outer Sheath armoured power cable of 1.1 KV grade conforming to IS-7098 Part 1(1988) amended up to date.
52.00 | 3 x 2.5 sq mm | 100.00 | Meter | 255.00 | 130.00 | 13000.00 | 350.00 | 35000.00 | 13000.00 | Awasthi Electric Works
53.00 | Supply of HDPE Pipe of size 160 mm OD, PE-63, PN-6 as per IS:4984 of wall thikness not less than 11.2 mm complete as required. | 1000.00 | Meter | 649.00 | 775.00 | 775000.00 | 620.00 | 620000.00 | 620000.00 | Manish Electricals
54.00 | Laying of 160 mm outer dia HDPE Pipe with HDD trenchless method direct in ground in all type soil including 4 mm PP rope coupling of pipe, etc. complete (3 mtr below in normal roads/soil and 6 mtr below runways and taxiways) in all respect as per specification. (Cost of HDPE Pipe is not included in the item) | 1000.00 | Mtr. | 883.00 | 500.00 | 500000.00 | 850.00 | 850000.00 | 500000.00 | Awasthi Electric Works
55.00 | Laying of following size HDPE pipe (PN8, PE 80 grade) DWC / HDPE ISI marked along with all accessory like socket, bend, coupler etc. complete with fitting and cutting joints etc. direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required.
56.00 | Upto 63 mm dia (OD-63 mm & ID-51 mm nominal) | 400.00 | Meter | 180.00 | 250.00 | 100000.00 | 210.00 | 84000.00 | 84000.00 | Manish Electricals
57.00 | Providing of rectangular type chamber having size 2 meter x 1.5 meter x 1.5 meter including brick works with position cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) of size 2 meter x 1.5 meter x 20 cm in bottom for foundation and rectangular type RCC 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) cover on top having thickness of 15 cm and minor civil work such as plastering and finishing etc. as required. | 4.00 | Job | 13542.00 | 18000.00 | 72000.00 | 14000.00 | 56000.00 | 56000.00 | Manish Electricals
58.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL/HDPE pipe as required.
59.00 | Upto 35 Sqmm | 400.00 | Meter | 31.00 | 30.00 | 12000.00 | 20.00 | 8000.00 | 8000.00 | Manish Electricals
60.00 | Above 95 sq. mm and upto 185 sq. mm | 1000.00 | Meter | 67.00 | 50.00 | 50000.00 | 50.00 | 50000.00 | 50000.00 | Awasthi Electric Works, Manish Electricals
61.00 | Supplying and making straight through joint of following size heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
62.00 | 3.5 C x 150 Sqmm | 3.00 | Each | 4458.00 | 4250.00 | 12750.00 | 4000.00 | 12000.00 | 12000.00 | Manish Electricals
63.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
64.00 | 3 X 2.5 sq. mm (12/16 mm) | 2.00 | Each | 422.00 | 120.00 | 240.00 | 300.00 | 600.00 | 240.00 | Awasthi Electric Works
65.00 | 3.5 X 150 sq. mm (50 mm) | 2.00 | Each | 982.00 | 450.00 | 900.00 | 800.00 | 1600.00 | 900.00 | Awasthi Electric Works
66.00 | 3.5 X 35 sq. mm (32 mm) | 7.00 | Each | 583.00 | 230.00 | 1610.00 | 500.00 | 3500.00 | 1610.00 | Awasthi Electric Works
67.00 | SH-V LIGHTNING CONDUCTOR & EARTHING WORKS
68.00 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 4.00 | Each | 10585.00 | 15250.00 | 61000.00 | 18000.00 | 72000.00 | 61000.00 | Awasthi Electric Works
69.00 | Providing and fixing 25 mm X 5 mm copper strip in 40 mm dia G.I. pipe from earth electrode including connection with brass nut, bolt, spring, washer excavation and re-filling etc. as required. | 16.00 | Meter | 1187.00 | 1450.00 | 23200.00 | 980.00 | 15680.00 | 15680.00 | Manish Electricals
70.00 | Providing and fixing 25 mm X 5 mm Copper strip on surface or in recess for connections etc. as required. | 30.00 | Meter | 871.00 | 1050.00 | 31500.00 | 780.00 | 23400.00 | 23400.00 | Manish Electricals
71.00 | Providing and fixing of lightning finial, made of 25 mm dia 300 mm long, copper tube, having single prong at top, with 85 mm dia 3mm thick copper base plate including holes etc. complete as required. | 2.00 | Each | 954.00 | 3000.00 | 6000.00 | 1000.00 | 2000.00 | 2000.00 | Manish Electricals
72.00 | Jointing copper / G.I. tape (with another copper/ G I tape, base of the final or any other metallic object) by riveting / nut bolting/ sweating and soldering etc. as required. | 2.00 | Each | 99.00 | 500.00 | 1000.00 | 150.00 | 300.00 | 300.00 | Manish Electricals
73.00 | SH-VI: AIR CONDITIONING WORKS
74.00 | Supply of 1.5 TR highly energy efficient, hi-wall mounted Split type inverter Air-conditioner with high ISEER, 5 star rating, dual inverter compressor, cordless remote, suitable for operation on 230 Volts +/- 10%, 50 Hz, single phase A.C. supply, having copper condenser coil, capable of performing cooling, dehumidifying, air circulating, filtering and ventilation complete etc. as required. | 6.00 | Nos | 50144.00 | 39900.00 | 239400.00 | 48000.00 | 288000.00 | 239400.00 | Awasthi Electric Works
75.00 | Installation, Testing & commissioning of indoor and outdoor 1.5 TR spilt Air conditioner units which includes mounting of indoor & outdoor unit including providing suitable size of MS angle type stand after preparing suitable height of PCC platform at their respective location along with laying of suitable size of refrigerant, UPVC drain pipeline with insulation & flexible PVC covering pipe up to 4 mtr. connecting both the units , leak testing of entire system, connecting both indoor and outdoor units with 4 core 2.5 sqmm PVC insulated flexible copper cable supplied with the unit , top up of refrigerant (if required), minor civil repairing work as per site requirement complete as required. | 6.00 | Job | 4762.00 | 2750.00 | 16500.00 | 4000.00 | 24000.00 | 16500.00 | Awasthi Electric Works
76.00 | Supply and laying of suitable size of refrigerant Pipe (suction / discharge pipeline) with insulation, UPVC drain pipeline with insulation & flexible PVC covering pipe for connecting both the units including supply and laying of 4 core 2.5 sqmm PVC insulated flexible copper cable. | 18.00 | Meter | 1376.00 | 1400.00 | 25200.00 | 900.00 | 16200.00 | 16200.00 | Manish Electricals
77.00 | Supply of Electronic digital Single Phase Changeover Switch (L&T Automatic Changeover with Current Limiter AUCL01030020) | 3.00 | Each | 1486.00 | 1750.00 | 5250.00 | 2000.00 | 6000.00 | 5250.00 | Awasthi Electric Works
78.00 | SH-VII: FADS & FIRE EXTINGUISHERS
79.00 | Supply and Installation of Microprocessor based 4 Zone non-expandable conventional fire alarm panel, should be equiped of 2 Zone capacity to take maximum 20 detections per Zone, reset function inbuilt and alarm & Fault Display by individual LEDs for each detector group. 240 volts AC power supply, automatic battery charges, 2 Nos. X 12 volt sealed maintenance free batteries sufficient for 12 hours normal working. | 1.00 | Each | 24401.00 | 17500.00 | 17500.00 | 30000.00 | 30000.00 | 17500.00 | Awasthi Electric Works
80.00 | Supply and Installation of 2 Channel Wireless auto dialer (GSM based) voice message. 40 (20+20) seconds voice recording. 9 nos. of tel./mobile 16 digit each. View numbers & user setting any time. Standard telephone key pads. Work with all types of GSM network. Easy menu based programming. 1 levels of password protected. Approved by various consultants. | 1.00 | Each | 19521.00 | 9000.00 | 9000.00 | 15000.00 | 15000.00 | 9000.00 | Awasthi Electric Works
81.00 | Supply and Installation of Conventional Type smoke Detector with LED indication, with mounting base complete etc. as required. | 8.00 | Each | 2440.00 | 1200.00 | 9600.00 | 3000.00 | 24000.00 | 9600.00 | Awasthi Electric Works
82.00 | Supply and Installation of Conventional Hooter complete etc. as required. | 4.00 | Each | 2928.00 | 1050.00 | 4200.00 | 3000.00 | 12000.00 | 4200.00 | Awasthi Electric Works
83.00 | Supply and Installation of manual call points complete etc. as required. | 1.00 | Each | 976.00 | 525.00 | 525.00 | 900.00 | 900.00 | 525.00 | Awasthi Electric Works
84.00 | SITC of Response indicator complete etc. as required. | 2.00 | Each | 488.00 | 200.00 | 400.00 | 300.00 | 600.00 | 400.00 | Awasthi Electric Works
85.00 | Supply of carbon dioxide (CO2) type fire extinguishers confi rming to IS 2878 : 1976 and cylinders fully charged of following capacity including providing suitable M.S. Stand. (a) 4.5 KG | 4.00 | Each | 6100.00 | 12500.00 | 50000.00 | 7000.00 | 28000.00 | 28000.00 | Manish Electricals
86.00 | Supply of multi-purpose Fire protection environmetn friendly dry chemical powder extinguishes type 1.3 Kg. GFO Fire Ball having ISO & OSHAS certification and approved by NTH which effective for all types of fire having minimum 5 years validity and multiple sensors. | 10.00 | Each | 3002.00 | 1900.00 | 19000.00 | 3500.00 | 35000.00 | 19000.00 | Awasthi Electric Works
87.00 | SH-VIII: Dismentaling A/C units & Panels
88.00 | Dismentaling Shifting of A/C units as availble at Existing DVOR to Electrical store which includes mounting of indoor & outdoor unit with MS stand at their respective location alongwith laying of refrigerant pipline with insulation & flexible PVC covering pipe upto standard lenght suppied with the unit connecting both the units leak testing of entire system conncting both indoor and outdoor units with three core 2.5sqmm PVC insulated flexible copper cable supplied with the unit, toup of refrigrent (if required) minor civil repairing work as per site requirment complete as required. | 6.00 | Each | 2040.00 | 800.00 | 4800.00 | 1000.00 | 6000.00 | 4800.00 | Awasthi Electric Works
89.00 | Dismentaling Shifting of outdoor and Indoor type change over panel from existing DVOR to Electrical Store site including foundation of panel etc as required. | 2.00 | Each | 2273.00 | 750.00 | 1500.00 | 1000.00 | 2000.00 | 1500.00 | Awasthi Electric Works
| Total in Figures |  |  |  |  | 3655000.00 |  | 4070530.00
Lowest Amount Quoted BY: Awasthi Electric Works(3655000.00)

## BOQ Summary
BOQ Summary Details Tender Title: Construction of DVOR building, approach path and other allied civil works. SH Electrical work at S.V. Airport, Raipur. Tender ID: 2022_AAI_135525_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Awasthi Electric Works | 3655000.00 | L1
| 2 | Manish Electricals | 4070530.00 | L2