## BoQ1
Government eProcurement System Created By: Krishna Kumar Soni Created Date/Time: 02-Jan-2023 04:49 PM Tender Title: Construction of Localizer hut and other associated Civil work. SH Electrical Work at S.V.Airport Raipur. Tender ID: 2022_AAI_135672_1
Tender Inviting Authority: Sr. Manager (E-E), Airports Authority of India, S.V. Airport, Raipur
Name of Work: Construction of localizer hut and other associated Civil work. SH: Electrical Work at S. V. Airport, Raipur.
Contract No: 2022_AAI_135672
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Awasthi Electric Works(GSTN-09ABAPA1866D1Z5)
[5 empty] | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SH-I: Internal Electrical Works
2.00 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in Fire Retardant uPVC trunking (as per IS 14927-Part 2), with modular switch, modular plate, suitable PVC box and earthing the point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable etc. as required.
3.00 | Group C | 20.00 | Each | 1485.00 | 900.00 | 18000.00 | 18000.00 | Awasthi Electric Works
4.00 | Wiring for light/ power plug with 2X4.0 sq. mm FRLS PVC insulated copper conductor single core cable in Fire Retardant uPVC trunking (as per IS 14927-Part 2) alongwith 1Nos. 4.0sq. mm FRLS PVC insulated copper conductor single core cable for loop earthing as required. | 120.00 | Meter | 555.00 | 175.00 | 21000.00 | 21000.00 | Awasthi Electric Works
5.00 | Wiring for light/ power plug/Wiring for circuit/ submain wiring with 2X2.5 sq. mm FRLS PVC insulated copper conductor single core cable in Fire Retardant uPVC trunking (as per IS 14927-Part 2) alongwith 1 No. 2.5 sq. mm FRLS PVC insulated copper conductor single core cable for loop earthing as required. | 80.00 | Meter | 272.00 | 160.00 | 12800.00 | 12800.00 | Awasthi Electric Works
6.00 | Supplying and drawing of 3 x 2.5 sq. mm sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required. | 180.00 | Meter | 149.00 | 125.00 | 22500.00 | 22500.00 | Awasthi Electric Works
7.00 | Supplying and fixing suitable size PVC Modular box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 5/6 & 15/16 A modular socket outlet and 15/16 A modular switch, connections etc. as required. | 25.00 | Each | 1315.00 | 700.00 | 17500.00 | 17500.00 | Awasthi Electric Works
8.00 | Supplying and fixing brass batten/ angle holder including connection etc. as required. | 2.00 | Each | 140.00 | 100.00 | 200.00 | 200.00 | Awasthi Electric Works
9.00 | Supply of 9 W LED Inverter/ rechargeable bulb With Auto-Charge Technology having Emergency time backup of not less than 4 Hours at min. of 50% illumination, suitable for 230 V, 50 Hz Single phase supply complete as required. | 2.00 | Each | 510.00 | 425.00 | 850.00 | 850.00 | Awasthi Electric Works
10.00 | Supply of 450 mm sweep wall fan having Aerodynamically designed, Balanced Blade, thermal overload protection, Jerk free oscillation (60o) & smooth running, 1400 RPM suitable for use on 230 volts, 50 Hz, single phase, A.C. supply etc. complete as required (Make:- Havells, Model -V3 or equivalent). | 2.00 | Each | 5481.00 | 2500.00 | 5000.00 | 5000.00 | Awasthi Electric Works
11.00 | Supply of indoor surface mounting 20 W (nominal capacity), LED light fitting efficacy of not less than 100 lumens, complete with LED tube rod, accessories etc and suitable for use on 230 volts, 50 Hz, single phase, A.C. supply as required. (Make:- Havells, Model - LHEXARP7UN1W020 LUMILINE or equivalent). | 15.00 | Each | 626.00 | 350.00 | 5250.00 | 5250.00 | Awasthi Electric Works
12.00 | Supply of 30 W (nominal capacity) LED integral Food Light type light fitting having pressure die cast housing with toughened glass, individual LEDs with secondary optics, IP 66, inbuilt convertor, accessories etc and suitable for use on 230 volts, 50 Hz, single phase, A.C. supply as required. (Make:- Havells, Model - LHEECNP7PB6J030 or equivalent). | 4.00 | Each | 1524.00 | 3000.00 | 12000.00 | 12000.00 | Awasthi Electric Works
13.00 | Supply of rechargeable portable type LED Emergency light with min 5 W output and having battery of suitable capacity to provide backup of min 3 Hrs. etc. complete as required.(Make:- Havells, Model LHEXAOPFUN1G005 or equivalent). | 2.00 | Each | 1115.00 | 1950.00 | 3900.00 | 3900.00 | Awasthi Electric Works
14.00 | Installation, testing and commissioning of wall bracket /ceiling fittings of all sizes and shapes containing upto two GLS/CFL/ LED lamps per fitting/wall fan, complete with all accessories including connections etc. as required. | 21.00 | Each | 97.00 | 150.00 | 3150.00 | 3150.00 | Awasthi Electric Works
15.00 | Supplying and fixing 3 pin 16 A Switch with socket in IP 66 enclosure suitable for outdoor installation on surface including connections etc. as required. | 3.00 | Each | 2909.00 | 3250.00 | 9750.00 | 9750.00 | Awasthi Electric Works
16.00 | Providing & fixing (80 X 50) mm size UPVC cable trunking on surface including necessary couplers, joint cover, angles etc. as required. | 30.00 | Meter | 1096.00 | 900.00 | 27000.00 | 27000.00 | Awasthi Electric Works
17.00 | Supply and fixing of 4 Module clip on supports suitable for fixing of switch, power Socket outlets including finishing plate etc. complete as required. | 25.00 | Each | 359.00 | 200.00 | 5000.00 | 5000.00 | Awasthi Electric Works
18.00 | SH-II: Distribution Boards & MCBs
19.00 | Supplying and fixing following way, single pole and neutral, sheet steel, glazed door, MCB distribution board, 240 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator)
20.00 | 8 way , Double door | 3.00 | Each | 2595.00 | 1500.00 | 4500.00 | 4500.00 | Awasthi Electric Works
21.00 | Supplying and fixing following way, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator)
22.00 | 6 way (4 + 18), Double door | 1.00 | Each | 6005.00 | 3500.00 | 3500.00 | 3500.00 | Awasthi Electric Works
23.00 | Supplying and fixing 5 A to 32 A rating, 240/415 V, 10 kA, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.
24.00 | Single pole | 20.00 | Each | 329.00 | 200.00 | 4000.00 | 4000.00 | Awasthi Electric Works
25.00 | Double pole | 2.00 | Each | 911.00 | 455.00 | 910.00 | 910.00 | Awasthi Electric Works
26.00 | Supplying and fixing of 63 amps rating, 415 volts, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.
27.00 | Four Pole | 1.00 | Each | 2673.00 | 1350.00 | 1350.00 | 1350.00 | Awasthi Electric Works
28.00 | Supplying and fixing of 25A rating, double pole, (single phase and neutral), 240 volts, residual current circuit breaker (RCCB), having a sensitivity current 300 milli amperes in the existing MCB DB complete with connections, testing and commissioning etc. as required. | 3.00 | Each | 3241.00 | 2250.00 | 6750.00 | 6750.00 | Awasthi Electric Works
29.00 | SH-III: LT Panel & SPDs
30.00 | Design, fabrication, supply, installation, testing and commissioning of vermin & dust proof, front operated cubicle type floor mounted, OUTDOOR double door type LT panel board made out of 2.0 mm thick for body & doors and all partitions shall be of 1.6 mm thick CRCA sheet, totally enclosed type, IP 54 ,duly rust inhibited, stove enameled, powder coated paint , fully compartmentalized complete with double hinged front door with lockable arrangement with name plates, heavy duty rubber gaskets, removable gland plates made out of 3 mm thick sheet steel, 02nos earth stud, MS angle iron channel, internal wiring with 1.5 sqmm FR copper wires/cable, connection, interconnection, mechanical interlocking between 2 incomers and Bus coupler including necessary civil works(if required) like PCC, brick work etc. complete as required. | 1.00 | Job | 183201.00 | 275000.00 | 275000.00 | 275000.00 | Awasthi Electric Works
31.00 | Incomer
32.00 | 3 Nos. 160 A, four pole Thermal Magnetic release variable range, Moulded Case Circuit Breaker with extended rotary handle and all accessories including providing spreader terminals and auxiliary contacts (Ics=100% Icu value 25 KA ).
33.00 | a) 9 Nos. Phase indication LED lamps with 2Amp MCB, 03 Sets ON/OFF' indicating light with 2A MCB, 03 Nos Multifunction meter, class 0.5 with LCD Display shown V, A, Hz & PF.
34.00 | Bus Bar
35.00 | 200 Amps FP bus bar of high conductivity electrolytic quality aluminium alloy.
36.00 | Bus Coupler
37.00 | 1 No. 160 A, MCCB and 1 No. 160 A, Manual change over with extended rotary handle and all accessories including providing spreader terminals indication LED lamps with 2Amp MCB, ON/OFF etc. complete as required.
38.00 | Out Going
39.00 | 4 Nos. 100 A, four pole Thermal Magnetic release variable range, Moulded Case Circuit Breaker with extended rotary handle and all accessories including providing spreader terminals and auxiliary contacts (Ics=100% Icu value 25 KA).
40.00 | Note: Output of each changeover should be distributed to 2 Nos O/Gs with suitable subsections/compartments for MCCBs, bubars, metering, cable alleys etc.
41.00 | Design, fabrication, supply, installation, testing and commissioning of dust, damp and vermin proof cubicle free floor, indoor type factory built sheet steel enclosed modular bolted construction, suitable for operation on 415 ±10% volts, 50 Hz AC 3 phase 4 wire supply system fabricated out of CRCA sheet steel of 2.0 mm thick for frame work and 2.0 mm thick for doors/ covers, 3mm thick for gland plates i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having TPN Aluminium bus bars of high conductivity, DMC/SMC bus bar supports, bottom base channel of section not less than ISMC 75mm, entire panel shall have a common copper earth bar of suitable size with 2 nos earth studs, including control wiring with 1.5 sqmm. PVC insulated FRLS copper conductor Single Core cable for voltage & 2.5 sq.mm for current circuits, cable alleys, cable gland plates, danger notice plates, etc. necessary metering protections & indications and mounted with the following switch gears. | 1.00 | Job | 352834.00 | 395000.00 | 395000.00 | 395000.00 | Awasthi Electric Works
42.00 | INCOMER i) 3 No. 100 Amps. 4P , MCCB '36KA, (Ics = Icu= 36KA) with thermal magnetic release having O/L & S/C protection equipped with extendable rotary Handle and extendable terminals with the following: ii) 6 Nos. Phase indication LED lamps with 2Amp MCB, 02 Sets ON/OFF' indicating light with 2A MCB, 02 Nos Multifunction meter, class 0.5 with LCD Display shown V, A, Hz & PF. iii) 1 No. for each incomer pre-wired Primary protection (Class B / Type 2) surge protection device (SPD) having 100KA , 10/350 micro seconds neutral to earth, 50 KA, 10/350 micro seconds line to neutral with limiting voltage less than 1.5 KV on the mains power entry point at the incomers. The enclosure shall have IP:55 weather proof with cable gland. The three phase SPD shall have the followings. i) Line protected : Line-Neutral and Neutral to earth + Line to Line +Line to Ground (4 modes). ii) Nominal Operating Voltage : 220/240 V AC iii) Input power Frequency : 47-60 Hz iv) Protection : Transverse and common mode v) Response Time : <100 ns vi) Surge rating : 10/350 us pulse response vii) Voltage Protection Level : < 1.5 KV viii) Approval and Testing : Listed with UL-1449-3/IEC - 61643 - 62305 as applicable.
43.00 | AUTO TRANSFER SWITCH i) 1 No. 4 pole, 100 Amps. Open execution type with complete protection.
44.00 | BUS-BAR : TPN aluminium main bus bars of minimum of 300 Amp capacity with heat shrinkable coloured sleeves and i/c DMC/SMC bus bars supports at required intervals complete.
45.00 | OUT GOING: i) 3 No. 63 Amps. 4P, MCCB '36KA, (Ics = Icu= 36KA) with thermal magnetic release having O/L & S/C protection equipped with extendable Rotary handle. ii) 1 No. 100Amps. 4P, MCCB '36KA, (Ics = Icu= 36KA) with thermal magnetic release having O/L & S/C protection equipped with extendable Rotary handle with the following: 4 Set of ON‐OFF indication lamps (LED type) with 2 Amp control MCBs. iii) 04 Nos 32 A, 10 kA, DP MCB
46.00 | Power Quality Analyzer & DATA LOGGER: Microprocessor based Multi channel Power Quality Analyzer and Data Logger device for electrical parameters measuring and monitoring on the data logger display as well as data archiving (storage) having inbuilt real time clock with power from a lithium-type battery
47.00 | Computer Set FOR DATA RECORD: 64 bit, Window 10 loaded with user friendly programs, 54.6 CM screen Monitor,CPU HP280Pro G6 Microtower PC , UPS Luminous 600VA, with Key board, HP Laser Jet Duplex Printer, Mouse and all accessories having Intel Core i5 (10th Gen) or equivalent processor, HDD (1TB), RAM (8 GB), Graphic Card (1 GB) including Corporate office Computer Wooden Table Polished with office Chair-CBL003 etc. complete as required (HP or equivalent)
48.00 | The panel shall have suitable DIN bar provision for fixing the Surge Protection Device of min. 4 modules
49.00 | SH-IV: CABLE LAYING WORK
50.00 | Supply of aluminium conductor XLPE insulated, PVC sheathed, armoured power cable of 1.1 KV grade conforming to IS-7098 Part 1(1988) amended up to date.
51.00 | 3.5 C X 150 Sq mm | 100.00 | Meter | 1058.00 | 625.00 | 62500.00 | 62500.00 | Awasthi Electric Works
52.00 | Supply of copper conductor XLPE insulated, PVC sheathed, armoured power cable of 1.1 KV grade conforming to IS-7098 Part 1(1988) amended up to date.
53.00 | 3 C x 10 Sqmm | 60.00 | Meter | 567.00 | 350.00 | 21000.00 | 21000.00 | Awasthi Electric Works
54.00 | 3 C x 2.5 sq mm | 130.00 | Meter | 157.00 | 130.00 | 16900.00 | 16900.00 | Awasthi Electric Works
55.00 | Supply of HDPE Pipe of size 160 mm OD, PE-63, PN-6 as per IS:4984 of wall thickness not less than 11.2 mm complete as required. | 100.00 | Meter | 649.00 | 775.00 | 77500.00 | 77500.00 | Awasthi Electric Works
56.00 | Laying of 160 mm outer dia HDPE Pipe with HDD trenchless method direct in ground in all type soil including 4 mm PP rope coupling of pipe, etc. complete (3 mtr below in normal roads/soil and 6 mtr below runways and taxiways) in all respect as per specification. (Cost of HDPE Pipe is not included in the item) | 100.00 | Mtr. | 883.00 | 500.00 | 50000.00 | 50000.00 | Awasthi Electric Works
57.00 | Laying of following size HDPE pipe (PN8, PE 80 grade) DWC / HDPE ISI marked along with all accessory like socket, bend, coupler etc. complete with fitting and cutting joints etc. direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required.
58.00 | upto 63 mm dia (OD-63 mm & ID-51 mm nominal) | 130.00 | Meter | 180.00 | 250.00 | 32500.00 | 32500.00 | Awasthi Electric Works
59.00 | Providing of rectangular type chamber having size 2 meter x 1.5 meter x 1.5 meter including brick works with position cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) of size 2 meter x 1.5 meter x 20 cm in bottom for foundation and rectangular type RCC 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) cover on top having thickness of 15 cm and minor civil work such as plastering and finishing etc. as required. | 2.00 | Job | 13542.00 | 18000.00 | 36000.00 | 36000.00 | Awasthi Electric Works
60.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL/HDPE pipe as required.
61.00 | Upto 35 Sqmm | 130.00 | Meter | 31.00 | 30.00 | 3900.00 | 3900.00 | Awasthi Electric Works
62.00 | Above 95 sq. mm and upto 185 sq. mm | 100.00 | Meter | 65.00 | 50.00 | 5000.00 | 5000.00 | Awasthi Electric Works
63.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required.
64.00 | Upto 35 sq. mm (clamped with 1mm thick saddle) | 60.00 | Meter | 31.00 | 100.00 | 6000.00 | 6000.00 | Awasthi Electric Works
65.00 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
66.00 | 3.5 C x 150 Sqmm | 3.00 | Each | 5016.00 | 4250.00 | 12750.00 | 12750.00 | Awasthi Electric Works
67.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
68.00 | 3.5 C X 150 sq. mm (50 mm) | 7.00 | each | 1008.00 | 450.00 | 3150.00 | 3150.00 | Awasthi Electric Works
69.00 | 3 C x 10 Sqmm | 2.00 | each | 402.00 | 200.00 | 400.00 | 400.00 | Awasthi Electric Works
70.00 | 3 C x 2.5 sq mm | 2.00 | each | 369.00 | 120.00 | 240.00 | 240.00 | Awasthi Electric Works
71.00 | SH V: EARTHING WORKS
72.00 | Lightning Conductor
73.00 | Providing and fixing of lightning finial, made of 25 mm dia 300 mm long, copper tube, having single prong at top, with 85 mm dia 3mm thick copper base plate including holes etc. complete as required. | 3.00 | Each | 954.00 | 3000.00 | 9000.00 | 9000.00 | Awasthi Electric Works
74.00 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 meter long etc. with charcoal/ coke and salt as required. | 4.00 | Each | 10969.00 | 15250.00 | 61000.00 | 61000.00 | Awasthi Electric Works
75.00 | Jointing copper / G.I. tape (with another copper/ G I tape, base of the final or any other metallic object) by riveting / nut bolting/ sweating and soldering etc. as required. | 3.00 | Each | 99.00 | 500.00 | 1500.00 | 1500.00 | Awasthi Electric Works
76.00 | Providing and fixing 25 mm X 5 mm copper strip in 40 mm dia G.I. pipe from earth electrode including connection with brass nut, bolt, spring, washer excavation and re-filling etc. as required. | 20.00 | Meter | 1187.00 | 1400.00 | 28000.00 | 28000.00 | Awasthi Electric Works
77.00 | Providing and fixing 25 mm X 5 mm Copper strip on surface or in recess for connections etc. as required. | 10.00 | Meter | 871.00 | 1050.00 | 10500.00 | 10500.00 | Awasthi Electric Works
78.00 | Providing and fixing copper tape 20mm X 3 mm thick on parapet or surface of wall for lightning conductor complete as required. (For horizontal run) | 35.00 | Meter | 451.00 | 700.00 | 24500.00 | 24500.00 | Awasthi Electric Works
79.00 | Providing and fixing copper tape 20mm X 3 mm thick on parapet or surface of wall for lightning conductor complete as required. (For Vertical run) | 15.00 | Meter | 512.00 | 700.00 | 10500.00 | 10500.00 | Awasthi Electric Works
80.00 | Providing and fixing testing joint, made of 20 mm X 3 mm thick Copper strip, 125 mm long, with 4 nos. of G.l. bolts, nuts, chuck nuts and spring washers etc. complete as required. | 3.00 | Each | 138.00 | 3000.00 | 9000.00 | 9000.00 | Awasthi Electric Works
81.00 | Providing and laying copper tape 32 mm X 6 mm from earth electrode in ground as required. | 20.00 | Meter | 1005.00 | 1600.00 | 32000.00 | 32000.00 | Awasthi Electric Works
82.00 | Supply and laying of 70 sqmm copper flexible cable for down conductor including suitable clamps and other accessories from air terminal to the earth pit. | 15.00 | Meter | 1210.00 | 900.00 | 13500.00 | 13500.00 | Awasthi Electric Works
83.00 | SH-VI: AIR CONDITIONING WORKS
84.00 | Supply of 1.5 TR (Nominal) Hi-Wall type Split Air conditioner 5 star BEE rating fitted with hermetically sealed rotary compressor operating on refrigerant R-32/Non CFC, minimum cooling capacity (Kcal/Hr) : 4500, Power Consumption (Max): 1500W with cleanable filters, cordless remote & all accessories supplied with the unit by OEM etc suitable for operation on 1 Ph, 230V, 50 Hz single phase AC supply. | 5.00 | Nos | 50144.00 | 39000.00 | 195000.00 | 195000.00 | Awasthi Electric Works
85.00 | Installation, Testing & commissioning of A/C units as mentioned in item no-1 which includes mounting of indoor & outdoor unit including supply and fixing of MS stand at their respective location along with laying of refrigerant pipeline with insulation & flexible PVC covering pipe up to standard length supplied with the unit , connecting both the units , leak testing of entire system, connecting both indoor and outdoor units with three core 2.5 sq mm PVC insulated flexible copper cable supplied with the unit , top up of refrigerant (if required), minor civil repairing work as per site requirement complete as required. | 5.00 | Job | 3674.00 | 2750.00 | 13750.00 | 13750.00 | Awasthi Electric Works
86.00 | Supply and laying of suitable size of refrigerant Pipe (suction / discharge pipeline) with insulation, UPVC drain pipeline with insulation & flexible PVC covering pipe for connecting both the units including supply and laying of 4 core 2.5 sqmm PVC insulated flexible copper cable. | 4.00 | Meter | 1376.00 | 1400.00 | 5600.00 | 5600.00 | Awasthi Electric Works
87.00 | Supply of Electronic Single Phase Changeover Switch (L&T Automatic Changeover with Current Limiter AUCL01030020) | 3.00 | Each | 1790.00 | 1750.00 | 5250.00 | 5250.00 | Awasthi Electric Works
88.00 | SH-VII: FADS & FIRE EXTINGUISHERS
89.00 | Supply and Installation of Microprocessor based 2 Zone non-expandable conventional fire alarm panel, should be equipped of 2 Zone capacity to take maximum 20 detections per Zone, reset function inbuilt and alarm & Fault Display by individual LEDs for each detector group. 240 volts AC power supply, automatic battery charges, 2 Nos. X 12 volt sealed maintenance free batteries sufficient for 12 hours normal working. | 1.00 | Each | 24401.00 | 12500.00 | 12500.00 | 12500.00 | Awasthi Electric Works
90.00 | Supply and Installation of 2 Channel Wireless auto dialer (GSM based) voice message. 40 (20+20) seconds voice recording. 9 nos. of tel./mobile 16 digit each. View numbers & user setting any time. Standard telephone key pads. Work with all types of GSM network. Easy menu based programming. 1 levels of password protected. Approved by various consultants. | 1.00 | Each | 19521.00 | 9000.00 | 9000.00 | 9000.00 | Awasthi Electric Works
91.00 | Supply and Installation of Conventional Type smoke Detector with LED indication, with mounting base complete etc. as required. | 4.00 | Each | 2440.00 | 1250.00 | 5000.00 | 5000.00 | Awasthi Electric Works
92.00 | Supply and Installation of Conventional Hooter complete etc. as required. | 1.00 | Each | 2928.00 | 1100.00 | 1100.00 | 1100.00 | Awasthi Electric Works
93.00 | Supply and Installation of manual call points complete etc. as required. | 1.00 | Each | 976.00 | 550.00 | 550.00 | 550.00 | Awasthi Electric Works
94.00 | SITC of Response indicator complete etc. as required. | 2.00 | Each | 488.00 | 400.00 | 800.00 | 800.00 | Awasthi Electric Works
95.00 | Supply of carbon dioxide (CO2) type fire extinguishers confirming to IS 2878 : 1976 and cylinders fully charged of following capacity including providing suitable M.S. Stand. (a) 4.5 KG | 4.00 | Each | 6100.00 | 12500.00 | 50000.00 | 50000.00 | Awasthi Electric Works
96.00 | Supply of multi-purpose Fire protection environment friendly dry chemical powder extinguishes type 1.3 Kg. GFO Fire Ball having ISO & OSHAS certification and approved by NTH which effective for all types of fire having minimum 5 years validity and multiple sensors. | 6.00 | Each | 3002.00 | 2000.00 | 12000.00 | 12000.00 | Awasthi Electric Works
97.00 | SH-VIII: Dismantling A/C units & Panels
98.00 | Dismantling Shifting of A/C units as available at Existing Localizer to Electrical store which includes mounting of indoor & outdoor unit with MS stand at their respective location alongwith laying of refrigerant pipeline with insulation & flexible PVC covering pipe upto standard length supplied with the unit connecting both the units leak testing of entire system connecting both indoor and outdoor units with three core 2.5sqmm PVC insulated flexible copper cable supplied with the unit, top of refrigerant (if required) minor civil repairing work as per site requirement complete as required. | 4.00 | Each | 2435.00 | 800.00 | 3200.00 | 3200.00 | Awasthi Electric Works
99.00 | Dismantling Shifting of outdoor and Indoor type change over panel from existing Localizer to Electrical Store site including foundation of panel etc as required. | 2.00 | Each | 2273.00 | 750.00 | 1500.00 | 1500.00 | Awasthi Electric Works
| Total in Figures |  |  |  |  | 1697500.00
Lowest Amount Quoted BY: Awasthi Electric Works(1697500.00)

## BOQ Summary
BOQ Summary Details Tender Title: Construction of Localizer hut and other associated Civil work. SH Electrical Work at S.V.Airport Raipur. Tender ID: 2022_AAI_135672_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Awasthi Electric Works | 1697500.00 | L1