## BoQ1
Government eProcurement System Created By: KAMBLE TANAJI Created Date/Time: 15-Dec-2022 03:26 PM Tender Title: Associate electrical works for operationalization of new terminal building, Sub Head Relocation of fire pump room. Tender ID: 2022_AAI_135783_1
Tender Inviting Authority: Asst. General Manager (Engg-Elect), Pune Airport
Name of Work: Associate electrical works for operationalization of new terminal building (SH: Relocation of fire pump room.)
Contract No:
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Voltas Ltd(GSTN-27AAACV2809D1ZM) |  | Sterling and Wilson Pvt. Ltd(GSTN-27AAACS9939D1Z4)
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supplying, installation, testing and commissioning of Electric driven Main Fire Pump suitable for automatic operation and consisting of following, complete in all respects, as required : (a) Horizontal type, multistage, centrifugal, split casing pump of cast iron body & bronze impeller with stainless steel shaft, mechanical seal conforming to IS 1520. (b) Suitable HP Squirrel cage induction motor, TEFC, synchronous speed 1500 RPM, suitable for operation on 415 volts, 3 phase 50 Hz, AC supply with IP 55 protection for enclosure, horizontal foot mounted type with Class-'F' insulation, conforming to IS-325. (c) M.S. fabricated Common base plate, coupling, coupling guard, foundation bolts etc. as required. (d) Suitable cement concrete foundation duly plastered with anti vibration pads. 2850 lpm at 70 m Head to ensure a minimum pressure of 3.5 kg/sq.cm. at highest and farthest outlet | 2.00 | Set |  | 738149.00 | 1476298.00 | 990459.00 | 1980918.00 | 1476298.00 | Voltas Ltd
2.00 | Supplying, installation, testing and commissioning of diesel engine driven main fire pump suitable for automatic operation and consisting of following, complete in all respects, as required : (a) Horizontal type, multistage, centrifugal pump of cast of iron body and bronze impeller with stainless steel shaft, mechanical seal conforming to IS 1520. (b) Suitable HP, 1500 RPM water cooled with radiator, diesel engine conforming to relevant IS standard complete with auto starting mechanism, 12 /24 volts electric starting equipment, diesel tank, exhaust pipe extended upto 10 m outside pump house duly insulated with 50 mm thick glass wool with 1.0 mm thick aluminium sheet cladding, residential silencer, instruments and protection as per standard specification, stop solenoid for auto stop in the event of fault with audio indications, painted with post office red colour etc. as required. (c) M.S fabricated, common base plate, coupling, coupling guard, foundation bolts etc. as required. (d) Suitable cement concrete foundation duly plastered and with anti vibration pads. 2850 lpm at 70 m Head to ensure a minimum pressure of 3.5 kg/sq.cm. at highest and farthest outlet | 1.00 | Set |  | 1074817.00 | 1074817.00 | 1086438.00 | 1086438.00 | 1074817.00 | Voltas Ltd
3.00 | Supplying, installation, testing and commissioning of electric driven pressurisation pump suitable for automatic operation and consisting of following, complete in all respects, as required : (Jockey Pump) (a) Horizontal type, multistage, centrifugal pump of cast iron body and bronze impeller with stainless steel shaft, mechanical seal conforming to IS : 1520. (b) Suitable HP squirell cage induction motor TEFC type suitable for operation on 415 volts, 3 phase 50 Hz AC supply with IP 55 class of protection for enclosure, horizontal foot mounted type with Class-'F' insulation, conforming to IS : 325. (c) M.S.fabricated Common base plate, coupling, coupling guard, foundation bolts etc. as required. (d) Suitable cement concrete foundation duly plastered and with anti vibration pads. 180 lpm at 70 m Head | 2.00 | Set |  | 157418.00 | 314836.00 | 154859.00 | 309718.00 | 309718.00 | Sterling and Wilson Pvt. Ltd
4.00 | Fabrication, supply, Insallation testing & commissioning of Electrical control panel DETAILED DESCRIPTION AS PER SOQ SL. NO. 4 OF TENDER DOCUMENT | 1.00 | Set |  | 1285073.00 | 1285073.00 | 682931.00 | 682931.00 | 682931.00 | Sterling and Wilson Pvt. Ltd
5.00 | Providing, laying, testing & commissioning of 'C' class heavy duty MS pipe conforming to IS 3589/IS 1239 including Welding, fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. and fixing the pipe on the wall/ceiling with suitable clamp/support frame and painting with two or more coats of synthetic enamel paint of required shade complete as required :
5.01 | 50 mm dia | 30.00 | Mtr |  | 1178.00 | 35340.00 | 1598.00 | 47940.00 | 35340.00 | Voltas Ltd
5.02 | 80 mm dia | 30.00 | Mtr |  | 1857.00 | 55710.00 | 2523.00 | 75690.00 | 55710.00 | Voltas Ltd
5.03 | 150 mm dia | 300.00 | Mtr |  | 3821.00 | 1146300.00 | 5331.00 | 1599300.00 | 1146300.00 | Voltas Ltd
5.04 | 200 mm dia (wall thickness 6.3 mm) | 50.00 | Mtr |  | 6152.00 | 307600.00 | 8338.00 | 416900.00 | 307600.00 | Voltas Ltd
6.00 | Providing laying, testing & commissioning of 'C' class heavy duty MS Pipe conforming to IS 1239/3589 i/c fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. in ground including welding, excavation & providing cement concrete blocks as supports, anticorrosive treatment with coaltar/asphalt tape as per IS 10221, refilling the trench etc. of following sizes complete as required.
6.01 | 200 mm. dia (wall thickness = 6.3 mm) | 60.00 | Mtr |  | 7726.00 | 463560.00 | 8338.00 | 500280.00 | 463560.00 | Voltas Ltd
6.02 | 150 mm. dia | 300.00 | Mtr |  | 4684.00 | 1405200.00 | 5331.00 | 1599300.00 | 1405200.00 | Voltas Ltd
7.00 | Supplying, fixing, testing & commissioning of double flanged sluice valve of rating PN 1.6 with non rising spindle, bronze/gun metal seat, ISI marked complete with nuts, bolts, washers, gaskets and conforming to IS 780 of following sizes as required :
7.01 | 80 mm dia | 4.00 | Set |  | 19070.00 | 76280.00 | 30348.00 | 121392.00 | 76280.00 | Voltas Ltd
7.02 | 150 mm dia | 7.00 | Set |  | 33546.00 | 234822.00 | 52823.00 | 369761.00 | 234822.00 | Voltas Ltd
7.03 | 200 mm dia | 2.00 | Set |  | 52556.00 | 105112.00 | 81614.00 | 163228.00 | 105112.00 | Voltas Ltd
8.00 | Supplying, fixing, testing and commissioning of butterfly valve of PN 1.6 rating with bronze/gunmetal seat duly ISI marked complete with nuts, bolts, washers, gaskets conforming to IS 13095 of following sizes as required :
8.01 | 50 mm dia | 1.00 | Set |  | 5016.00 | 5016.00 | 4118.00 | 4118.00 | 4118.00 | Sterling and Wilson Pvt. Ltd
8.02 | 80 mm dia | 2.00 | Set |  | 6101.00 | 12202.00 | 5121.00 | 10242.00 | 10242.00 | Sterling and Wilson Pvt. Ltd
9.00 | Providing, installation, testing and commissioning of non-return valve of following sizes confirming to IS: 5312 complete with rubber gasket, GI bolts, nuts, washers etc.as required :
9.01 | 80 mm dia | 2.00 | Set |  | 10709.00 | 21418.00 | 5736.00 | 11472.00 | 11472.00 | Sterling and Wilson Pvt. Ltd
9.02 | 150 mm dia | 3.00 | Set |  | 25490.00 | 76470.00 | 13913.00 | 41739.00 | 41739.00 | Sterling and Wilson Pvt. Ltd
10.00 | Providing, installation, testing and commissioning of stainless steel Y-strainer fabricated out of 1.6 mm thick stainless steel, Grade 304, sheet with 3 mm dia holes with stainless steel flange.
10.01 | 80 mm dia | 2.00 | Each |  | 25495.00 | 50990.00 | 11171.00 | 22342.00 | 22342.00 | Sterling and Wilson Pvt. Ltd
10.02 | 150 mm dia | 3.00 | Each |  | 82971.00 | 248913.00 | 17498.00 | 52494.00 | 52494.00 | Sterling and Wilson Pvt. Ltd
10.03 | 200 mm dia | 2.00 | Each |  | 100967.00 | 201934.00 | 27545.00 | 55090.00 | 55090.00 | Sterling and Wilson Pvt. Ltd
11.00 | Supplying and fixing air vessel made of 250 mm dia, 8mm thick MS sheet, 1200 mm in height with air release valve on top and flanged connection to riser, drain arrangement with 25 mm dia gun metal wheel valve with required accessories, pressure gauge and paintingwith synthetic enamel paint of approved shade as required. | 1.00 | Set |  | 58951.00 | 58951.00 | 50354.00 | 50354.00 | 50354.00 | Sterling and Wilson Pvt. Ltd
12.00 | Providing & fixing of pressure switch in M.S. pipe line including connection etc. as required. | 5.00 | Each |  | 3120.00 | 15600.00 | 6670.00 | 33350.00 | 15600.00 | Voltas Ltd
13.00 | Providing & fixing flow switch in following sizes M.S. pipe including connection etc as required. 150 mm dia | 7.00 | Each |  | 3233.00 | 22631.00 | 4450.00 | 31150.00 | 22631.00 | Voltas Ltd
14.00 | Providing, fixing, testing & commissioning of installation control valve of cast iron body, brass/bronze working parts comprising of water motor alarm, bronze seat clapper, clapper arm and hydraulically driven mechanical gong bell to sound continuous alarm when the wet riser/sprinkler system activates, pressure gauges, emergency releases, strainer, pressure switch, cock valve complete with drain valve and bypass, test control box, ball valves, MS pipe of required size, flanges, orifice plate, gasket etc of follwing sizes as required : 150 mm dia | 2.00 | Set |  | 139091.00 | 278182.00 | 77610.00 | 155220.00 | 155220.00 | Sterling and Wilson Pvt. Ltd
15.00 | Providing, Fixing, reinforced neoprene rubber vibration eliminators/expansion joints (to provide relief from stresses at pipe flanges) suitable for upto 16 kg/cm2 pressure, as per specification of the manufacturers complete as required and as specified.
15.01 | 150 mm dia | 6.00 | Each |  | 13000.00 | 78000.00 | 17498.00 | 104988.00 | 78000.00 | Voltas Ltd
15.02 | 80 mm dia | 4.00 | Each |  | 8883.00 | 35532.00 | 8288.00 | 33152.00 | 33152.00 | Sterling and Wilson Pvt. Ltd
16.00 | Supplying and fixing following way, single pole and neutral, sheet steel, MCB distribution board, 240 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator) 8 way, Double door | 1.00 | Each |  | 18630.00 | 18630.00 | 13281.00 | 13281.00 | 13281.00 | Sterling and Wilson Pvt. Ltd
17.00 | Supplying and fixing following rating, double pole, (single phase and neutral), 240V, residual current circuit breaker (RCCB), having a sensitivity current 30mA in the existing MCB DB complete with connections, testing and commissioning etc. as required. 63 A | 1.00 | Each |  | 4051.00 | 4051.00 | 6244.00 | 6244.00 | 4051.00 | Voltas Ltd
18.00 | Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, 10 kA, “C” curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. Single pole | 6.00 | Each |  | 590.00 | 3540.00 | 2894.00 | 17364.00 | 3540.00 | Voltas Ltd
19.00 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed steel conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required. Group C | 10.00 | Point |  | 1140.00 | 11400.00 | 8331.00 | 83310.00 | 11400.00 | Voltas Ltd
20.00 | Wiring for light/ power plug with 2X4 sq. mm FRLS PVC insulated copper conductor single core cable in surface/ recessed steel conduit alongwith 1 No 4 sq. mm FRLS PVC insulated copper conductor single core cable for loop earthing as required. | 80.00 | Mtr |  | 738.00 | 59040.00 | 583.00 | 46640.00 | 46640.00 | Sterling and Wilson Pvt. Ltd
21.00 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed steel conduit as required 2 X 4 sq. mm + 1 X 4 sq. mm earth wire | 40.00 | Mtr |  | 738.00 | 29520.00 | 583.00 | 23320.00 | 23320.00 | Sterling and Wilson Pvt. Ltd
22.00 | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 5/6 & 15/16 A modular socket outlet and 15/16 A modular switch, connections etc. as required. | 6.00 | Each |  | 1140.00 | 6840.00 | 1714.00 | 10284.00 | 6840.00 | Voltas Ltd
23.00 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 2.00 | Each |  | 16634.00 | 33268.00 | 15844.00 | 31688.00 | 31688.00 | Sterling and Wilson Pvt. Ltd
24.00 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 30.00 | Mtr |  | 1254.00 | 37620.00 | 287.00 | 8610.00 | 8610.00 | Sterling and Wilson Pvt. Ltd
25.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | 50.00 | Mtr |  | 228.00 | 11400.00 | 287.00 | 14350.00 | 11400.00 | Voltas Ltd
26.00 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc.direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required. 90 mm dia (OD-90 mm & ID-76 mm nominal) | 150.00 | Mtr |  | 966.00 | 144900.00 | 618.00 | 92700.00 | 92700.00 | Sterling and Wilson Pvt. Ltd
27.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL/DWC HDPE pipe as required. Above 95 sq. mm and upto 185 sq. mm | 150.00 | Mtr |  | 195.00 | 29250.00 | 192.00 | 28800.00 | 28800.00 | Sterling and Wilson Pvt. Ltd
28.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required.
28.01 | Upto 35 sq. mm (clamped with 1mm thick saddle) | 60.00 | Mtr |  | 141.00 | 8460.00 | 104.00 | 6240.00 | 6240.00 | Sterling and Wilson Pvt. Ltd
28.02 | Above 35 sq. mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp) | 60.00 | Mtr |  | 181.00 | 10860.00 | 132.00 | 7920.00 | 7920.00 | Sterling and Wilson Pvt. Ltd
28.03 | Above 95 sq. mm and upto 185 sq. mm (clamped with 25/40x3mm MS flat clamp) | 80.00 | Mtr |  | 221.00 | 17680.00 | 201.00 | 16080.00 | 16080.00 | Sterling and Wilson Pvt. Ltd
29.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required. Upto 35 sq. mm (clamped with 1mm thick saddle) | 60.00 | Mtr |  | 141.00 | 8460.00 | 104.00 | 6240.00 | 6240.00 | Sterling and Wilson Pvt. Ltd
30.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
30.01 | 3½ X 95 sq. mm (45mm) | 4.00 | Each |  | 2388.00 | 9552.00 | 2048.00 | 8192.00 | 8192.00 | Sterling and Wilson Pvt. Ltd
30.02 | 3½ X 150 sq. mm (50mm) | 2.00 | Each |  | 2522.00 | 5044.00 | 2836.00 | 5672.00 | 5044.00 | Voltas Ltd
30.03 | 4 X 16 sq. mm (28mm) | 4.00 | Each |  | 1476.00 | 5904.00 | 1193.00 | 4772.00 | 4772.00 | Sterling and Wilson Pvt. Ltd
31.00 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray (Galvanisation thickness not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc. as required. 225 mm width X 50 mm depth X 1.6 mm thickness | 60.00 | Mtr |  | 1315.00 | 78900.00 | 1611.00 | 96660.00 | 78900.00 | Voltas Ltd
32.00 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray "bends" (galvanisation not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc. as required. 225 mm width X 50 mm depth X 1.6 mm thickness | 15.00 | Each |  | 2994.00 | 44910.00 | 2017.00 | 30255.00 | 30255.00 | Sterling and Wilson Pvt. Ltd
33.00 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray "Tee" (galvanisation not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc. as required. 225 mm width X 50 mm depth X 1.6 mm thickness | 6.00 | Each |  | 3924.00 | 23544.00 | 2017.00 | 12102.00 | 12102.00 | Sterling and Wilson Pvt. Ltd
34.00 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray "Cross member"(galvanisation not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc as required. 225 mm width X 50 mm depth X 1.6 mm thickness | 6.00 | Each |  | 3659.00 | 21954.00 | 2643.00 | 15858.00 | 15858.00 | Sterling and Wilson Pvt. Ltd
35.00 | Providing, laying, testing & commissioning of 'B' class heavy duty G.I. pipe conforming to IS 1239 including welding, fittings like elbows, tees, flanges, tapers, nuts, bolts, gaskets etc. and fixing the pipe on the wall/ceiling with suitable clamp/support frame and painting with two or more coats of synthetic enamel paint of required shade complete as required : 100 mm | 80.00 | Mtr |  | 2335.00 | 186800.00 | 3266.00 | 261280.00 | 186800.00 | Voltas Ltd
36.00 | Supply of PVC/XLPE insulated and PVC sheathed / XLPE of 1.1 KV grade following type armoured power cable conforming to IS 7098 part-I complete as required.
36.01 | 4 Core x 6 sqmm. copper conductor | 100.00 | Mtr |  | 421.00 | 42100.00 | 689.00 | 68900.00 | 42100.00 | Voltas Ltd
36.02 | 4 Core x 16 sqmm. Aluminum conductor | 70.00 | Mtr |  | 202.00 | 14140.00 | 343.00 | 24010.00 | 14140.00 | Voltas Ltd
36.03 | 3.5 Core x 95 sqmm. Aluminum conductor | 70.00 | Mtr |  | 679.00 | 47530.00 | 1154.00 | 80780.00 | 47530.00 | Voltas Ltd
36.04 | 3.5 Core x 150 sqmm. Aluminum conductor | 250.00 | Mtr |  | 981.00 | 245250.00 | 1670.00 | 417500.00 | 245250.00 | Voltas Ltd
37.00 | Supply and fixing of 450mm swep metal blade exhaust fan suitable for operation on 230 V, 50 Hz, Single phase, A.C supply in the existing opening including connections, testing, commissioning etc. as required | 8.00 | Each |  | 8761.00 | 70088.00 | 8702.00 | 69616.00 | 69616.00 | Sterling and Wilson Pvt. Ltd
38.00 | Supply and fixing of 600mm swep metal blade metal body industrial wall fan suitable for 240V, 1-ph 50HZ AC supply on wall including connections, testing, commissioning etc. complete as required. | 2.00 | Each |  | 14053.00 | 28106.00 | 20657.00 | 41314.00 | 28106.00 | Voltas Ltd
39.00 | Supply installation testing commissioning of 4 ft long Surface mounting LED batten 6500K, efficacy >100 lumen/watt, power factor >0.95 , IP20, CRI >80, burning hours>50000 hours, 85% driver efficiency, THD<10% with 05 years warranty certificate from OEM, made out of CRCA / extruded aluminum/PDC aluminum, mounting clamps, fixing arrangement, LEDs driver, complying with LM 80 & LM 79 etc. complete as required. | 6.00 | Each |  | 2234.00 | 13404.00 | 1903.00 | 11418.00 | 11418.00 | Sterling and Wilson Pvt. Ltd
40.00 | Supply, installation, testing and commissioning of 80W LED streel light 5700K, efficacy >110 lumen/watt, power factor>0.95 , IP65, CRI >70, burning hours>50000 hours, 85% driver efficiency, THD<10% with 05 years warranty certificate from OEM, made out of CRCA / extruded aluminum/ PDC aluminum, heat sink, mounting clamps, fixing arrangement, LEDs driver, surge protection system, cpmlying with LM 80 & LM 79 etc. complete as required. | 16.00 | Each |  | 8545.00 | 136720.00 | 8237.00 | 131792.00 | 131792.00 | Sterling and Wilson Pvt. Ltd
41.00 | Supply and fixing wall mounting type metal bracket for streetlight including clamps, nuts, bolts, screws, making holes on wall etc. complete as required at suitable locations as directed by Engineer-In-Charge. | 16.00 | Each |  | 1409.00 | 22544.00 | 1715.00 | 27440.00 | 22544.00 | Voltas Ltd
42.00 | Supplying, installation, testing and commissioning of electric driven positive suction pump consisting of following complete in all respects, as required :(a) Horizontal type, multistage, centrifugal pump of cast iron body and bronze impeller with stainless steel shaft, mechanical seal (b) Suitable HP squirell cage induction motor TEFC type suitable for operation on 415 volts, 3 phase 50 Hz AC supply with IP 55 class of protection for enclosure, horizontal foot mounted type with Class-'F' insulation (c) M.S.fabricated Common base plate, coupling, coupling guard, foundation bolts etc. as required. (d) Suitable cement concrete foundation duly plastered and with anti vibration pads (e) Rain shed with enclosure for outdoor use (f) interconnection with suction and discharge pipe line with reducer, flanges, gasket, nuts, bolts etc. Range: 30m-45m head range and 17-10 lps capacity | 2.00 | Each |  | 180693.00 | 361386.00 | 69803.00 | 139606.00 | 139606.00 | Sterling and Wilson Pvt. Ltd
43.00 | Supply installation testing commissioning of star-delta starter suitable for up to 12.5 HP pump-motor set including drilling on wall, screws, nuts, bolts, connection with proper lugs etc. and ensuring successful operation of the pump motor set associated with the starter complete as required. | 2.00 | Each |  | 44305.00 | 88610.00 | 33483.00 | 66966.00 | 66966.00 | Sterling and Wilson Pvt. Ltd
44.00 | Supply installation testing commissioning of 2HP 1-ph 230V 50Hz dewatering submerssible pump including connection, discharge pipe line of minimum 6 mtr long of suitable size etc. complete as required. Make: KSB, Model: AMAPORTER503 SE or equivalent. | 2.00 | Each |  | 65087.00 | 130174.00 | 81281.00 | 162562.00 | 130174.00 | Voltas Ltd
45.00 | Excavation of hard rock including getting out the excavated soil and disposal of excavated soil as directed within a lead of 50 metres. | 5.00 | Cum |  | 1610.00 | 8050.00 | 4359.00 | 21795.00 | 8050.00 | Voltas Ltd
46.00 | Excavation of soft soil including getting out the excavated soil and disposal of surplus excavated soil as directed within a lead of 50 metres. | 5.00 | Cum |  | 939.00 | 4695.00 | 3963.00 | 19815.00 | 4695.00 | Voltas Ltd
| Total in Figures |  |  |  |  | 11111111.00 |  | 11690883.00
Lowest Amount Quoted BY: Voltas Ltd(11111111.00)

## BOQ Summary
BOQ Summary Details Tender Title: Associate electrical works for operationalization of new terminal building, Sub Head Relocation of fire pump room. Tender ID: 2022_AAI_135783_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Voltas Ltd | 11111111.00 | L1
| 2 | Sterling and Wilson Pvt. Ltd | 11690883.00 | L2