## BoQ1
Government eProcurement System Created By: THIRUNAVUKKARASU M Created Date/Time: 13-Jan-2023 03:58 PM Tender Title: SITC of DG Sets, Internal and External Electrification work for DVOR Building of VSI Airport Port Blair Tender ID: 2022_AAI_137004_1
Tender Inviting Authority: The Assistant General Manager (Engg-Elect), AAI, VSI Airport, Port Blair.
Name of Work: SITC of DG sets,Internal & External electrical work for DVOR Building of VSI Airport,Port Blair
Contract No: 2022_AAI_137004_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | SARASWAT ENGINEERING SERVICES(GSTN-27AAZFS6239C1ZO) |  | Mona Generator Services Pvt. Ltd.(GSTN-07AAFCM4263P1ZZ) |  | Prasur Electricals and Engineering Co.(GSTN-NA) |  | ICON AGENCIES(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply Installation Testing Commissioning of "Silent Type" water Cooled, Diesel Generating Set along with having Prime mover power rating of 62.5 KVA at 0.8 lagging power factor, 415 volts, 1500 RPM, 3 phase system, as per ISO 8528 and consisting of the following: (a) Diesel Engine:electronic governor, Liquid cooled, electric start, of suitable BHP at 1500 RPM suitable for above output of alternator at 40 Degree C at 1000 Meter MSL and capable of taking 10% over loading for one hour after 12 hours of continuous operation. The engine will be fitted complete with all the required accessories. (b) Alternator: Synchronous alternator rated for 62.5 KVA, 415 volts at 1500 RPM, 3 phase 50 Hz, AC supply with 0.8 lagging power factor at 40 Degree C at 1000 Meter MSL.The alternator will be fitted complete with all the required accessories. c) Fuel Tank : OEM recommended fuel tank shall be considered (d) Exhaust System: OEM recommended Exhaust shall be considered (e) Starting System: OEM recommended battery specification and arrangement for initial excitation complete with suitable nos. of batteries with MS battery stand etc. (f) Acoustic Enclosure : Acoustic and weather proof enclosure with arrangement for fresh air intake for cooling of the engine & alternator, extraction, discharging hot air in to the atmosphere as per OEM specifications. (g)AMF panel along with necessary control, metering and protection systems suitable for 62.5 KVA DG set etc as required as per Technical specification. (h)The work should be as per Central Electrical Authority / Pollution control board standards. | 2.00 | Each | 100.00 | 873220.00 | 1746440.00 | 914400.00 | 1828800.00 | 875000.00 | 1750000.00 | 975000.00 | 1950000.00 | 1746440.00 | SARASWAT ENGINEERING SERVICES
2.00 | Design, fabrication, supply, installation, testing and commissioning of vermin, dust proof, front operated cubicle type floor mounted, indoor type LT panel board made out of 2 mm thick CRCA sheet duly rust inhibited, stove enameled, powder coated paint, fully compartmentalized complete with double hinged front door with lockable arrangement etc including necessary iron channel stand, control wiring etc. and having following accessories(PTTA panel) INCOMER 4 Pole, 250 amp, 36KA, 415 volts, 50Hz, AC, Moulded Case Circuit Breaker with extended terminals and adjustable Thermal setting With suitable accessories (02 Nos.). With suitabl rating of surge protection device & Digital voltmeter & ammeter metering device, LED TYPE INDICATION LAMPS (RYB) with protection MCB Bus coupler 4 Pole, 250 amp, 36KA, 415 volts, 50Hz, AC, Moulded Case Circuit Breaker with extended terminals and adjustable Thermal setting With suitable accessories OUTGOING 4 Pole, 250 amp, 36KA, 415 volts, 50Hz, AC, Moulded Case Circuit Breaker adjustable Thermal setting (03 Nos.). 4 Pole, 125 amp, 25KA, 415 volts, 50Hz, AC, Moulded Case Circuit Breaker adjustable Thermal setting (03 Nos.). METERING Digital Ammeter 0-125 A, three phase with suitable CTs, selector switch and protection MCB LED TYPE INDICATION LAMPS (RYB) with protection MCB | 2.00 | Each | 100.00 | 640562.00 | 1281124.00 | 375000.00 | 750000.00 | 500000.00 | 1000000.00 | 175000.00 | 350000.00 | 350000.00 | ICON AGENCIES
3.00 | Design, fabrication, supply, installation, testing and commissioning of vermin, dust proof, front operated cubicle type floor mounted, indoor type LT panel board made out of 2 mm thick CRCA sheet duly rust inhibited, stove enameled, powder coated paint, fully compartmentalized complete with double hinged front door with lockable arrangement etc including necessary iron channel stand, control wiring etc. and having following accessories(PTTA panel) INCOMER 4 Pole, 250 amp, 36KA, 415 volts, 50Hz, AC, Moulded Case Circuit Breaker with extended terminals and adjustable Thermal setting With suitable accessories (03Nos.). With Digital voltmeter & ammeter metering device, LED TYPE INDICATION LAMPS (RYB) with protection MCB & necessery electrical and mechnical(key arrangement) interlock OUTGOING 4 Pole, 250 amp, 36KA, 415 volts, 50Hz, AC, Moulded Case Circuit Breaker with extended terminals and adjustable Thermal setting With suitable accessories (02 Nos.). , LED TYPE INDICATION LAMPS (RYB) with protection MCB & necessery electrical and mechnical(key arrangement) interlock METERING Digital Voltmeter 0-500V, three phase with selector switch and protection MCB - 02 Set. Digital Ammeter 0-100 A, three phase with suitable CTs, selector switch and protection MCB - 02 No. LED TYPE INDICATION LAMPS (RYB) with protection MCB - 2 set (1 set = 03 Lamp). | 1.00 | Each | 10.00 | 448003.00 | 448003.00 | 302000.00 | 302000.00 | 345000.00 | 345000.00 | 240000.00 | 240000.00 | 240000.00 | ICON AGENCIES
4.00 | Supplying and fixing following way, Vertical type three pole and neutral, sheet steel, MCB distribution board, 415 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCCB/MCB/RCCB/Isolator)(VTPN DB) 6way (8 + 18), Double door | 1.00 | Each | 10.00 | 13504.00 | 13504.00 | 5289.00 | 5289.00 | 8000.00 | 8000.00 | 37000.00 | 37000.00 | 5289.00 | Mona Generator Services Pvt. Ltd.
5.00 | Supplying and fixing folowing amps rating, 240 / 415 volts, C - curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.
5.10 | Single pole ( 6 - 32 A) | 18.00 | Each | 10.00 | 338.00 | 6084.00 | 170.00 | 3060.00 | 191.00 | 3438.00 | 205.00 | 3690.00 | 3060.00 | Mona Generator Services Pvt. Ltd.
5.20 | Triple Pole 63A | 1.00 | Each | 10.00 | 8265.00 | 8265.00 | 1250.00 | 1250.00 | 1130.00 | 1130.00 | 2200.00 | 2200.00 | 1130.00 | Prasur Electricals and Engineering Co.
6.00 | Supplying and fixing following rating, four pole, (three phase and neutral), 415 volts, residual current circuit breaker (RCCB), having a sensitivity current 30 mA in the existing MCB DB complete with connections, testing and commissioning etc. as required 63 A | 1.00 | Each | 10.00 | 4556.00 | 4556.00 | 2622.00 | 2622.00 | 2500.00 | 2500.00 | 3600.00 | 3600.00 | 2500.00 | Prasur Electricals and Engineering Co.
7.00 | Supply of following sizes of XLPE insulated PVC sheathed, armoured, aluminium conductor cable of 1.1KV grade as per IS 7098: 1988 part-I asamended up to date complete etc., as required.
7.10 | 3.5 X 70 Sq.mm | 500.00 | Mtr | 10.00 | 451.00 | 225500.00 | 307.00 | 153500.00 | 416.00 | 208000.00 | 650.00 | 325000.00 | 153500.00 | Mona Generator Services Pvt. Ltd.
7.20 | 3.5x120 Sq mm | 120.00 | Mtr | 10.00 | 716.00 | 85920.00 | 487.00 | 58440.00 | 668.00 | 80160.00 | 980.00 | 117600.00 | 58440.00 | Mona Generator Services Pvt. Ltd.
8.00 | Supply & laying of following size Double Walled Corrugated high density polyethylene pipe having corrugation on the outer wall confirming to IS 14930 part-II and ISI marked complete with necessary fittings such as couplers, bends and end caps etc., for protection of 1.1KV grade under ground cable directly in ground complete etc as required. 110 mm dia | 600.00 | Mtr | 10.00 | 328.00 | 196800.00 | 229.00 | 137400.00 | 500.00 | 300000.00 | 180.00 | 108000.00 | 108000.00 | ICON AGENCIES
9.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL pipe as required.
9.10 | Above 95 sq mm & Up to 185 sq mm | 500.00 | Mtr | 10.00 | 99.00 | 49500.00 | 60.00 | 30000.00 | 120.00 | 60000.00 | 40.00 | 20000.00 | 20000.00 | ICON AGENCIES
9.20 | Above 35 sq mm & Up to 95 sq mm | 120.00 | Mtr | 10.00 | 86.00 | 10320.00 | 47.00 | 5640.00 | 80.00 | 9600.00 | 50.00 | 6000.00 | 5640.00 | Mona Generator Services Pvt. Ltd.
10.00 | Supplying and making end termination with brass compression gland and Aluminum lugs for following size of PVC insulated and PVC sheathed / XLPE copper conductor cable of 1.1 kV grade as required.
10.10 | 3.5x70 Sq.mm | 6.00 | Set | 10.00 | 716.00 | 4296.00 | 810.00 | 4860.00 | 400.00 | 2400.00 | 60.00 | 360.00 | 360.00 | ICON AGENCIES
10.20 | 3.5x120 Sq mm | 2.00 | Set | 10.00 | 907.00 | 1814.00 | 1020.00 | 2040.00 | 600.00 | 1200.00 | 80.00 | 160.00 | 160.00 | ICON AGENCIES
11.00 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 4.00 | Job | 10.00 | 18995.00 | 75980.00 | 7500.00 | 30000.00 | 8000.00 | 32000.00 | 8100.00 | 32400.00 | 30000.00 | Mona Generator Services Pvt. Ltd.
12.00 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 40.00 | Mtr | 10.00 | 1002.00 | 40080.00 | 455.00 | 18200.00 | 900.00 | 36000.00 | 890.00 | 35600.00 | 18200.00 | Mona Generator Services Pvt. Ltd.
13.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | 20.00 | Mtr | 10.00 | 231.00 | 4620.00 | 130.00 | 2600.00 | 250.00 | 5000.00 | 210.00 | 4200.00 | 2600.00 | Mona Generator Services Pvt. Ltd.
14.00 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 4.00 | Job | 10.00 | 25084.00 | 100336.00 | 12750.00 | 51000.00 | 25000.00 | 100000.00 | 14100.00 | 56400.00 | 51000.00 | Mona Generator Services Pvt. Ltd.
15.00 | Providing and fixing 25 mm X 5 mm copper strip in 40 mm dia G.I. pipe from earth electrode including connection with brass nut, bolt, spring, washer excavation and re-filling etc. as required. | 40.00 | Mtr | 10.00 | 2219.00 | 88760.00 | 1185.00 | 47400.00 | 2000.00 | 80000.00 | 1400.00 | 56000.00 | 47400.00 | Mona Generator Services Pvt. Ltd.
16.00 | Providing and fixing 25 mm X 5 mm copper strip on surface or in recess for connections etc. as required. | 20.00 | Mtr | 10.00 | 1730.00 | 34600.00 | 860.00 | 17200.00 | 1200.00 | 24000.00 | 900.00 | 18000.00 | 17200.00 | Mona Generator Services Pvt. Ltd.
17.00 | SITC of Surge protection device Type 2 ( Class C), 4 Mode, MOV type suitable for 8/ 20µs surge, Voltage Protection level Up < 1.5kV, Operating Temperature -40 deg 'c' - +80 deg 'C', Connected Between 3Nos. phase to neutral and 1Nos. neutral to earth with discharge Current Imax. ≥ 40KA Per mode & In ≤ 20kA per Mode. SPD with inbuilt fuses of 100kA breaking capacity. For connecting SPD minimum 10sqmm copper wire must be used & length of connecting leads shall not be more than 500mm for per mode connection including necessary power coated MS enclosure along with all necessary accessories. The SPD shall compliance with IEC 61643-11. | 2.00 | Each | 10.00 | 17627.00 | 35254.00 | 5200.00 | 10400.00 | 65000.00 | 130000.00 | 1200.00 | 2400.00 | 2400.00 | ICON AGENCIES
18.00 | Supply of Gas Suppression System consisting of Cylinder PESO Approved (M/s. Everest Kanto Cylinder Limited and equivalent make), complete with UL / VDS / PESO approved valve assembly (M/s. Tyco Fire Protection LP and equivalent make) and arrangement for supervisory switch connection for monitoring cylinder pressure, a pressure gauge with a safety burst disc, electronic control head / solenoid, pressure operated control, head, flexible hose, strap, NRV, Pressure Switch and a safety cap, required nos. of nozzles (UL / VDS listed), piping, manifold, including smoke detector,FRLS Cable & control panel etc. complete as reqd. with autodialler system. Gas (Quantity would be as per the volume given below and as per the UL / VDS certification) CLEAN AGENT (FK-5-1-12) / Inert Gas with Zero Ozone Depletion Potential (ODP), has appearance / colourless gas and odourless.
18.10 | for the room size of 5 m x 7.5m and 3 m height | 1.00 | No. | 10.00 | 589691.00 | 589691.00 | 800000.00 | 800000.00 | 1270000.00 | 1270000.00 | 750000.00 | 750000.00 | 589691.00 | SARASWAT ENGINEERING SERVICES
18.20 | for the room size of 5 m x 5 m and 3 m height | 1.00 | No. | 10.00 | 563376.00 | 563376.00 | 720000.00 | 720000.00 | 1075000.00 | 1075000.00 | 632000.00 | 632000.00 | 563376.00 | SARASWAT ENGINEERING SERVICES
18.30 | for the room size of 5 m x 4 m and 3 m height | 1.00 | No. | 10.00 | 537060.00 | 537060.00 | 620000.00 | 620000.00 | 975000.00 | 975000.00 | 610000.00 | 610000.00 | 537060.00 | SARASWAT ENGINEERING SERVICES
19.00 | Existing 02 nos. DG set to be dismentaled at DVOR site in Port Blair and shifted from DVOR site to Port Blair Airport. | 1.00 | Job | 10.00 | 30444.00 | 30444.00 | 30000.00 | 30000.00 | 30000.00 | 30000.00 | 80000.00 | 80000.00 | 30000.00 | Prasur Electricals and Engineering Co., Mona Generator Services Pvt. Ltd.
20.00 | SITC of 30 watt LED fixture suitable for outdoor applications with heat sink, driver & all accessories etc as required operating on 140 v -270 volts & 50 Hz, CRI>70% & IP 65 (minimum) for complete fixture as per technical specifications. Driver shall be with THD less than 10% & Constant Current Constant Voltage(CCCV) and power factor greater than 0.95. | 6.00 | Nos. | 10.00 | 2217.00 | 13302.00 | 2150.00 | 12900.00 | 2000.00 | 12000.00 | 3100.00 | 18600.00 | 12000.00 | Prasur Electricals and Engineering Co.
21.00 | Supply of 5 star rated energy efficient, 1.5 TR, invertor type, single phase, wall mounting type split Air conditioner unit, consisting of indoor unit, out door unit, cordless remote control, refrigerant gas, standard length of refrigerant pipe, drain pipe, power cable etc. and suitable for operation on 230 V, 50 HZ, single phase AC supply etc. as per OEM standard and complete as required as per technical specifications. | 6.00 | Nos. | 10.00 | 45809.00 | 274854.00 | 42000.00 | 252000.00 | 65000.00 | 390000.00 | 56000.00 | 336000.00 | 252000.00 | Mona Generator Services Pvt. Ltd.
22.00 | Installation testing and commissioning of 1.5 TR Single phase Split AC units including fixing the condenser unit by providing and fixing suitable dimension of angle iron stand duly painted and fixing of evaporator unit including fixing of liquid & suction line, wiring between indoor and outdoor units, drain piping, insulation etc. supplied with unit, first charge of refrigerant etc. complete as required as per site conditions | 6.00 | Job | 10.00 | 6618.00 | 39708.00 | 3000.00 | 18000.00 | 7500.00 | 45000.00 | 3100.00 | 18600.00 | 18000.00 | Mona Generator Services Pvt. Ltd.
23.00 | SITC of wall mounted, automatic voltage stabilizer suitable for 1.5 TR split A/C with complete accessories and protection systems having output provision of 1ph 240V+ 2%, 50Hz with input supply of 170 to 270V with protection fuse/MCB etc., as required. | 6.00 | Nos. | 10.00 | 4753.00 | 28518.00 | 3200.00 | 19200.00 | 5000.00 | 30000.00 | 4100.00 | 24600.00 | 19200.00 | Mona Generator Services Pvt. Ltd.
24.00 | SITC of Timers for A.C. of 1.5/2.0 TR Capacity (5 Star Rating) up to 4 Hours automatic changing operation complete as required. | 3.00 | Nos. | 10.00 | 3798.00 | 11394.00 | 6500.00 | 19500.00 | 7500.00 | 22500.00 | 2400.00 | 7200.00 | 7200.00 | ICON AGENCIES
25.00 | Supplying and fixing 20 A, 240 V, SPN Industrial type socket outlet, with 2 pole and earth, metal enclosed plug top alongwith 20 A "C" curve, SP, MCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning etc. as required. | 6.00 | Nos. | 10.00 | 2401.00 | 14406.00 | 1620.00 | 9720.00 | 1800.00 | 10800.00 | 860.00 | 5160.00 | 5160.00 | ICON AGENCIES
26.00 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed PVC conduit, with modular switch, modular plate, suitable plastic box and earthing the point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable etc. as required. Group C | 6.00 | Nos. | 10.00 | 1082.00 | 6492.00 | 1480.00 | 8880.00 | 1200.00 | 7200.00 | 890.00 | 5340.00 | 5340.00 | ICON AGENCIES
27.00 | Wiring for light/ power plug with 2X4 sq. mm FRLS PVC insulated copper conductor single core cable in surface/ recessed medium class PVC conduit alongwith 1 No 4 sq. mm FRLS PVC insulated copper conductor single core cable for loop earthing as required. | 6.00 | Nos. | 10.00 | 1172.00 | 7032.00 | 1200.00 | 7200.00 | 1300.00 | 7800.00 | 1100.00 | 6600.00 | 6600.00 | ICON AGENCIES
28.00 | Supplying and fixing suitable size Plastic surface box with modular plate and cover in front on surface or in recess, including providing and fixing 5 pin 5/6 & 15/16 A modular socket outlet and 15/16 A modular switch, connections etc. as required. | 3.00 | Nos. | 10.00 | 915.00 | 2745.00 | 550.00 | 1650.00 | 800.00 | 2400.00 | 450.00 | 1350.00 | 1350.00 | ICON AGENCIES
29.00 | Supplying and fixing suitable size Plastic surface box with modular plate and cover in front on surface or in recess, including providing and fixing 5 pin 5/6 & 15/16 A modular socket outlet and 15/16 A modular switch, connections etc. as required. | 3.00 | Nos. | 10.00 | 915.00 | 2745.00 | 550.00 | 1650.00 | 850.00 | 2550.00 | 450.00 | 1350.00 | 1350.00 | ICON AGENCIES
30.00 | Supplying and fixing of following sizes of medium class PVC conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required. 25 mm dia | 80.00 | Meter | 10.00 | 107.00 | 8560.00 | 90.00 | 7200.00 | 70.00 | 5600.00 | 35.00 | 2800.00 | 2800.00 | ICON AGENCIES
31.00 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required.
31.10 | 3 x 2.5 sq. mm | 30.00 | Meter | 10.00 | 139.00 | 4170.00 | 84.00 | 2520.00 | 80.00 | 2400.00 | 180.00 | 5400.00 | 2400.00 | Prasur Electricals and Engineering Co.
31.20 | 3 x 4 sq. mm | 30.00 | Meter | 10.00 | 200.00 | 6000.00 | 136.00 | 4080.00 | 120.00 | 3600.00 | 220.00 | 6600.00 | 3600.00 | Prasur Electricals and Engineering Co.
32.00 | Supply & installation of Wall bracket fan of 400 mm sweep,1350 RPM suitable for operation on 230 V, 50 Hz A.C. supply complete with pull cord control for speed & oscillation on & off , copper wound motor, blades, outer cage for protection, capacitor etc. complete as required | 2.00 | Nos. | 10.00 | 4752.00 | 9504.00 | 2800.00 | 5600.00 | 3500.00 | 7000.00 | 2900.00 | 5800.00 | 5600.00 | Mona Generator Services Pvt. Ltd.
33.00 | SITC of 15 watt LED fixture suitable for indoor applications with heat sink, driver & all accessories etc as required for operation and rating feature as per Technical specification | 6.00 | Nos. | 10.00 | 1860.00 | 11160.00 | 165.00 | 990.00 | 1740.00 | 10440.00 | 1100.00 | 6600.00 | 990.00 | Mona Generator Services Pvt. Ltd.
34.00 | Providing and laying in position ready mixed or site batched design mix cement concrete for reinforced cement concrete work; using coarse aggregate and fine aggregate derived from natural sources, Portland Pozzolana / Ordinary Portland /Portland Slag cement, admixtures in recommended proportions as per IS: 9103 to accelerate / retard setting of concrete, to improve durability and workability without impairing strength; including pumping of concrete to site of laying, curing, carriage for all leads; but excluding the cost of centering, shuttering, finishing and reinforcement as per direction of the engineer-in-charge; for the following grades of concrete. Note: Extra cement up to 10% of the minimum specified cement content in design mix shall be payable separately. In case the cement content in design mix is more than 110% of the specified minimum cement content, the contractor shall have discretion to either re-design the mix or bear the cost of extra cement. All works upto plinth level Concrete of M25 grade with minimum cementcontent of 330 kg /cum | 10.00 | Cum | 10.00 | 19193.00 | 191930.00 | 10300.00 | 103000.00 | 10000.00 | 100000.00 | 8000.00 | 80000.00 | 80000.00 | ICON AGENCIES
35.00 | SITC of AMF panel along with necessary metering and protection systems suitable for 62.5 KVA DG set etc as required as per Technical specification | 1.00 | No. | 10.00 | 107172.00 | 107172.00 | 150006.00 | 150006.00 | 125000.00 | 125000.00 | 195000.00 | 195000.00 | 107172.00 | SARASWAT ENGINEERING SERVICES
| Total in Figures |  |  |  |  | 6922019.00 |  | 6255797.00 |  | 8312718.00 |  | 6167610.00
Lowest Amount Quoted BY: ICON AGENCIES(6167610.00)

## BOQ Summary
BOQ Summary Details Tender Title: SITC of DG Sets, Internal and External Electrification work for DVOR Building of VSI Airport Port Blair Tender ID: 2022_AAI_137004_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | ICON AGENCIES | 6167610.00 | L1
| 2 | Mona Generator Services Pvt. Ltd. | 6255797.00 | L2
| 3 | SARASWAT ENGINEERING SERVICES | 6922019.00 | L3
| 4 | Prasur Electricals and Engineering Co. | 8312718.00 | L4