## BoQ1
Government eProcurement System Created By: SYED TANWEER ASHRAF Created Date/Time: 25-Jan-2023 11:13 AM Tender Title: SITC of 50 KLD FRP Underground Packaged Sewage Treatment Plant including Annual Operation and Comprehensive Maintenance for 05 Years at Gaya Airport, Gaya Bihar Tender ID: 2022_AAI_137455_1
Tender Inviting Authority: <AGM ( Engg. Elect), AAI, Gaya Airport, Gaya>
Name of Work: <SITC of 50 KLD FRP Underground Packaged Sewage Treatment Plant including Annual Operation & Comprehensive Maintenance for 05 Years at Gaya Airport, Gaya (Bihar).>
Contract No: <0631-2210043>
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | chemeco Engineers(GSTN-09AAGFC1336D1ZV) |  | CLEAR ION EXPERTS PVT LTD(GSTN-06AAACC5410H1Z6) |  | OM JYOTI ENGINEERING ENTERPRISES(GSTN-NA) |  | greenagersenviro solutions and services pvt. ltd.(GSTN-NA) |  | Unicare Technologies Pvt Ltd(GSTN-NA) |  | BLUEWATERTECH SERVICES PRIVATE LIMITED(GSTN-NA) |  | PALEO CRYSTAL ENVIRO TECHNOLOGIES PVT LTD(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Design , supply, Installation, Testing & Commissioning of underground FRP tank based Package type prefabricated Moving Bed Bio Reactor Based Sewage Treatment Plant of 50 KLD capacity System. The FRP Tank should be suitable for installation below ground . Semi treated water from settling / Sedimentation zone shall be tertiary treated using a pressure sand filter, Activated Carbon Filter (ACF). System must be designed to meet the outlet parameters given below. The system must be provided with UV based disinfection at the final outlet. INLET EFFLUENT CHARACTERSTICS pH - 6.5 –8.5 BOD - 300-350Mg/L S. Solids - 400-500 Mg/L COD - 500-600 Mg/L Oil & Grease - 40-50 Mg / L DISCHARGE EFFLUENT CHARACTERSTICS AFTER TREATMENT pH - 6.0 – 9.0 BOD - Less than 10 Mg/L S. Solids - Less than 20 Mg/L COD - Less than 250 Mg/L Oil & Grease - Less than 10 Mg/L FRP Package type Sewage treatment plant shall include the following items: RCC Chamber with S.S Bar screen (Size shall be as per OEM) RCC Chamber with S.S Bar screen (Size shall be as per OEM) Oil & Grease Trap including RCC Chamber (Size shall be as per OEM) FRP underground Tank with different zone as below. (Complying Relevant IS/ International standard if any). Solid separation Zone Aeration zone with MBBR Reactors Sedimentation zone Raw sewage Pumps (1 working and 1 standby)- Capacity shall be as per OEM & Make shall be as per list of approved make. HDPE pipeline of suitable diameter as per OEM for raw sewage from septic tank to inlet of STP- 150m (approx) Air Blowers (1 working and 1 standby) - Capacity shall be as per OEM & Make shall be as per list of approved make. Filter feed Pumps (1 working and 1 standby)- Capacity shall be as per OEM & Make shall be as per list of approved make. Piping, valves etc. Tertiary treatment plant with MGF filter and Activated carbon filter with FRP Tank. Irrigation/ Final treated Water tank (FRP Tank capacity 10KL). Dedicated Irrigation / Final treated Water Transfer Pumps (Capacity 3 cum per hour with 30 mtr. Head). Electrical Panel as per OEM, Cabling and 2 Nos. GI Plate Earthing. i) Electrical cable from STP electrical panel to all STP equipments including making their connnection, termination etc shall also be included in quoted price. Note: ii) Total capacity of FRP underground tank shall be minimum 30KL (which shall include solid separation zone+ aeration zone + Sedimentation zone) and thickness of FRP underground tank shall be 20mm minimum. Semi treated water zone may be constructed in main FRP Tank or separate FRP Tank of capacity 5KL can be provided. iii) Contractor shall ensure submission of detailed GA drawings (Plan & Section), P&I diagram, schematic diagram for the above system including additional component if so required for the complete working of the STP before procurement of material for approval from Engineer-In-charge. Associated Civil works : A) EXCAVATION of soil, Construction of PCC, RCC, Brick work for mounting FRP Package type STP above & below ground, Foundation for Panel, HDPE tank, Air Blower, pumps etc. Complete as required. B)Construction of Bar screen chamber, Oil Grease trap etc complete as required already mentioned in Item No.01. | 1.00 | Job | 263.00 | 3557000.00 | 3557000.00 | 3600000.00 | 3600000.00 | 2620000.00 | 2620000.00 | 3000000.00 | 3000000.00 | 2799999.00 | 2799999.00 | 3000000.00 | 3000000.00 | 3492000.00 | 3492000.00 | 2620000.00 | OM JYOTI ENGINEERING ENTERPRISES
2.00 | Construction of Plant/Control Room of minimum size of 6 x 4 x 4 Mtr with good engineering practice and as per CPWD / IS specifications using Brick work, Cement Concrete for walls & Concrete Cement floor, suitable size reinforcement with galvanized iron profile roofing of minimim 0.5 mm thickness, complete with plastering , painting etc. as required. Providing 1 no. Aluminium Door & 2 nos Windows also in scope of contractor. Electrical works inside the control room i/c providing & fixing 4 Nos of LED type 20 W tube light fixture complete with all accesories & drivers etc including wiring, supply & installation i/c wiring of 02 number of 1200 mm sweep ceiling fans with regulators, supply, installation i/c wiring of 1 No. of 450 mm sweep exhaust fan including making holes to suit the size (all items should be as per approved makes) & providing point wiring & switch and sockets as per site requirement etc complete as directed by the Engineer-in-charge are also in scope of Contractor. | 1.00 | Job | 263.00 | 543000.00 | 543000.00 | 700000.00 | 700000.00 | 575000.00 | 575000.00 | 280000.00 | 280000.00 | 100000.00 | 100000.00 | 100000.00 | 100000.00 | 574000.00 | 574000.00 | 100000.00 | Unicare Technologies Pvt Ltd, BLUEWATERTECH SERVICES PRIVATE LIMITED
3.00 | Providing and fixing HDPE pipes, HDPE & brass threaded fittings for treated water reuse. This includes jointing of pipes & fittings, trenching, refilling & testing of joints complete as per direction of Engineer in Charge.
3.10 | 63 mm dia | 500.00 | mtr | 263.00 | 450.00 | 225000.00 | 450.00 | 225000.00 | 160.00 | 80000.00 | 1100.00 | 550000.00 | 1111.00 | 555500.00 | 300.00 | 150000.00 | 599.00 | 299500.00 | 80000.00 | OM JYOTI ENGINEERING ENTERPRISES
3.20 | 25 mm dia | 100.00 | mtr | 263.00 | 250.00 | 25000.00 | 900.00 | 90000.00 | 120.00 | 12000.00 | 500.00 | 50000.00 | 999.00 | 99900.00 | 225.00 | 22500.00 | 146.00 | 14600.00 | 12000.00 | OM JYOTI ENGINEERING ENTERPRISES
4.00 | Demolishing cement concrete manually/ by mechanical means including disposal of material within 50 metres lead as per direction of Engineer-in-charge. | 25.00 | Cum | 263.00 | 180.00 | 4500.00 | 500.00 | 12500.00 | 120.00 | 3000.00 | 800.00 | 20000.00 | 11000.00 | 275000.00 | 250.00 | 6250.00 | 1500.00 | 37500.00 | 3000.00 | OM JYOTI ENGINEERING ENTERPRISES
5.00 | Annual Operation and Comprehensive Maintainance Contract for five (5) Years Annual operation and all- inclusive comprehensive maintenance of 50 KLD STP inclusive of all spares & material & carrying out breakdown & the preventive maintenance complete as per direction of AAI. (After testing, commissioning and handing over to AAI)
5.10 | First year ( during Defect Liabilty Period) (17.28% of item no. 1) | 1.00 | Year | 263.00 | 614650.00 | 614650.00 | 622080.00 | 622080.00 | 452736.00 | 452736.00 | 518400.00 | 518400.00 | 483840.00 | 483840.00 | 518400.00 | 518400.00 | 603418.00 | 603418.00 | 452736.00 | OM JYOTI ENGINEERING ENTERPRISES
5.20 | Second year (after Defect Liabilty Period ) (19.01% of item no. 1) | 1.00 | Year | 263.00 | 676186.00 | 676186.00 | 684360.00 | 684360.00 | 498062.00 | 498062.00 | 570300.00 | 570300.00 | 532280.00 | 532280.00 | 570300.00 | 570300.00 | 663829.00 | 663829.00 | 498062.00 | OM JYOTI ENGINEERING ENTERPRISES
5.30 | Third Year (after Defect Liabilty Period ) (20.91% of item no. 1) | 1.00 | Year | 263.00 | 743769.00 | 743769.00 | 752760.00 | 752760.00 | 547842.00 | 547842.00 | 627300.00 | 627300.00 | 585480.00 | 585480.00 | 627300.00 | 627300.00 | 730177.00 | 730177.00 | 547842.00 | OM JYOTI ENGINEERING ENTERPRISES
5.40 | Fourth Year (after Defect Liabilty Period ) (22.05% of item no. 1) | 1.00 | Year | 263.00 | 784319.00 | 784319.00 | 793800.00 | 793800.00 | 577710.00 | 577710.00 | 661500.00 | 661500.00 | 617400.00 | 617400.00 | 661500.00 | 661500.00 | 769986.00 | 769986.00 | 577710.00 | OM JYOTI ENGINEERING ENTERPRISES
5.50 | Fifth Year (after Defect Liabilty Period ) (22.65% of item no. 1) | 1.00 | Year | 263.00 | 805661.00 | 805661.00 | 815400.00 | 815400.00 | 593430.00 | 593430.00 | 679500.00 | 679500.00 | 634200.00 | 634200.00 | 679500.00 | 679500.00 | 790938.00 | 790938.00 | 593430.00 | OM JYOTI ENGINEERING ENTERPRISES
| Total in Figures |  |  |  |  | 7979085.00 |  | 8295900.00 |  | 5959780.00 |  | 6957000.00 |  | 6683599.00 |  | 6335750.00 |  | 7975948.00
Lowest Amount Quoted BY: OM JYOTI ENGINEERING ENTERPRISES(5959780.00)

## BOQ Summary
BOQ Summary Details Tender Title: SITC of 50 KLD FRP Underground Packaged Sewage Treatment Plant including Annual Operation and Comprehensive Maintenance for 05 Years at Gaya Airport, Gaya Bihar Tender ID: 2022_AAI_137455_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | OM JYOTI ENGINEERING ENTERPRISES | 5959780.00 | L1
| 2 | BLUEWATERTECH SERVICES PRIVATE LIMITED | 6335750.00 | L2
| 3 | Unicare Technologies Pvt Ltd | 6683599.00 | L3
| 4 | greenagersenviro solutions and services pvt. ltd. | 6957000.00 | L4
| 5 | PALEO CRYSTAL ENVIRO TECHNOLOGIES PVT LTD | 7975948.00 | L5
| 6 | chemeco Engineers | 7979085.00 | L6
| 7 | CLEAR ION EXPERTS PVT LTD | 8295900.00 | L7