## BoQ1
Government eProcurement System Created By: Raj Kapoor Meena Created Date/Time: 21-Feb-2023 12:15 PM Tender Title: Provision of CAT-II Lighting System Tender ID: 2022_AAI_137821_1
Tender Inviting Authority: AIRPORTS AUTHORITY OF INDIA
Name of Work:Provision of CAT II Lighting System at Birsa Munda Airport, Ranchi
Tender ID: 2022_AAI_137821_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | AMA Private Limited(GSTN-27AAACA1016F1ZE) |  | Vardhman Airport Solutions Pvt Ltd(GSTN-07AAECN5914F1ZK) |  | JCC ENGINEERS PRIVATE LIMITED(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Design, supply and installation of Frangible & tiltable type pole/ lattice mast (base mounted/central hinge /counter balanced type ) of following height as mentioned below complying with relevant ICAO standards suitable for Cat –II Approach light system (baratte type) as per the indicative profile attached including necessary foundation as per specifications required and as per directions of the Engineer In charge.
1.01 | a)0.3-0.5 mtr. Frangible Pole | 10.00 | Each |  | 16651.00 | 166510.00 | 18825.00 | 188250.00 | 10000.00 | 100000.00 | 100000.00 | JCC ENGINEERS PRIVATE LIMITED
1.02 | b)0.5 -1.2 mtr. Frangible Pole | 30.00 | Each |  | 18013.00 | 540390.00 | 21048.00 | 631440.00 | 12000.00 | 360000.00 | 360000.00 | JCC ENGINEERS PRIVATE LIMITED
1.03 | c)2.0-2.5 mtr. Frangible Pole | 14.00 | Each |  | 37070.00 | 518980.00 | 46136.00 | 645904.00 | 30000.00 | 420000.00 | 420000.00 | JCC ENGINEERS PRIVATE LIMITED
1.04 | d)2.5-3.0 mtr. Frangible Pole | 10.00 | Each |  | 41834.00 | 418340.00 | 54921.00 | 549210.00 | 30000.00 | 300000.00 | 300000.00 | JCC ENGINEERS PRIVATE LIMITED
1.05 | e)3.0-3.5 mtr. Frangible Lattice | 1.00 | Each |  | 133513.00 | 133513.00 | 155316.00 | 155316.00 | 100000.00 | 100000.00 | 100000.00 | JCC ENGINEERS PRIVATE LIMITED
1.06 | f)3.5-4.5 mtr. Frangible Lattice | 4.00 | Each |  | 147964.00 | 591856.00 | 171971.00 | 687884.00 | 120000.00 | 480000.00 | 480000.00 | JCC ENGINEERS PRIVATE LIMITED
1.07 | g)4.5-5.5 mtr. Frangible Lattice | 2.00 | Each |  | 175189.00 | 350378.00 | 207045.00 | 414090.00 | 145000.00 | 290000.00 | 290000.00 | JCC ENGINEERS PRIVATE LIMITED
1.08 | h)6.5-8.5 mtr. Frangible Lattice | 8.00 | Each |  | 237050.00 | 1896400.00 | 277407.00 | 2219256.00 | 175000.00 | 1400000.00 | 1400000.00 | JCC ENGINEERS PRIVATE LIMITED
1.09 | i)8.5-10.5 mtr. Frangible Lattice | 15.00 | Each |  | 291528.00 | 4372920.00 | 343110.00 | 5146650.00 | 225000.00 | 3375000.00 | 3375000.00 | JCC ENGINEERS PRIVATE LIMITED
1.10 | j)10.5-12.5 mtr. Frangible Lattice | 6.00 | Each |  | 348975.00 | 2093850.00 | 383970.00 | 2303820.00 | 300000.00 | 1800000.00 | 1800000.00 | JCC ENGINEERS PRIVATE LIMITED
2.00 | Supply of FAA Certified Inset type LED high intensity Runway CENTRE LINE (CL) light fitting for aviation visual aids requirements complete with shallow base and matching body of the fitting, inner body of the fitting, inner body and outer cover made of die cast aluminium complete with LED lamp of 6.6 Amps current with connected heat resistant accessories, prism assembly, optical assembly, "O" ring seal, pressure relief test plug, hardware, lenses and all standard accessories and ready for site installation as per sepcifications complete as required. a) Bidirectional Centerline fitting (RED/White) | 64.00 | Each |  | 60363.00 | 3863232.00 | 54410.00 | 3482240.00 | 52000.00 | 3328000.00 | 3328000.00 | JCC ENGINEERS PRIVATE LIMITED
3.00 | Supply of FAA Certified Inset type LED high intensity Runway CENTRE LINE (CL) light fitting for aviation visual aids requirements complete with shallow base and matching body of the fitting, inner body of the fitting, inner body and outer cover made of die cast aluminium complete with LED lamp of 6.6 Amps current with connected heat resistant accessories, prism assembly, optical assembly, "O" ring seal, pressure relief test plug, hardware, lenses and all standard accessories and ready for site installation as per sepcifications complete as required. b) Bidirectional Centerline fitting (White/White) | 108.00 | Each |  | 60363.00 | 6519204.00 | 54410.00 | 5876280.00 | 52000.00 | 5616000.00 | 5616000.00 | JCC ENGINEERS PRIVATE LIMITED
4.00 | Supply of FAA Certified Inset type LED high intensity Runway CENTRE LINE (CL) light fitting for aviation visual aids requirements complete with shallow base and matching body of the fitting, inner body of the fitting, inner body and outer cover made of die cast aluminium complete with LED lamp of 6.6 Amps current with connected heat resistant accessories, prism assembly, optical assembly, "O" ring seal, pressure relief test plug, hardware, lenses and all standard accessories and ready for site installation as per sepcifications complete as required. c) Bidirectional Centerline fitting (RED / Blank) | 20.00 | Each |  | 60363.00 | 1207260.00 | 54410.00 | 1088200.00 | 52000.00 | 1040000.00 | 1040000.00 | JCC ENGINEERS PRIVATE LIMITED
5.00 | Supply of FAA Certified Inset type LED Uni directional high intensity TOUCH DOWN ZONE (TDZ) (White) light fitting for aviation visual aids requirements complete with shallow base and matching body of the fitting, inner body and outer cover made of die cast aluminium complete LED lamp of 6.6 amps current with connected heat resistant accessories, prism assembly, optical assembly, "O" ring seal, pressure relief test plug, hardware, clear lenses and all standard accessories and ready for site installation as per sepcifications complete as required. | 189.00 | Each |  | 55000.00 | 10395000.00 | 49573.00 | 9369297.00 | 52000.00 | 9828000.00 | 9369297.00 | Vardhman Airport Solutions Pvt Ltd
6.00 | Supply of Inset type LED Uni directional high intensity SIDE ROW (SR) (RED Color) Approach light fitting for aviation visual aids requirements complete with shallow base and matching body of the fitting, inner body and outer cover made of die cast aluminium complete with LED lamp of 6.6 amps current with connected heat resistant accessories, prism assembly, optical assembly, "O" ring seal, pressure relief test plug, hardware, red lenses and all standard accessories and ready for site installation complete as required. | 13.00 | Each |  | 89030.70 | 1157399.10 | 114865.00 | 1493245.00 | 95000.00 | 1235000.00 | 1157399.10 | AMA Private Limited
7.00 | Supply of Elevated type LED Uni directional high intensity SIDE ROW (SR) (RED Color) Approach light fitting for aviation visual aids requirements complete with base plate, breakable coupling, mounting assembly, gasket complete with LED lamp of 6.6 amps current and all standard accessories and ready for site installation as per sepcifications complete as required. | 44.00 | Each |  | 48000.00 | 2112000.00 | 55619.00 | 2447236.00 | 65000.00 | 2860000.00 | 2112000.00 | AMA Private Limited
8.00 | Supply of Inset type LED fittings suitable for Uni directional high intensity APPROACH CENTRE LINE (APCL) (White) light fitting for aviation visual aids requirements complete with shallow base and matching body of the fitting, inner body and outer cover made of die cast aluminium complete with LED lamp of 6.6 amps current with connected heat resistant accessories, prism assembly, optical assembly, "O" ring seal, pressure relief test plug, hardware, clear lenses and all standard accessories and ready for site installation as per sepcifications complete as required. | 9.00 | Each |  | 90000.00 | 810000.00 | 114865.00 | 1033785.00 | 95000.00 | 855000.00 | 810000.00 | AMA Private Limited
9.00 | Supply of Elevated type LED Uni directional high intensity APPROACH CENTRE LINE (APCL) (White) light fitting for aviation visual aids requirements complete with base plate, breakable coupling, mounting assembly, gasket complete with LED lamp of 6.6 amps current and all standard accessories and ready for site installation as per sepcifications complete as required. | 139.00 | Each |  | 48000.00 | 6672000.00 | 55619.00 | 7731041.00 | 65000.00 | 9035000.00 | 6672000.00 | AMA Private Limited
10.00 | Supply of Elevated type LED unidirectional approach sequenced flashing light fixtures (White) with Flash Field control Unit with IP67 protection, driver unit, connected heat resistant accessories etc. The lights shall be compatible with the controller supplied and should be capable of flashing at frequencies 1 or 2 Hz at three different brillancies and suitable for remote operation. The fixtures together with the other lights of the same flashing system should be connected to the flash master control unit. The overall power consumption of light & flashing control field units should be less than 70W and suitable to works on Single Phase 230V+ 10%, 50 Hz, single phase, AC Supply etc. as per sepcifications complete as required. | 21.00 | Each |  | 160385.00 | 3368085.00 | 193456.00 | 4062576.00 | 155000.00 | 3255000.00 | 3255000.00 | JCC ENGINEERS PRIVATE LIMITED
11.00 | Supply of Flash master control unit (FMCU) with touch screen in metallic cabinet box. The controller cabinet feed the power supply to FFU's for flashing & powerline communication between FMCU and FFU's via 3 - wires standard installation cable connected in one parallel circuit to all LED sequential flashing light fixtures (inset & elevated). The powerline communication includes the information to each light fixtures i.e. luminance level, flashing frequency, synchronization information for the sequence, light monitoring information etc. The lights shall be compatible with the controller supplied and should be capable of flashing at frequencies 1 or 2 Hz at three different brillancies and suitable to works on Single Phase 230V+ 10%, 50 Hz, single phase, AC Supply/p & O/P circuit breaker, suitable for remote operation, ethernet port etc. complete as required and confirming to relevant standards, specifications as per the requirements. | 2.00 | Each |  | 750000.00 | 1500000.00 | 967280.00 | 1934560.00 | 600000.00 | 1200000.00 | 1200000.00 | JCC ENGINEERS PRIVATE LIMITED
12.00 | Supply of FAA Certified Inset type LED high intensity THRESHOLD (THD) (Green) light fitting for aviation visual aids requirements complete with shallow base and matching body of the fitting, inner body and outer cover made of die cast aluminium complete with LED lamp of 6.6 amps current with connected heat resistant accessories, prism assembly, optical assembly, "O" ring seal, pressure relief test plug, hardware, green prism / lenses and all standard accessories and ready for site installation as per sepcifications complete as required. | 38.00 | Each |  | 92000.00 | 3496000.00 | 89473.00 | 3399974.00 | 65000.00 | 2470000.00 | 2470000.00 | JCC ENGINEERS PRIVATE LIMITED
13.00 | Supply of FAA Certified Inset type LED high intensity END (RED) light fitting for aviation visual aids requirements complete with shallow base and matching body of the fitting, inner body and outer cover made of die cast aluminium complete with LED lamp of 6.6 amps current with connected heat resistant accessories, prism assembly, optical assembly, "O" ring seal, pressure relief test plug, hardware, red prism / lenses and all standard accessories and ready for site installation as per sepcifications complete as required. | 21.00 | Each |  | 89000.00 | 1869000.00 | 50782.00 | 1066422.00 | 55000.00 | 1155000.00 | 1066422.00 | Vardhman Airport Solutions Pvt Ltd
14.00 | Supply of FAA Certified Inset type LED Uni directional Stop Bar (RED) light fitting suitable for straight section/straight section (off set) / curved section for aviation visual aids requirements complete with shallow base and matching body of the fitting, inner body and outer cover made of die cast aluminium complete with LED lamp of 6.6 amps current with connected heat resistant accessories, prism assembly, optical assembly, "O" ring seal, pressure relief test plug, hardware, red prism / lenses and all standard accessories and ready for site installation as per sepcifications complete as required. | 66.00 | Each |  | 48000.00 | 3168000.00 | 43528.00 | 2872848.00 | 55000.00 | 3630000.00 | 2872848.00 | Vardhman Airport Solutions Pvt Ltd
15.00 | Supply of LED high intensity Runway guard light, Elevated, A pair of unidirectional, flashing yellow lights as per ICAO Annex 14. (1 set = 2 unit of light, one at left side and other at right side of taxiway) | 8.00 | Each |  | 176750.00 | 1414000.00 | 435276.00 | 3482208.00 | 215000.00 | 1720000.00 | 1414000.00 | AMA Private Limited
16.00 | Supply of inset type LED Uni directional Intermediate holding position (Yellow) light fitting for aviation visual aids requirements complete with shallow base and matching body of the fitting, inner body and outer cover made of die cast aluminium complete with LED lamp of 6.6 amps current with connected heat resistant accessories, prism assembly, optical assembly, "O" ring seal, pressure relief test plug, hardware, yellow prism / lenses and all standard accessories and ready for site installation as per sepcifications complete as required. | 23.00 | Each |  | 42000.00 | 966000.00 | 44737.00 | 1028951.00 | 55000.00 | 1265000.00 | 966000.00 | AMA Private Limited
17.00 | Supply of Inset type LED Uni-directional Rapid Exit Taxi Indicator (yellow) light for aviation visual aids requirements complete with shallow base and matching body of the fitting, inner body of the fitting, inner body and outer cover made of die cast aluminium complete with LED lamp of 6.6 Amps current with connected heat resistant accessories, prism assembly, optical assembly, "O" ring seal, pressure relief test plug, hardware, lenses and all standard accessories and ready for site installation as per sepcifications complete as required. | 13.00 | Each |  | 42000.00 | 546000.00 | 44737.00 | 581581.00 | 55000.00 | 715000.00 | 546000.00 | AMA Private Limited
18.00 | Supply of FAA Certified inset type LED Bidirectional Runway Edge light fitting for aviation visual aids requirements complete with shallow base and matching body of the fitting, inner body and outer cover made of die cast aluminium complete with LED lamp of 6.6 amps current with connected heat resistant accessories, prism assembly, optical assembly, "O" ring seal, pressure relief test plug, hardware, prism / lenses and all standard accessories and ready for site installation as per sepcifications complete as required. a) Bidirectional White/Yellow or White/White | 13.00 | Each |  | 70000.00 | 910000.00 | 114865.00 | 1493245.00 | 85000.00 | 1105000.00 | 910000.00 | AMA Private Limited
19.00 | Supply of Elevated type LED Omnidirectional Taxiway Edge light fixtures (Blue) for aviation visual aids requirements complete with base plate, breakable coupling, mounting assembly, gasket, BLUE lens complete with LED lamp of 6.6 amps current and all standard accessories and ready for site installation as per sepcifications complete as required. | 315.00 | Each |  | 3000.00 | 945000.00 | 3627.00 | 1142505.00 | 6000.00 | 1890000.00 | 945000.00 | AMA Private Limited
20.00 | Supply of 2 x 4 sqmm secondary lead made out of multi stranded copper conductor EPR insulated & PCP sheathed, anti-termite & anti rodent treated 600 V grade cable as specified in particular specifications as required. | 19800.00 | Mtr. |  | 135.00 | 2673000.00 | 179.00 | 3544200.00 | 180.00 | 3564000.00 | 2673000.00 | AMA Private Limited
21.00 | Supply of 1 x 6 sq.mm, 5 KV grade, AFL cable, type-C stranded tinned copper conductor, XLPE insulated with copper braided screened | 115060.00 | Mtr. |  | 145.00 | 16683700.00 | 221.00 | 25428260.00 | 180.00 | 20710800.00 | 16683700.00 | AMA Private Limited
22.00 | Supply of 6 sqmm, 5 KV grade plug and receptacle of type I, class 'B' connector and suitable field attachment with 5 KV grade XLPE insulated, PE sheathed, single core copper conductor screened cable as required. | 1124.00 | Each |  | 575.00 | 646300.00 | 789.00 | 886836.00 | 600.00 | 674400.00 | 646300.00 | AMA Private Limited
23.00 | Supply 2 pin plug and receptacles suitable for 2X4 Sq. mm copper conductor secondary lead | 1124.00 | Each |  | 750.00 | 843000.00 | 1147.00 | 1289228.00 | 850.00 | 955400.00 | 843000.00 | AMA Private Limited
24.00 | Supply of following rating completely enclosed rubber covered isolating transformer for use of 6.6 amps series airport lighting circuits having nominal voltage rating of 5KV and all rated for operation on 50 Hz. The transformer shall be water tight and shall be designed for direct burial in the earth or installation in a base confirming to the specifications, complete as required. a) 15 Watt 6.6/6.6 Amps | 315.00 | Each |  | 2500.00 | 787500.00 | 3226.00 | 1016190.00 | 3500.00 | 1102500.00 | 787500.00 | AMA Private Limited
25.00 | Supply of following rating completely enclosed rubber covered isolating transformer for use of 6.6 amps series airport lighting circuits having nominal voltage rating of 5KV and all rated for operation on 50 Hz. The transformer shall be water tight and shall be designed for direct burial in the earth or installation in a base confirming to the specifications, complete as required. b) 45 Watt 6.6/6.6 Amps | 291.00 | Each |  | 3500.00 | 1018500.00 | 3800.00 | 1105800.00 | 5000.00 | 1455000.00 | 1018500.00 | AMA Private Limited
26.00 | Supply of following rating completely enclosed rubber covered isolating transformer for use of 6.6 amps series airport lighting circuits having nominal voltage rating of 5KV and all rated for operation on 50 Hz. The transformer shall be water tight and shall be designed for direct burial in the earth or installation in a base confirming to the specifications, complete as required. c) 65 Watt, 6.6/6.6 Amp | 442.00 | Each |  | 4000.00 | 1768000.00 | 5090.00 | 2249780.00 | 6000.00 | 2652000.00 | 1768000.00 | AMA Private Limited
27.00 | Supply of following rating completely enclosed rubber covered isolating transformer for use of 6.6 amps series airport lighting circuits having nominal voltage rating of 5KV and all rated for operation on 50 Hz. The transformer shall be water tight and shall be designed for direct burial in the earth or installation in a base confirming to the specifications, complete as required. d) 100 Watt, 6.6/6.6 Amp | 35.00 | Each |  | 4300.00 | 150500.00 | 5162.00 | 180670.00 | 7500.00 | 262500.00 | 150500.00 | AMA Private Limited
28.00 | Supply of LED Guidance signage board (as per ICAO standard) of various sizes made out of 2 mm thick anodized aluminium frame with suitable angel support, 1.5 mm thick aluminium back symbols of sign should be screen printed on inside of sign face made of self-adhesive 3M film applied on the inside face with required coloring. Sign board shall be uniformly internally illuminated with required LED's i/c all other accessories to achieve uniform illumination level and with suitable converter to operate on 2.8 Amp to 6.6 Amp AC made for water tightness and locking arrangements, mounting legs with frangible coupling & base frame complete as per specifications etc. as required meeting ICAO Annexure 14 Vol.1. | 40.00 | Sq.mtr. |  | 40000.00 | 1600000.00 | 36562.00 | 1462480.00 | 50000.00 | 2000000.00 | 1462480.00 | Vardhman Airport Solutions Pvt Ltd
29.00 | Supply, Installation, Testing & Commissioning of 160 KVA capacity 3 phase input, 3 phase output IGBT based, modular type, true online double conversion type with isolation transformer, harmonic filter etc. 2 nos UPSs with provision to run in load sharing mode suitable to drive constant current regulators(CCR) with 100% unbalanced load at output at full load condition with standard features like 100% rated static bypass, maintenance bypass facilities active input power factor correction, phase sequence corrector, pure sinewave output, compatibility of generator supply, user friendly LCD display and battery management features integrated with main UPS controller, operating condition 415V +15%, ‐20%, 3 phase, 50Hz ±5%, IP20 capable of running at 100% 2 phase/single phase unbalance load with 3phase of output and as per the enclosed technical specification. The job also includes.. (a) Supply, Installation, Testing & Commissioning suitable capacity SMF batteries to give a backup time of minimum 30 minutes at full load with each UPS System along with suitable rating switch gears, interconnection between battery bank and UPS , battery rack etc. as required. (b) Supply, Installation, Testing and Commissioning of necessary switchgears, cables etc. for synchronisation of the UPSs on load sharing mode. | 2.00 | Each |  | 4000000.00 | 8000000.00 | 2183530.00 | 4367060.00 | 4200000.00 | 8400000.00 | 4367060.00 | Vardhman Airport Solutions Pvt Ltd
30.00 | Supply of following size 1.1 KV grade XLPE insulated, PVC sheathed, armoured Copper conductor conforming to IS 7098 (Part I) amended upto date. a) 3 C x 25 Sq. mm. | 500.00 | Mtr. |  | 1070.00 | 535000.00 | 819.00 | 409500.00 | 1000.00 | 500000.00 | 409500.00 | Vardhman Airport Solutions Pvt Ltd
31.00 | Supplying of 1100V grade multicore stranded Aluminium Conductor XLPE insulated core laid up, extruded inner sheath of PVC, galvanised steel strip armoured & overall PVC sheathed armoured cables a) 3.5 X 35 Sq.mm | 500.00 | Mtr. |  | 276.00 | 138000.00 | 234.00 | 117000.00 | 250.00 | 125000.00 | 117000.00 | Vardhman Airport Solutions Pvt Ltd
32.00 | Supplying of 1100V grade multicore stranded Aluminium Conductor XLPE insulated core laid up, extruded inner sheath of PVC, galvanised steel strip armoured & overall PVC sheathed armoured cables b) 3.5 X 50 Sq.mm | 2500.00 | Mtr. |  | 372.00 | 930000.00 | 287.00 | 717500.00 | 350.00 | 875000.00 | 717500.00 | Vardhman Airport Solutions Pvt Ltd
33.00 | Supplying of 1100V grade multicore stranded Aluminium Conductor XLPE insulated core laid up, extruded inner sheath of PVC, galvanised steel strip armoured & overall PVC sheathed armoured cables c) 3.5 X 240 Sq.mm | 500.00 | Mtr. |  | 1475.00 | 737500.00 | 1224.00 | 612000.00 | 1300.00 | 650000.00 | 612000.00 | Vardhman Airport Solutions Pvt Ltd
34.00 | Fabrication & supply of MS transformer housing box of size 750mm x 350 mm x 450 mm ( H) made out 6 mm thick MS heet and top cover 10 mm thick MS sheet with two compartment as per drawing and all inserts should be suitable for M-10 size bolt shall be of SS including painting of box with one coat of primer & two coats of black enamel paint etc. as per specifications as required . | 133.00 | Each |  | 12500.00 | 1662500.00 | 13908.00 | 1849764.00 | 15000.00 | 1995000.00 | 1662500.00 | AMA Private Limited
35.00 | Fabrication & supply of MS transformer housing box of size 600mm x 350 mm x 450 mm (H) made out 6 mm thick MS sheet and top cover 10 mm thick MS sheet with two compartment as per drawing and all inserts should be suitable for M-10 size bolt shall be of SS including painting of box with one coat of primer & two coats of black enamel paint etc. as per specifications as required . | 83.00 | Each |  | 9500.00 | 788500.00 | 12904.00 | 1071032.00 | 12000.00 | 996000.00 | 788500.00 | AMA Private Limited
36.00 | Fabrication & supply of MS transformer housing box of size 350mm x 350 mm x 450 mm (H) made out 6 mm thick MS sheet and top cover 10 mm thick MS sheet as per drawing and all inserts should be suitable for M-10 size bolt shall be of SS including painting of box with one coat of primer & two coats of black enamel paint etc. as per specificaitons as required. | 249.00 | Each |  | 5500.00 | 1369500.00 | 8603.00 | 2142147.00 | 7500.00 | 1867500.00 | 1369500.00 | AMA Private Limited
37.00 | Installation, testing and Commissioning of inset type fitting with core cutting, aligning and setting i/c providing sealing material and installation of Isolating Transformer, switching device, Crimping / Jointing of Plug receptacles & other accessories required for commissioning i/c supply of all materials except isolating transformer etc. complete as required. a) Fitting size up to 8 " / 12" | 547.00 | Each |  | 6000.00 | 3282000.00 | 6700.00 | 3664900.00 | 10000.00 | 5470000.00 | 3282000.00 | AMA Private Limited
38.00 | Installation, testing & commissioning of Elevated type approach / runway edge / threshold / end / taxiway light fixtures/ Runway Guard light/Sequential flashing Lights on existing transformer housing boxes and installation of isolating transformers, switching device i/c supply of all materials except isolating transformer etc. complete as required. | 501.00 | Each |  | 500.00 | 250500.00 | 268.00 | 134268.00 | 300.00 | 150300.00 | 134268.00 | Vardhman Airport Solutions Pvt Ltd
39.00 | Installation of rectangular MS Transformer housing box of Size 750mm x 350mm X 450mm height including excavation of surface in soil etc , providing three nos. 250 mm long 15 mm dia 'B' class GI pipe in the bottom surface for drainage of water etc., cutting & threading of pipe i/c leveling of housing box with suitable instrument etc. and installation of housing box by providing base cement concrete of 1:3:6 of size 950 x 550 x 150 mm thick, and PCC of 1:2:4 all around the housing box of width not less than 100 mm and making suitable pedestal of 300mm & 100 mm thick & making slope to the level with the surface all around the housing box, painting, lettering, numbring etc i/c disposal of excavated material and making good the same as original complete as required. | 127.00 | Each |  | 4000.00 | 508000.00 | 4020.00 | 510540.00 | 6000.00 | 762000.00 | 508000.00 | AMA Private Limited
40.00 | Installation of MS transformer housing box of size 600mm x 350 mm x 450 mm (H) including excavation of surface in soil etc , providing two nos. 250 mm long 15 mm dia 'B' class GI pipe in the bottom surface for drainage of water etc., cutting & threading of pipe i/c leveling of housing box with suitable instrument etc. and installation of housing box by providing base cement concrete of 1:3:6 of size 800 x 550 x 150 mm thick, and PCC of 1:2:4 all around the housing box of width not less than 100 mm and making suitable pedestal of 300mm & 100 mm thick & making slope to the level with the surface all around the housing box, painting, lettering, numbring etc i/c disposal of excavated material and making good the same as original complete as required. | 79.00 | Each |  | 4000.00 | 316000.00 | 3350.00 | 264650.00 | 5000.00 | 395000.00 | 264650.00 | Vardhman Airport Solutions Pvt Ltd
41.00 | Installation of MS transformer housing box of size350mm x 350 mm x 450 mm (H) including excavation of surface in soil etc , providing one nos. 250 mm long 15 mm dia 'B' class GI pipe in the bottom surface for drainage of water etc., cutting & threading of pipe i/c leveling of housing box with suitable instrument etc. and installation of housing box by providing base cement concrete of 1:3:6 of size 550 x 550 x 150 mm thick, and PCC of 1:2:4 all around the housing box of width not less than 100 mm and making suitable pedestal of 300mm & 100 mm thick & making slope to the level with the surface all around the housing box, painting, lettering, numbring etc i/c disposal of excavated material and making good the same as original complete as required. | 237.00 | Each |  | 3200.00 | 758400.00 | 2680.00 | 635160.00 | 3500.00 | 829500.00 | 635160.00 | Vardhman Airport Solutions Pvt Ltd
42.00 | Installation of guidance signboards of various sizes i/c spply & installation of suitable isolating transformer and providing secondary leads etc. i/c supply of all materials, i/c pedestal upto 1m all around the signage with 1:2:4 (cement, concrete, coarse) of thickness 100mm with neat cement finish plaster, testing and commissioning etc. as required. | 20.00 | Job |  | 10000.00 | 200000.00 | 10720.00 | 214400.00 | 10000.00 | 200000.00 | 200000.00 | JCC ENGINEERS PRIVATE LIMITED, AMA Private Limited
43.00 | Supply & laying of 01 No. 63 mm dia size PN10, PE 80 rating HDPE pipe through trenchless technology (HDD) upto a depth of approx. 2 meter as required and as specified. | 2900.00 | Mtr. |  | 900.00 | 2610000.00 | 466.00 | 1351400.00 | 600.00 | 1740000.00 | 1351400.00 | Vardhman Airport Solutions Pvt Ltd
44.00 | Supply and laying of double wall corrugated high density polyethylene (DWC HDPE pipe) pipe confirming to IS:14930 (part-2) with latest amendment, complete along with 4mm nylon rope with accessories like couplers, bends, tee etc. in the soil for GLF work upto 750 mm deep, back filling & making good the same as per site requirement a) OD 63 mm/ ID 50 mm DWC | 49900.00 | Mtr. |  | 150.00 | 7485000.00 | 154.00 | 7684600.00 | 300.00 | 14970000.00 | 7485000.00 | AMA Private Limited
45.00 | Supply of 50 mm dia OD ISI marked HDPE pipe as per IS:4984:2016, of rating PE 80, PN 10 with 4 mm nylon rope complete as required | 360.00 | Mtr. |  | 100.00 | 36000.00 | 129.00 | 46440.00 | 150.00 | 54000.00 | 36000.00 | AMA Private Limited
46.00 | Laying of 50 mm dia OD HDPE pipe in soil including providing the socket at transformer housing upto a depth of 500 mm from the finished surface and refilling the same as required including consolidation & disposal of un-used material etc. as required as per the direction of engineer in charge. | 360.00 | Mtr. |  | 120.00 | 43200.00 | 107.00 | 38520.00 | 200.00 | 72000.00 | 38520.00 | Vardhman Airport Solutions Pvt Ltd
47.00 | Laying of 63mm /50 mm dia (OD), HDPE pipe in hard surface to connect the consecutive transformer housing boxes and transformer housing box to Runway centreline / other fitting / location at a suitable depth. The laying shall be done in hard surface / PQC/ bitumin by cutting the surface using jack hammer/ hydrulic excavator cutter etc. upto a depth of 500 mm of finished surface and making the same good and disposal of un-usable materials etc. i/c drawing 4 mm thick nylon rope in the complete length of HDPE pipe, suitable for drawing the cable and earth wire in the pipe after re-carpeting etc. complete as required, as per the direction of Engineer-in-Charge. | 360.00 | Mtr. |  | 250.00 | 90000.00 | 402.00 | 144720.00 | 1000.00 | 360000.00 | 90000.00 | AMA Private Limited
48.00 | Laying of one number PVC insulated & PVC sheathed armoured aluminium / copper conductor power cable of grade exceeding .4 KV but not exceeding 11 KV of size not exceeding 25 sq. mm. in the existing cable duct / masonry trench/ RCC/HUME/METAL/HDPE pipes etc. as required. (Feeder & looping cable) | 100000.00 | Mtr. |  | 20.00 | 2000000.00 | 20.00 | 2000000.00 | 35.00 | 3500000.00 | 2000000.00 | AMA Private Limited, Vardhman Airport Solutions Pvt Ltd
49.00 | Laying of one number 2 X 4 sq. mm AFL secondary cable along with 1 X 4 sq. mm earth cable of voltage grade not exceeding 1.1 KV in the cable duct / masonry trench / RCC / HUME / METAL / GI / HDPE pipes etc. as required. | 4420.00 | Mtr. |  | 20.00 | 88400.00 | 24.00 | 106080.00 | 35.00 | 154700.00 | 88400.00 | AMA Private Limited
50.00 | Kerf cutting with machine in taxiway/runway/apron of PQC/bituminous surface of depth upto 50 mm and width upto 15 mm for 1 or 2 nos secondary lead along with earth cables and laying of secondary lead and earth cable by wrapping cotton tape i/c refilling the same by suitable sealing material (PIDILITE) etc complete as required and as per instruction of EIC. | 8600.00 | Mtr. |  | 325.00 | 2795000.00 | 268.00 | 2304800.00 | 550.00 | 4730000.00 | 2304800.00 | Vardhman Airport Solutions Pvt Ltd
51.00 | Kerf cutting with machine in taxiway/runway/apron of PQC/bituminous surface of depth upto 80 mm and width upto 15 mm for 3 or 4 nos secondary lead along with earth cables and laying of secondary lead and earth cable by wrapping cotton tape i/c refilling the same by suitable sealing material (PIDILITE) etc complete as required and as per instruction of EIC. | 2200.00 | Mtr. |  | 325.00 | 715000.00 | 369.00 | 811800.00 | 600.00 | 1320000.00 | 715000.00 | AMA Private Limited
52.00 | Making connection of secondary Connectors (male & Female) of size 2 x 4 Sq.mm multi stranded annealed conductor CPE sheathed unshielded cable of 600 V grade on one end. | 1048.00 | Job |  | 150.00 | 157200.00 | 134.00 | 140432.00 | 200.00 | 209600.00 | 140432.00 | Vardhman Airport Solutions Pvt Ltd
53.00 | Earthing with 'B' class G. I. earth pipe 4.5 mtrs. long x 40 mm dia i/c accessories and providing masonry enclosures with cover plate having locking arrangement & watering pipe etc. i/c charcoal/ coke and salt complete as required. | 80.00 | Each |  | 9500.00 | 760000.00 | 9380.00 | 750400.00 | 8000.00 | 640000.00 | 640000.00 | JCC ENGINEERS PRIVATE LIMITED
54.00 | Providing and laying earth connection from earth electrode with 6 SWG dia G.I. Wire in 15 mm dia G.I. pipe medium class from earth electrode including connection with G.I. thimble excavation and re-filling as required. | 570.00 | Mtr. |  | 275.00 | 156750.00 | 268.00 | 152760.00 | 200.00 | 114000.00 | 114000.00 | JCC ENGINEERS PRIVATE LIMITED
55.00 | Providing and fixing 6 SWG G. I. wire on surface or in recess for loop earthing as required. | 57530.00 | Mtr. |  | 15.00 | 862950.00 | 24.00 | 1380720.00 | 23.00 | 1323190.00 | 862950.00 | AMA Private Limited
56.00 | Providing and laying of yellow/ green 4 Sq.mm earth cable in existing HDPE/DWC Pipe/Kerf. | 19800.00 | Mtr. |  | 60.00 | 1188000.00 | 53.00 | 1049400.00 | 50.00 | 990000.00 | 990000.00 | JCC ENGINEERS PRIVATE LIMITED
57.00 | Making connection of 5 KV grade, 6 Sq.mm Copper conductor Screened cable with plug & receptacle i/c connecting continuity wire for screen etc. complete as required. | 1048.00 | Job |  | 150.00 | 157200.00 | 134.00 | 140432.00 | 200.00 | 209600.00 | 140432.00 | Vardhman Airport Solutions Pvt Ltd
58.00 | Taking GPS based co-ordinates on complete length of main runway, cable route etc. by using total station for installation of CAT-I/II approach lighting system and taking the level, making the approach profile at each point with mast foundation level and identifying the locations of light fixtures, route of cable etc. based on GPS co- ordinates and marking, submission of reports / drawings as required and as per directions of the Engineer In charge. | 1.00 | Job |  | 200000.00 | 200000.00 | 670000.00 | 670000.00 | 300000.00 | 300000.00 | 200000.00 | AMA Private Limited
59.00 | Numbering of Airfield Light Fixtures on the base/ top surface/ RCC foundation of light fixture with good quality of black color enamel paint etc. complete as required. | 1048.00 | Job |  | 75.00 | 78600.00 | 67.00 | 70216.00 | 100.00 | 104800.00 | 70216.00 | Vardhman Airport Solutions Pvt Ltd
60.00 | Supply, Installation, Testing and Commissioning of TTA type indoor cubicle LT panel as per IEC 61439, IP42, suitable for 415V+/-10%, 3 Phase, 4 wire 50 Hz AC supply system, fabricated in compartmentalized modular design from CRCA sheet steel of 2 mm thick for frame work and covers, 3 mm thick for gland plates i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having TPN Aluminium alloy bus bars with 100% size neutral bus as that of phase bus, supported with SMC bus bar supports, with short circuit withstand capacity as per design subject to minimum 35 kA for 1 sec, bottom base channel of MS section not less than 75 mm x 40 mm, fabrication shall be done in transportable sections, entire panel shall have a common Copper earth bus bar of size as per IS 3043 subject to minimum 32 mm x 5 mm at the rear with 2 Nos. earth stud, solid/ flexible copper connections from main earth bus bar to switchgears with required size of Cooper conductors/ bus bars and control wiring with 2.5 sqmm FRLS PVC insulated copper conductor cable, cable alleys, cable gland plates in two halves, including control and interlocking of incomers, bus coupler and providing following switchgears/ accessories as per specifications. Incomer 2 Nos. 630A, 4P MCCB, Microprocessor based release (Ics = Icu = 35kA) with inbuilt O/L , S/C & E/F protection as per specification and each incomer shall be provided with following accessories. 1 Set of phase indicating LED lamps with 2 amp back up MCB. 1 No. 96 x 96 sqmm Digital MFM meter and 3 nos. Cast resin CTs of ratio 630/5A , Class 0.5 accuracy and 10 VA burden, suitable to measure voltage, Ampere, Frequency, Power Factor, KVA, KW, KVAH, KWH, MDI & Individual Odd Harmonics for voltage and current including THD upto 31st Order with RS-485 port. 1 Set of ON/ OFF/TRIP Indicating LED Lamps With 2 Amp MCB . Bus coupler 1 Nos. 630A 4P MCCB, Microprocessor based release (Ics = Icu = 35kA) with inbuilt O/L , S/C & E/F protection as per specification with following accessories. 1 Set of ON/ OFF/TRIP Indicating LED Lamps With 2 Amp MCB. Electrical & Mechanical Interlocking between both incomers & Bus coupler. Busbars 4P aluminium bus bars of 800A capacity with heat shrinkable coloured sleeves incl. SMC bus bars supports at required intervals complete for cross section, size supports & their spacing etc. for withstanding fault level of 35 KA for 1 sec. The electrical panel shall be fully ventilated to maintain internal body temp. < 40 deg 'C' when room amb. temp. is equal of less than 35 deg 'C'. Required ventilation fans shall be provided and tested. Outgoings 12 Nos - (9 +03Spares ). 160A 4P MCCB with built in thermal magnetic release with adjustable thermal setting (Ics = Icu =25 KA) 09 Nos. (6 Nos +3 spares) 125A 4P MCCB with built in thermal magnetic release with adjustable thermal setting (Ics = Icu =25 KA) 12 (9 Nos. + 3 spares) 63A 4P MCCB with built in thermal magnetic release with adjustable thermal setting (Ics = Icu =25 KA) 26 (20 Nos. + 6 spares) 32A 4P MCCB with built in thermal magnetic release with adjustable thermal setting (Ics = Icu =25 KA) For each busbar section-1 Set Surge protection device Type 2 ( Class C), 4 Module, MOV type suitable for 8/ 20µs surge, Voltage Protection level Up < 1.5kV, Operating Temperature -40 deg 'c' - +80 deg 'C', Connected Between 3Nos. phase to neutral and 1Nos. neutral to earth with discharge Current Imax. ≥ 40KA Per module & In ≥ 20kA per Module. SPD with built in fuse and pluggable type. For connecting SPD minimum 10sqmm copper wire must be used & length of connecting leads shall not be more than 500mm for per mode connection including all necessary accessories. The SPD shall be compliant and tested from KEMA KEUR / VDE / NABL tested as per IEC 61643-11 / UL. 1 Set of earth leakage relay (ELR) (30-3000mA) with CBCT & TRIP due to earth leakage Indicating LED Lamps with 2 Amp MCB for each outgoing MCCB. | 1.00 | Job |  | 2800000.00 | 2800000.00 | 3027797.00 | 3027797.00 | 1064815.00 | 1064815.00 | 1064815.00 | JCC ENGINEERS PRIVATE LIMITED
61.00 | Laying of one number PVC insulated & PVC sheathed XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required a) Upto 35 sqmm | 450.00 | Mtr. |  | 20.00 | 9000.00 | 34.00 | 15300.00 | 35.00 | 15750.00 | 9000.00 | AMA Private Limited
62.00 | Laying of one number PVC insulated & PVC sheathed XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required b) Above 35 sqmm and upto 95 sqmm | 2300.00 | Mtr. |  | 20.00 | 46000.00 | 40.00 | 92000.00 | 50.00 | 115000.00 | 46000.00 | AMA Private Limited
63.00 | Laying of one number PVC insulated & PVC sheathed XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required c) Above 185 sqmm and upto 400 sqmm | 400.00 | Mtr. |  | 20.00 | 8000.00 | 47.00 | 18800.00 | 100.00 | 40000.00 | 8000.00 | AMA Private Limited
64.00 | Construction of masonry Chamber 2m x 1.2 m x 1.5m (deep) inside, in precast cement concrete solid block made from 1:1.5:3 (1 Cement: 1.5 coarse and sand : 3 graded stone aggregate 20 mm nominal size ) in cement mortar 1:4 (1 cement :4 coarse and sand) including necessary excavation, foundation concrete 1:5:10 (1 cement :5 fine sand : 10 graded stone aggregated 40 mm nominla size ) of thickness 100 mm and inside plastering with cement mortar 1:3 (1 cement : 3 coarse sand ) 12 mm thick, finished with a floating coat of neat cement complete as per standard design. | 12.00 | Each |  | 20000.00 | 240000.00 | 20100.00 | 241200.00 | 25000.00 | 300000.00 | 240000.00 | AMA Private Limited
65.00 | Providing and placing in position 150 mm thick, factory made machine batched & machine precast RCC Rectangular Covers on chambers of various sizes of M-25 grade cement concrete for RCC work, including cost of centering, shuttering, reinforcement of 8 mm dia TMT mm dia bar for hooks etc, i/c cost of cartage, all leads & lift, handling at site etc. all complete as per direction of Engineer-in-Charge. Slab Size - 2.4 mtr x 1.6 mtr. | 12.00 | Each |  | 45000.00 | 540000.00 | 8509.00 | 102108.00 | 10000.00 | 120000.00 | 102108.00 | Vardhman Airport Solutions Pvt Ltd
66.00 | Supplying and making end termination with brass compression gland and Aluminimum lugs for following size of PVC insulated and PVC sheathed / XLPE Aluminium conductor cable of 1.1 KV grade as required. a)3.5 X 35 Sq.mm | 4.00 | Set |  | 1000.00 | 4000.00 | 695.00 | 2780.00 | 500.00 | 2000.00 | 2000.00 | JCC ENGINEERS PRIVATE LIMITED
67.00 | Supplying and making end termination with brass compression gland and Aluminimum lugs for following size of PVC insulated and PVC sheathed / XLPE Aluminium conductor cable of 1.1 KV grade as required. b)3.5 X 50 Sq.mm | 50.00 | Set |  | 1200.00 | 60000.00 | 1100.00 | 55000.00 | 800.00 | 40000.00 | 40000.00 | JCC ENGINEERS PRIVATE LIMITED
68.00 | Supplying and making end termination with brass compression gland and Aluminimum lugs for following size of PVC insulated and PVC sheathed / XLPE Aluminium conductor cable of 1.1 KV grade as required. c) 3.5 X 240 Sq.mm | 4.00 | Set |  | 2000.00 | 8000.00 | 2148.00 | 8592.00 | 1000.00 | 4000.00 | 4000.00 | JCC ENGINEERS PRIVATE LIMITED
69.00 | Supplying and making end termination with brass compression gland and Copper lugs for following size of PVC insulated and PVC sheathed / XLPE Copper conductor cable of 1.1 KV grade as required. a) 3C x 25 Sq. mm. | 72.00 | Set |  | 1800.00 | 129600.00 | 794.00 | 57168.00 | 600.00 | 43200.00 | 43200.00 | JCC ENGINEERS PRIVATE LIMITED
70.00 | Note 1: Rate quoted shall be inclusive of any taxes, duties, cess, fee, royalty charges etc. levied under any statute but exclusive of GST. Goods & Services Tax (GST) shall be paid to the contractor for any taxable supply / services / works against a valid tax invoice as per terms and conditions of the contract. 2. The work is to be executed in operational area of airport, nos. of working hours might be restricted, accordingly contractor has to quote considering all these factors as per SCC. Adequate skilled manpower and vehicle for transportation of manpower and material will be provided during execution of the work as per SCC. On this account, any claim for extra payment shall not be entertained. 3. For further detail of BOQ please refer tender document.
| Total in Figures |  |  |  |  | 130915617.10 |  | 142864844.00 |  | 149955555.00
Comparative Chart(eAuction)
Sl.No | Bidder Name | Auction Start Price | Quoted Rate in Figures and Words (Iteration 0)
|  |  | Bidder Price | Amount in Words
1 | AMA Private Limited | 130915617.00 | 128915617.00 | Tweleve Crore Eighty Nine Lakh Fifteen Thousand Six Hundred and Seventeen
2 | Vardhman Airport Solutions Pvt Ltd | 130915617.00 | 127415617.00 | Tweleve Crore Seventy Four Lakh Fifteen Thousand Six Hundred and Seventeen
3 | JCC ENGINEERS PRIVATE LIMITED | 130915617.00 | 126915617.00 | Tweleve Crore Sixty Nine Lakh Fifteen Thousand Six Hundred and Seventeen
Lowest Amount Quoted BY: JCC ENGINEERS PRIVATE LIMITED(126915617.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of CAT-II Lighting System Tender ID: 2022_AAI_137821_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | AMA Private Limited | 130915617.10 | L1
| 2 | Vardhman Airport Solutions Pvt Ltd | 142864844.00 | L2
| 3 | JCC ENGINEERS PRIVATE LIMITED | 149955555.00 | L3