## BoQ1
Government eProcurement System Created By: MUKESH KUMAR Created Date/Time: 18-Jan-2023 03:53 PM Tender Title: Provision of Surge suppression and Fire suppression Tender ID: 2022_AAI_138018_1
Tender Inviting Authority: AGM (ENGG-ELECT), AAI, SRINAGAR INTERNATIONAL AIRPORT, SRINAGAR, J&K-190007.
Name of Work: Provision of Surge suppression and Fire suppression systems etc. for Electrical and CNS installation at Srinagar Airport.
Contract No: <Enter Contract No Details>
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | CENTRE TAP ENGINEERING(GSTN-24AGPPP8172K1ZP) |  | PRUDENT EPC PRIVATE LIMITED(GSTN-27AAKCP4656L1ZS) |  | Unex Power Point Pvt Ltd(GSTN-07AAACU1740J1ZG)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply, Installation, Testing & Commissioning of Aerosol based Fire Suppression System Aerosol generator having aerosol mass of 2500gm shall be electrically actuated by means of Fire Alarm cum Release Panel. The housing shall be constructed of stainless steel shell.Housing shall be sealed with a non-permeable membrane. Units shall have passed salt spray corrosion testing per UL Standard 2127 as part of their listing. Aerosol generated shall be potassium based. Agent shall have no ozone depletion potential and no global warming potential. Agent shall be listed by the US EPA under the SNAP program. Aerosol generators shall be listed by Underwriter’s Laboratories (UL) to UL Subject 2775 covering Fixed Condensed Aerosol Systems per NFPA 2010. UL approved design density of the aerosol should be less than 100g/cu.mtr for Class A, B & C fires as per NFPA. The Aerosol generator should have self life of 15 years. Aerosol generator shall be supplied with Stainless steel Bracket & Gland. | 7.00 | Each |  | 430000.00 | 3010000.00 | 106000.00 | 742000.00 | 80500.00 | 563500.00 | 563500.00 | Unex Power Point Pvt Ltd
2.00 | Supply, Installation, Testing & Commissioning of Aerosol based Fire Suppression System Aerosol generator having aerosol mass of 1500gm shall be electrically actuated by means of Fire Alarm cum Release Panel. The housing shall be constructed of stainless steel shell.Housing shall be sealed with a non-permeable membrane. Units shall have passed salt spray corrosion testing per UL Standard 2127 as part of their listing. Aerosol generated shall be potassium based. Agent shall have no ozone depletion potential and no global warming potential. Agent shall be listed by the US EPA under the SNAP program. Aerosol generators shall be listed by Underwriter’s Laboratories (UL) to UL Subject 2775 covering Fixed Condensed Aerosol Systems per NFPA 2010. UL approved design density of the aerosol should be less than 100g/cu.mtr for Class A, B & C fires as per NFPA. The Aerosol generator should have self life of 15 years. Aerosol generator shall be supplied with Stainless steel Bracket & Gland | 1.00 | Each |  | 350000.00 | 350000.00 | 93000.00 | 93000.00 | 58700.00 | 58700.00 | 58700.00 | Unex Power Point Pvt Ltd
3.00 | Supply, Installation, Testing & Commissioning of Aerosol based Fire Suppression System Aerosol generator having aerosol mass of 1000gm shall be electrically actuated by means of Fire Alarm cum Release Panel. The housing shall be constructed of stainless steel shell.Housing shall be sealed with a non-permeable membrane. Units shall have passed salt spray corrosion testing per UL Standard 2127 as part of their listing. Aerosol generated shall be potassium based. Agent shall have no ozone depletion potential and no global warming potential. Agent shall be listed by the US EPA under the SNAP program. Aerosol generators shall be listed by Underwriter’s Laboratories (UL) to UL Subject 2775 covering Fixed Condensed Aerosol Systems per NFPA 2010. UL approved design density of the aerosol should be less than 100g/cu.mtr for Class A, B & C fires as per NFPA. The Aerosol generator should have self life of 15 years. Aerosol generator shall be supplied with Stainless steel Bracket & Gland. | 2.00 | Each |  | 250000.00 | 500000.00 | 82000.00 | 164000.00 | 50750.00 | 101500.00 | 101500.00 | Unex Power Point Pvt Ltd
4.00 | Supply, Installation, Testing & Commissioning of UL/EN Listed Fire Detection Cum Release System with cross zoning of UL listed heat & smoke detectors, UL listed hooter cum strobe, UL listed abort & release button with SMPS & Battery complete as required | 3.00 | Each |  | 50000.00 | 150000.00 | 73000.00 | 219000.00 | 52400.00 | 157200.00 | 150000.00 | CENTRE TAP ENGINEERING
5.00 | Supply, Installation, Testing & Commissioning of 2 Core 1.5 sq. mm. FRLS type Armored cable complete as required. | 100.00 | Meter |  | 150.00 | 15000.00 | 250.00 | 25000.00 | 155.00 | 15500.00 | 15000.00 | CENTRE TAP ENGINEERING
6.00 | Smart Surge Protection Device: Supply, Installation, Testing & Commissioning of 3 Phase / Type1+2 (KEMA Certified) Lightning current & Surge Protection Device at mains LT panel (3 phase, 415 V) for (L-N) Single-pole combined lightning current and surge arrester, Type 1 SPD. The device shall be non-exhausting metal encapsulated, spark gap based technology and tested as per latest and valid IEC 61643-11:2011 or EN 61643-11:2012 standards. It shall be capable to discharge Lightning current (10/350μs) of 25 KA (L-N) and 100kA(N-E) and voltage protection level of device shall be ≤ 1.5 KV,. The device shall haveinbuilt fuse for L-N. Follow current extinguishing capability [L-N]/[N-PE] : 100kArms / 100Arms. The device shall have built in fuse and operation of SPD shall be independent of Line current for L-N SPD. The short circuit with stand capability of the device shall be 100 KArms for L-N SPD. The device shall have mechanical indication for both the states (green for ‘healthy’ and red for failure) on L-N and N-PE. The device shall be certified by KEMA /VDE or NABL lab as per IEC 61643-11:2011 or or EN 61643-11:2012 for testing of all parameter at 10/350 μs and 8/20 μs. with transparent enclosure IP65. | 2.00 | Each |  | 30000.00 | 60000.00 | 220000.00 | 440000.00 | 72200.00 | 144400.00 | 60000.00 | CENTRE TAP ENGINEERING
7.00 | Supply, Installation, Testing & Commissioning Cylinderless Clean Agent based (Zero global warming potential) Fire Suppression systems, suitable for extinguishing, electrical enclosed panel, fire by automatically triggering the thermo-activated micro capsules of aerosol forming solid compound (minimum 100gm aerosol for 1 cum panel space) or equivalent compound with cord minimum 3.5 Mtr for 1 cum panel space activated at 120-175 Degree C temperature ( as per requirement of compartment of the panel).in each compartment of the panel confoming to relevant NFPA 2010,UL approved .Agent shall be listed by the US EPA under the SNAP program. The system has to be maintenance free and without any pressurized cylinder,tube, pressure gauge as required. | 120.00 | Cum |  | 10000.00 | 1200000.00 | 30000.00 | 3600000.00 | 35100.00 | 4212000.00 | 1200000.00 | CENTRE TAP ENGINEERING
| Total in Figures |  |  |  |  | 5285000.00 |  | 5283000.00 |  | 5252800.00
Lowest Amount Quoted BY: Unex Power Point Pvt Ltd(5252800.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of Surge suppression and Fire suppression Tender ID: 2022_AAI_138018_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Unex Power Point Pvt Ltd | 5252800.00 | L1
| 2 | PRUDENT EPC PRIVATE LIMITED | 5283000.00 | L2
| 3 | CENTRE TAP ENGINEERING | 5285000.00 | L3