## BoQ1
Government eProcurement System Created By: ALLAN TOMY Created Date/Time: 13-Feb-2023 05:23 PM Tender Title: SITC OF PAC 13TR AND 10 TR UNDER BUYBACK Tender ID: 2022_GAIL_136993_1
Tender Inviting Authority: GAIL (India) Limited, Noida
Name of Work: SUPPLY, INSTALLATION, TESTING & COMMISSIONING OF PRECISION AIR CONDITIONERS (13TR & 10TR) AT GAIL NOIDA UNDER BUYBACK BASIS
Contract/Tender No: NIC E-TENDER NO. 2022_GAIL_136993_1 [TENDER REF. NO. GAIL/NOIDA/CNP/MAINT/22161]
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | VOLKS ENERGIE PVT LTD(GSTN-07AADCV9396C1ZZ) |  | APEXINFRANET PVT LTD(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Cat (A) -New PAC System Items
2.00 | SUPPLY PART
3.00 | 13 Tr. Precision Air Conditioning Units Supply of Floor Mounted, Bottom discharge, Air Cooled DX type CRAC units for server room application, equipped with most advanced technology, guaranteeing precise control of Data Centers and server room. The units shall be selected on the basis of following parameters: i) 27 Deg C / 36% RH of return air ii) Supply air in between 15 - 17 Deg C iii) 45 Deg C of Design Ambient temperature iv) Precision Air-Conditioner will have green refrigerant (R407C/410A). v) Specific Power consumption shall be low as per site design conditions including compressor, evaporator fans and condensers The Indoor unit shall comprise of Digital Scroll Compressor, Fiberglass corrosion resistant EC fans, Evaporator DX Cooling Coil with hydrophilic coating, Microprocessor controllers, TXV, Driers, G4 Filter, Suction and Discharge piping, Internal power and Control wiring, Crankcase heaters, Infrared Humidifier, Heaters, HP/LP Cutouts, Power and Control contactors, water leak detectors and Other Electrical accessories. The Outdoor Condenser unit shall comprise of Condenser fans & motor, Condenser cooling coil (Copper coil with aluminum fins), Fan speed controller, Isolator switch. The unit shall be suitable for operation on 415 Volts, (+/-5%) 50 Hz, 3 Phase, 4 Wire AC supply. Each unit should be having individual display panel, which shall display date, time, actual & set values, operating conditions, signal faults, collective faults, limiting values and PAC wellness alarm / service alarm to reduce the down time and unit memory shall hold the 400 most recent events with ID number, time and date stamp for each event. The dimensions of the unit shall not be more than 1200 mm x 890mm x 1950mm (L x D x H) Team Mode feature for PAC units controller for synchronizing the Multiple No. of units to work as single system for all above units. Bidders are requested to visit the site before quoting to see the compatibility of the available space with the units being offered. Load sharing mode feature Cascading Effect Sequencing of above Units | 2.00 | EA | 0.00 | 1220000.00 | 3123200.00 | 1095000.00 | 2584200.00 | 2584200.00 | APEXINFRANET PVT LTD
4.00 | 10 Tr. Precision Air Conditioning Units Supply of Floor Mounted, Bottom discharge, Air Cooled DX type CRAC units for server room application, equipped with most advanced technology, guaranteeing precise control of Data Centers and server room. The units shall be selected on the basis of following parameters: i) 27 Deg C / 36% RH of return air ii) Supply air in between 15 - 17 Deg C iii) 45 Deg C of Design Ambient temperature iv) Precision Air-Conditioner will have green refrigerant (R407C/410A). v) Specific Power consumption shall be low as per site design conditions including compressor, evaporator fans and condensers The Indoor unit shall comprise of Digital Scroll Compressor, Fiberglass corrosion resistant EC fans, Evaporator DX Cooling Coil with hydrophilic coating, Microprocessor controllers, TXV, Driers, G4 Filter, Suction and Discharge piping, Internal power and Control wiring, Crankcase heaters, Infrared Humidifier, Heaters, HP/LP Cutouts, Power and Control contactors, water leak detectors and Other Electrical accessories. The Outdoor Condenser unit shall comprise of Condenser fans & motor, Condenser cooling coil (Copper coil with aluminum fins), Fan speed controller, Isolator switch. The unit shall be suitable for operation on 415 Volts, (+/-5%) 50 Hz, 3 Phase, 4 Wire AC supply. Each unit should be having individual display panel, which shall display date, time, actual & set values, operating conditions, signal faults, collective faults, limiting values and PAC wellness alarm / service alarm to reduce the down time and unit memory shall hold the 400 most recent events with ID number, time and date stamp for each event. The dimensions of the unit shall not be more than 1200 mm x 890mm x 1950mm (L x D x H) Team Mode feature for PAC units controller for synchronizing the Multiple No. of units to work as single system for all above units. Bidders are requested to visit the site before quoting to see the compatibility of the available space with the units being offered. Load sharing mode feature Cascading Effect Sequencing of above Units | 4.00 | EA | 0.00 | 1192000.00 | 6103040.00 | 998000.00 | 4710560.00 | 4710560.00 | APEXINFRANET PVT LTD
5.00 | INSTALLATION, ERECTION & COMMISSIONING OF 2 NOS. OF PAC UNITS. (13 Tr.)
6.00 | Installation & commissioning of Precision AC units comprising of | 2.00 | Nos. | 0.00 | 25000.00 | 59000.00 | 55000.00 | 129800.00 | 59000.00 | VOLKS ENERGIE PVT LTD
7.00 | Lifting, shifting & positioning of units to site with help of crane | 2.00 | Nos. | 0.00 | 4000.00 | 9440.00 | 15000.00 | 35400.00 | 9440.00 | VOLKS ENERGIE PVT LTD
8.00 | Commissioning of the system
9.00 | Indoor Unit | 2.00 | Nos. | 0.00 | 1917.00 | 4524.12 | 9000.00 | 21240.00 | 4524.12 | VOLKS ENERGIE PVT LTD
10.00 | Outdoor Unit Structure | 2.00 | Kgs | 0.00 | 200.00 | 472.00 | 9000.00 | 21240.00 | 472.00 | VOLKS ENERGIE PVT LTD
11.00 | Initial charge of R-410a refrigerant gas & oil. | 50.00 | Kgs | 0.00 | 750.00 | 44250.00 | 1400.00 | 82600.00 | 44250.00 | VOLKS ENERGIE PVT LTD
12.00 | Interconnecting Copper piping between indoor & outdoor unit. Copper piping will be duly insulated with in the AC space along with Tray (@30RMT/Ckt)
13.00 | Hot gas line | 30.00 | mtr | 0.00 | 810.00 | 28674.00 | 1400.00 | 49560.00 | 28674.00 | VOLKS ENERGIE PVT LTD
14.00 | Liquid line | 30.00 | mtr | 0.00 | 545.00 | 19293.00 | 1400.00 | 49560.00 | 19293.00 | VOLKS ENERGIE PVT LTD
15.00 | Interconnecting copper cabling between indoor & outdoor unit along with cable tray - 3C x 2.5 sqmm | 300.00 | mtr | 0.00 | 110.00 | 38940.00 | 325.00 | 115050.00 | 38940.00 | VOLKS ENERGIE PVT LTD
16.00 | Incoming Copper Cabling from Incoming Isolator to CRAC Unit (@5RMT/Unit) - 4C x 10 sqmm | 10.00 | mtr | 0.00 | 400.00 | 4720.00 | 1150.00 | 13570.00 | 4720.00 | VOLKS ENERGIE PVT LTD
17.00 | Condensate drain piping with CPVC pipes (@5RMT/Unit) | 20.00 | mtr | 0.00 | 413.00 | 9746.80 | 450.00 | 10620.00 | 9746.80 | VOLKS ENERGIE PVT LTD
18.00 | Humidifier water piping with CPVC pipes (@5RMT/Unit) | 20.00 | mtr | 0.00 | 271.00 | 6395.60 | 550.00 | 12980.00 | 6395.60 | VOLKS ENERGIE PVT LTD
19.00 | Extension piping kit | 2.00 | Nos. | 0.00 | 1000.00 | 2360.00 | 12000.00 | 28320.00 | 2360.00 | VOLKS ENERGIE PVT LTD
20.00 | Misc, Civil, Tile cutting and adjustment | 1.00 | LS | 0.00 | 5000.00 | 5900.00 | 15000.00 | 17700.00 | 5900.00 | VOLKS ENERGIE PVT LTD
21.00 | INSTALLATION, ERECTION & COMMISSIONING OF 4 NOS. OF PAC UNITS. (10 Tr.)
22.00 | Installation & commissioning of Precision AC units comprising of | 4.00 | Nos. | 0.00 | 22000.00 | 103840.00 | 45000.00 | 212400.00 | 103840.00 | VOLKS ENERGIE PVT LTD
23.00 | Lifting, shifting & positioning of units to site with help of crane | 4.00 | Nos. | 0.00 | 6000.00 | 28320.00 | 15000.00 | 70800.00 | 28320.00 | VOLKS ENERGIE PVT LTD
24.00 | Commissioning of the system
25.00 | Indoor Unit | 4.00 | Nos. | 0.00 | 2000.00 | 9440.00 | 9000.00 | 42480.00 | 9440.00 | VOLKS ENERGIE PVT LTD
26.00 | Outdoor Unit structure | 4.00 | Kgs | 0.00 | 200.00 | 944.00 | 9000.00 | 42480.00 | 944.00 | VOLKS ENERGIE PVT LTD
27.00 | Initial charge of R-410a refrigerant gas & oil. | 120.00 | Kgs | 0.00 | 750.00 | 106200.00 | 1400.00 | 198240.00 | 106200.00 | VOLKS ENERGIE PVT LTD
28.00 | Interconnecting Copper piping between indoor & outdoor unit. Copper piping will be duly insulated with in the AC space along with Tray (@30RMT/Ckt)
29.00 | Hot gas line | 160.00 | mtr | 0.00 | 810.00 | 152928.00 | 1400.00 | 264320.00 | 152928.00 | VOLKS ENERGIE PVT LTD
30.00 | Liquid line | 160.00 | mtr | 0.00 | 545.00 | 102896.00 | 1400.00 | 264320.00 | 102896.00 | VOLKS ENERGIE PVT LTD
31.00 | Interconnecting copper cabling between indoor & outdoor unit along with cable tray - 3C x 2.5 sq mm | 170.00 | mtr | 0.00 | 110.00 | 22066.00 | 325.00 | 65195.00 | 22066.00 | VOLKS ENERGIE PVT LTD
32.00 | Incoming Copper Cabling from Incoming Isolator to CRAC Unit (@5RMT/Unit) - 4C x 10 sqmm | 20.00 | mtr | 0.00 | 400.00 | 9440.00 | 1150.00 | 27140.00 | 9440.00 | VOLKS ENERGIE PVT LTD
33.00 | Condensate drain piping with CPVC pipes (@5RMT/Unit) | 20.00 | mtr | 0.00 | 415.00 | 9794.00 | 450.00 | 10620.00 | 9794.00 | VOLKS ENERGIE PVT LTD
34.00 | Humidifier water piping with CPVC pipes (@5RMT/Unit) | 20.00 | mtr | 0.00 | 271.00 | 6395.60 | 550.00 | 12980.00 | 6395.60 | VOLKS ENERGIE PVT LTD
35.00 | Extension piping kit | 4.00 | Nos. | 0.00 | 1000.00 | 4720.00 | 9000.00 | 42480.00 | 4720.00 | VOLKS ENERGIE PVT LTD
36.00 | Misc., Civil, Tile cutting and adjustment | 1.00 | LS | 0.00 | 12000.00 | 14160.00 | 15000.00 | 17700.00 | 14160.00 | VOLKS ENERGIE PVT LTD
37.00 | Cat (B) - Buy Back Exisiting PAC System Items
38.00 | BUY-BACK: BUY-BACK OF PRECISION ACs AS PER ANNEXURE G
39.00 | Buy back of the existing PAC System (Serial Number 90340130121) (8.5 TR) | 1.00 | No. | 0.00 | 40000.00 | -47200.00 | 10000.00 | -11800.00 | -47200.00 | VOLKS ENERGIE PVT LTD
40.00 | Buy back of the existing PAC System (Serial Number 50130128104) (7.9 TR) | 1.00 | No. | 0.00 | 40000.00 | -47200.00 | 10000.00 | -11800.00 | -47200.00 | VOLKS ENERGIE PVT LTD
41.00 | Buy back of the existing PAC System (Serial Number 50130128103) (8.5 TR) | 1.00 | No. | 0.00 | 40000.00 | -47200.00 | 10000.00 | -11800.00 | -47200.00 | VOLKS ENERGIE PVT LTD
42.00 | Buy back of the existing PAC System (Serial Number 50230128105) (7.9 TR) | 1.00 | No. | 0.00 | 40000.00 | -47200.00 | 10000.00 | -11800.00 | -47200.00 | VOLKS ENERGIE PVT LTD
43.00 | Buy back of the existing PAC System (9.95 TR) | 1.00 | No. | 0.00 | 40000.00 | -47200.00 | 10000.00 | -11800.00 | -47200.00 | VOLKS ENERGIE PVT LTD
44.00 | Buy back of the existing PAC System (9.95 TR) | 1.00 | No. | 0.00 | 40000.00 | -47200.00 | 10000.00 | -11800.00 | -47200.00 | VOLKS ENERGIE PVT LTD
| Total in Figures |  |  |  |  | 9747899.12 |  | 9082755.00
Lowest Amount Quoted BY: APEXINFRANET PVT LTD(9082755.00)

## BOQ Summary
BOQ Summary Details Tender Title: SITC OF PAC 13TR AND 10 TR UNDER BUYBACK Tender ID: 2022_GAIL_136993_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | APEXINFRANET PVT LTD | 9082755.00 | L1
| 2 | VOLKS ENERGIE PVT LTD | 9747899.12 | L2