## BoQ1
Government eProcurement System Created By: VINOD KUMAR BHAT Created Date/Time: 13-Feb-2023 05:24 PM Tender Title: IMPROVEMENT OF VENTILATION AND AIR QUALITY AT GAIL JUBIEE TOWER SECTOR-1 NOIDA Tender ID: 2022_GAIL_138778_1
Tender Inviting Authority: GAIL INDIA LIMITED, NOIDA
Name of Work:TENDER DOCUMENT FOR WORK FOR IMPROVEMENT OF VENTILATION AND AIR QUALITY AT GAIL JUBILEE TOWER, NOIDA
Contract No: GAIL/NOIDA/CNP/MAINT/22162 [NIC E-TENDER NO. 2022_GAIL_138778_1]
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | SNOWMEX ENGINEERS LIMITED(GSTN-07AAMCS8717P1ZF)
[5 empty] | Rate | Amount | L1 Amount | L1 Vendor
1.10 | TFAU WITH HEAT RECOVERY WHEEL (HR TFAU): Supply, Installation, Testing & Commissioning of Factory assembled/ modular Double Skin chilled water Floor Mounted type Treated Fresh Air Handling Units (TFAUs) complete with double skin (50mm) insulated with CFC free polyurethane foam (PUF) panels of 42 Kg/cum density sandwitched between 0.8 mm thick Alu Zinc Sheets, thermal break profile and canopy. Outer skin shall be precoated G.I. sheet. The control wiring and power wiring shall be in the scope of OEM AHU manufactuer and to be carried out at factory with terminations to Marshalling box. Food grade self adhesive coated EPDM gasket to be provided between panels and structure of the AHU to ensure the entire housing is airtight. The fresh air treatment units shall comprise of supply air segment (lower tier) and an extract air segment (upper tier) in double decker construction. The lower tier shall be complete with 50mm thick washable panel type pre-filter (MERV-8), EAC filter either with ESP & Activated Carbon Filter OR Ion-jet Filter, 6 bank chemical filter for Gx to G1 level of chemical filtration, heat recovery section complete with heat recovery wheel and associated motor, coil section with multi-rows deep chilled water cooling coil of copper tube & aluminium fin construction, insulated SS drain pan, copper header with "Copper to MS" adopter, and vibration isolation arrangement all complete as per the specifications. The unit shall be provided with built-in CE Certified Electronic Air Cleaner (EAC) with either ESP (Electro Static Precipitator) with Activated Carbon Filters OR Ion Jet Filters of approved make, with minimum 90% filtration efficiency for PM 10, PM 2.5 and PM 1. The electrical control box or high voltage box must be CE Certified and meet EU Safety Standards, and should have test certificates for EMI/EMC compatibility from a reputed International Laboratory - in order to avoid interference in IT/ LV equipment. The DC High Voltage power supply should be of approved make. Maximum allowable Ozone generation shall be 50 ppb, in line with EU Directive 2008/50/EU. The upper tier shall be complete with 50mm thick washable panel type pre-filter (MERV-8). Both tiers shall be supplied with HR TFAU blower fans with wall mounted EC PLUG Fans complete with BLDC motor & controller, fan wheel rotor mounted, potentiometer for speed control. The fan shall be selected for appropriate static pressure pressure drop across the pre-filters, EAC filter etc. The fan shall be suitable for BMS connectivity. The Single or multiple fans shall be considered depending upon the capacity of the units (as mentioned below). TFAU manufacturer should supply cover plate for Fans in sufficient quantity for maintanance purpose. EC fan incoming supply to be terminated with MCB/ MCCB and shall be included in the power terminal box for electrical connection of EC fans and should be facotry fitted on the TFAUs. Potentio-meter shall be provided in the marshalling box for manual operation of EC fans. Relay for AUTO/MANUAL operation should be a part of Marshalling box supplied by the AHU manufacturer. Face velocity across Filters and Heat Recovery Wheel shall not exceed 500 FPM (2.54 MPS) and 800 FPM (4 MPS) respectively, and TFAUs shall be selected as per Schedule of Air Handling Units drawn under APPENDIX VII. Fan outlet velocity shall not exceed 2000 FPM (10.2 MPS). The unit shall be provided mixing box having access doors/ panels for fresh air/ extract air for duct termination on both tiers as per "Approved for Construction" - Shop Drawings. TFAUs shall follow the design parameters as mentioned below: (CONTD. AT S.NO.1.2 BELOW) | 1.00 | NUMBER |  | 3964779.00 | 4678439.22 | 4678439.22 | SNOWMEX ENGINEERS LIMITED
1.20 | HR TFAU controller with display should be mounted on the Marshalling box and should have RS 485 output to be integrated to BMS. The AHU controller should be compatible with Modbus protocol. All control wiring and integration should be done at factory level. The unit shall be provided with well calibrated external sensor/s of approved make for PM 1/ 2.5 etc. and shall be factory wired to each unit's built-in PLC. The PLC shall be BMS compatible with BACnet/ Modbus output towards soft integration (maximum 10 IO points), the controller shall generate alarms, monitor all above mentioned IAQ parameters, and control fan speed & on/off etc. The unit should meet all specified IAQ parameters, and maybe subjected to 3rd Party IAQ Testing. HR TFAU should have marine lamp including adequately rated CFL bulb inside the AHU Cabinet. AHU inspection door should have View Window with perfectly sealed gaksets on either side to ensure air tightness. All HR TFAUs shall be provided with door limit switch and also door safety GI guard. All internals shall be powder coated for corrosion resistance. The unit shall be provided mixing box having access doors/ panels for fresh air duct termination as per "Approved for Construction" - Shop Drawings. TFAU control panel should have NO/NC contacts for AFAS Integration. TFAUs shall be suitable for BMS Integration and EC Fan speed modulatiion through DPS. TFAUs shall follow the design parameters as mentioned below: Lower Tier: i) Supply Air Quantity: 15000 Cfm (two fans 50% capacity each) ii) Static Pressure : 120 mm WG iii) Motor Rating : 2x10 HP Upper Tier i) Supply Air Quantity: 12000 Cfm (two fans 50% capacity each) ii) Static Pressure : 70 mm WG iii) Motor Rating : 2x7.5 HP HR TFAU as described above. Note: HRW minimum 75% efficeincy. Motor Rating is only indicative. The work also includes de-installation/Dismantling and Lifting/Shifting of the New/Old/Existing complete TFA unit including tools, tackles and labour charges etc.(As per SCC/SOW and directions of EIC).
2.00 | CHILLED WATER PIPING (CHW): Providing and fixing in position MS heavy class pipes, controls, valves & fittings, and all accessories required to make the FATU fully functional. Quoted price shall be inclusive of insulation and weather-proof treatment as required for the complete chilled water supply and return network, and requisite hydronic balancing. (As per SCC/SOW and directions of EIC). | 1.00 | LUMPSUM |  | 242373.00 | 286000.14 | 286000.14 | SNOWMEX ENGINEERS LIMITED
3.00 | AIR DISTRIBUTION
3.10 | Ductwork: Conventional Site Fabricated Ductwork: Supply, Fabrication, Installation and Testing of sheet metal ducts complete with Slip-on/ TDF flanges and fire retardant gaskets as per specifications, threaded rod suspension arrangement, GI perforated 'C' channel supports etc. in accordance with the approved shop drawings and specifications. The ducts shall be fabricated on site by HVAC vendor as per specifications. The joints shall be with least leak and shall be pressure tested. All ducts shall undergo deep cleaning process to remove construction dust prior to testing & commisioning. Quoted price shall be inclusive of insulation and weather-proof treatment as required for the complete treated fresh air supply and return network. (As per SCC/SOW and directions of EIC). | 1.00 | LUMPSUM |  | 135000.00 | 159300.00 | 159300.00 | SNOWMEX ENGINEERS LIMITED
3.20 | Complete Air Distribution System Balancing for Treated Fresh Air System for all floors. Quoted price shall be inclusive of air balancing readings through capture hood, any additional manual VCDs required etc. to completely balance the system. Exisitng DCV to be disabled to allow for more ventilation air to the office. (As per SCC/SOW and directions of EIC). | 1.00 | LUMPSUM |  | 481355.00 | 567998.90 | 567998.90 | SNOWMEX ENGINEERS LIMITED
| Total in Figures |  |  |  |  | 5691738.26
Lowest Amount Quoted BY: SNOWMEX ENGINEERS LIMITED(5691738.26)

## BOQ Summary
BOQ Summary Details Tender Title: IMPROVEMENT OF VENTILATION AND AIR QUALITY AT GAIL JUBIEE TOWER SECTOR-1 NOIDA Tender ID: 2022_GAIL_138778_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | SNOWMEX ENGINEERS LIMITED | 5691738.26 | L1