## BoQ1
Government eProcurement System Created By: Ajay Kumar Deswal Created Date/Time: 03-Mar-2023 11:27 AM Tender Title: Replacement/Retrofitting of ACBs in existing LT panels at Rajiv Gandhi Bhawan, New Delhi. Tender ID: 2023_AAI_140462_1
Tender Inviting Authority: Jt. Gen. Mgr. (Engg. – Elect)- IMU, AAI, CHQ, R.G. Bhawan, New Delhi-110003
Name of Work: Replacement/Retrofitting of ACBs in existing LT panels at Rajiv Gandhi Bhawan, New Delhi.
Contract No - Tender ID- 2023_AAI_140462_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Elbe Engineering Services(GSTN-07ACVPR5041D2ZD) |  | Avon Electricals(GSTN-07AAPFA2943K1Z6) |  | vk sam engineering(GSTN-33AMZPS4037L1ZA) |  | C AND S ELECTRIC LTD(GSTN-NA) |  | REGENT SWITCHGEAR(GSTN-NA) |  | RISHA CONTROL ENGINEERS PRIVATE LIMITED(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Providing and retrofitting of following rating FP EDO ACBs installed in existing LT Panel at substation with all suitable accessories, pre-fabricated (factory cut) Aluminum Bus Bar/links to cater connections with existing Bus-bar, Bus – Bar supports, replacement of Panel front door made of 2 mm thick CRCA sheet steel of ACB feeder along with replacement of Multifunction meter, LED indication lamps, sleeves, gasket, suitable modification in control wiring etc. including testing & commissioning of system and dismantling of existing ACBs, complete as per technical specifications and to the entire satisfaction of Engineer in charge. The specifications of ACBs are as under:- i) Microprocessor release. ii) Fault breaking capacity 65/50 KA (Ics=lcu=Icw for 1.0 secs). iii) Electrical Draw Out Motorized operated, fitted with interlocked door, automatic safety shutters, mechanical ON / OFF and service/ test/ isolated position indicators, operational counter and frame earthing contact. iv) Conforming to IEC/IS-60947-2 1993 as amended up-to-date. v) Independent Electrical & manual spring closing mechanism. vi) Microprocessor release for adjustable over current (Phase & neutral), earth fault & short circuit protection. vii) Shunt trip coil & under voltage coil suitable with 24V DC / 220V AC supply, Breaker Control Switch - 16A, Test terminal block set, circuits as per standard practice, auxiliary contacts (minimum 4NO+4NC) for positive interlocking of the breakers, necessary interlocking with existing PLC/ auto controls. viii) All protection i/e Earth fault, Under/Over Voltage, Under/Over Frequency, Current & Voltage Unbalance, etc. ix) Real-time stamping, On-screen display of measurements, Current : phase / neutral / earth, average, max & % loading, Voltage : Phase, Line & Average. Power and Energy : active, reactive & total, Frequency, Power Factor, Maximum Demand, temperature and with communication port facility etc. Complete as per technical specifications.
1.10 | 2500A (65 KA) | 3.00 | Job | 10.00 | 423730.00 | 1271190.00 | 250720.00 | 752160.00 | 370000.00 | 1110000.00 | 345600.00 | 1036800.00 | 260126.00 | 780378.00 | 416000.00 | 1248000.00 | 752160.00 | Avon Electricals
1.20 | 1250A (50 KA) | 5.00 | Job | 10.00 | 249600.00 | 1248000.00 | 163000.00 | 815000.00 | 286000.00 | 1430000.00 | 302500.00 | 1512500.00 | 194091.00 | 970455.00 | 260000.00 | 1300000.00 | 815000.00 | Avon Electricals
2.00 | Providing and retrofitting of following rating FP EDO ACBs installed in existing LT Panel at substation with all suitable accessories, pre-fabricated (factory cut) Aluminum Bus Bar/links to cater connections with existing Bus-bar, Bus – Bar supports, replacement of Panel front door made of 2 mm thick CRCA sheet steel of ACB feeder along with replacement of LED indication lamps, sleeves, gasket, suitable modification in control wiring etc. including testing & commissioning of system and dismantling of existing ACBs, complete as per technical specifications and to the entire satisfaction of Engineer in charge. The specifications of ACBs are as under:- i) Microprocessor release. ii) Fault breaking capacity 65/50 KA (Ics=lcu=Icw for 1.0 secs). iii) Electrical Draw Out Motorized operated, fitted with interlocked door, automatic safety shutters, mechanical ON / OFF and service/ test/ isolated position indicators, operational counter and frame earthing contact. iv) Conforming to IEC/IS-60947-2 1993 as amended up-to-date. v) Independent Electrical & manual spring closing mechanism. vi) Microprocessor release for adjustable over current (Phase & neutral), earth fault & short circuit protection. vii) Shunt trip coil & under voltage coil suitable with 24V DC / 220V AC supply, Breaker Control Switch - 16A, Test terminal block set, circuits as per standard practice, auxiliary contacts (minimum 4NO+4NC) for positive interlocking of the breakers, necessary interlocking with existing PLC/ auto controls. viii) All protection i/e Earth fault, Current Unbalance, etc. ix) Real-time stamping, On-screen display of measurements of Current : phase / neutral / earth, average, max & % loading, temperature and with communication port facility etc. Complete as per technical specifications.
2.10 | 2500A (65 KA) | 4.00 | Job | 10.00 | 348460.00 | 1393840.00 | 250720.00 | 1002880.00 | 370000.00 | 1480000.00 | 304000.00 | 1216000.00 | 248070.00 | 992280.00 | 416000.00 | 1664000.00 | 992280.00 | REGENT SWITCHGEAR
2.20 | 1250A (50 KA) | 12.00 | Job | 10.00 | 270600.00 | 3247200.00 | 163000.00 | 1956000.00 | 286000.00 | 3432000.00 | 405000.00 | 4860000.00 | 175528.00 | 2106336.00 | 260000.00 | 3120000.00 | 1956000.00 | Avon Electricals
2.30 | 1000A (50 KA) | 2.00 | Job | 10.00 | 230290.00 | 460580.00 | 154542.00 | 309084.00 | 277000.00 | 554000.00 | 40000.00 | 80000.00 | 167418.00 | 334836.00 | 225000.00 | 450000.00 | 80000.00 | C AND S ELECTRIC LTD
2.40 | 800A (50 KA) | 3.00 | Job | 10.00 | 258770.00 | 776310.00 | 147144.00 | 441432.00 | 273500.00 | 820500.00 | 35000.00 | 105000.00 | 162893.00 | 488679.00 | 215000.00 | 645000.00 | 105000.00 | C AND S ELECTRIC LTD
| Total in Figures |  |  |  |  | 8397120.00 |  | 5276556.00 |  | 8826500.00 |  | 8810300.00 |  | 5672964.00 |  | 8427000.00
Lowest Amount Quoted BY: Avon Electricals(5276556.00)

## BOQ Summary
BOQ Summary Details Tender Title: Replacement/Retrofitting of ACBs in existing LT panels at Rajiv Gandhi Bhawan, New Delhi. Tender ID: 2023_AAI_140462_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Avon Electricals | 5276556.00 | L1
| 2 | REGENT SWITCHGEAR | 5672964.00 | L2
| 3 | Elbe Engineering Services | 8397120.00 | L3
| 4 | RISHA CONTROL ENGINEERS PRIVATE LIMITED | 8427000.00 | L4
| 5 | C AND S ELECTRIC LTD | 8810300.00 | L5
| 6 | vk sam engineering | 8826500.00 | L6