## BoQ1
Government eProcurement System Created By: Ravindra Kumar Created Date/Time: 06-Feb-2023 11:39 AM Tender Title: Electrical Substation Work at Moradabad Airport Tender ID: 2023_AAI_140789_1
Tender Inviting Authority: Airports Authority of India
Name of Work: Electrical Substation work at Moradabad Airport.
Contract No:
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Aditya Techno Products Private Limited(GSTN-09AAGCA0910L1ZS) |  | Mona Generator Services Pvt. Ltd.(GSTN-07AAFCM4263P1ZZ)
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | MV PANELS Totally Type Tested Assemblies (TTA) Design, manufacture , supply , assembly at site , installation, testing and commissioning of following cubical type panels Totally Type Tested (TTA) made of 2 mm CRCA sheet, base channel, doors & partitions complete with, Air Circuit Breaker, Moulded Case Circuit Breakers, meters, indicating lamps, current transformer etc. complete in all respects, insulated aluminium bus bars with heat shrinkable PVC sleeve in suitable bus bar chambers, interconnection,bus bar shrouds at joints, wiring, name plate, danger plate, earth bus etc. & comprising of compartments with hinged door for each feeder & its accessories, cable alley with hinged doors, bus chamber with bolted door etc. The panel shall be dust & vermin proof construction with rubber gasket and powder coated . The panel shall be free standing floor mounted type as per relevant drawing. The panel shall be completely modular and compartmentalised with Form 4 B Seperation as per IEC 61439. The panel shall be manufactured as per IEC 61439.
1.01 | Note:- i) All MCCBS shall be with Extended type Front door operating handle, Phase Spreaders & Phase Barriers. ii) Metering CT's burden shall be 15VA & accuracy class 1.0. iii) CT's shall be "CAST RESIN" type . iv) MCCB's up to and including 250 Amp shall be with adjustable thermal-magnetic release for over current and short circuit protection adjustable from 80-100%. MCCB above 250 amp shall be with Microprocessor based release for over current and short circuit protection. All incoming MCCBs above 250 A will be provided additionally with earth falut protection. Bus-coupler MCCB may be without protection. v) All indication lights shall be LED type. vi) All meter shall be "DIGITAL" type. vii) Rated Short time withstand current of all ACB's are Icw for one second. viii) Breaking Capacity of all MCCB's are Ics Service Breaking Capacity ix) Degree of Protection shall be IP:42 .For indoor aplication. x) Panel Manufacturer should have Type Test Certificates for Short Time withstand current test of 50KA for 1.0 Sec from CPRI. Bhopal / Bangalore. xii) "ON" Indicating lamp shall be provided for all 3 phase MCCB out going feeders . xiii) Control SP MCB's of 2A Rating shall be provided for each metering circuit. xiv) 20% spare control terminal to be provided. xv) Live parts shall not be accessible after opening the door, Transparent acrylic sheet to be provided to cover the same & busbar joints section shall be covered with PVC shrouds. xvi) All MFM will have M-Bus conectvity over 485 port for BMS integration. xvii) All EDO breakers shall have spare contacts on the rear of the panel for BMS conectivity. xviii) The panel shall be suitable for BMS Integeration.
1.02 | Main MV Panel . i. Incomer for Transforrmers: Two ( 2) Nos 800 Amp 50 kA , Four pole , EDO ACB, with ON/OFF/TRIP indication lamp and TNC control switch, etc complete as required and as per approved SLD of following ratings. Each Transformers supply breaker shall be provided with the following: One (1) No. Digital Multifunction meter suitable for measurement of voltage, currents, Power Factor, Frequency, Power & Energy with one set (3 Nos.) of CTs of ratio 800/5A Class 1.0, 15VA. One set ( 3 nos.) phase indication lamps with control MCB. One (1) No Microprocessor based relay for short circuit, over current and earth fault protection. One (1) No. of C.L. 1.0, 15VA, CT for input to APFC relay. One (1) No. Reverse Power Relay One (1) No. Under voltage relay. One (1) No. Over voltage relay. One (1) No Trip circuit supervision relay One (1) No Master trip relay Auxiliary relay as required shall be provided with in the scope of item.
1.03 | ii. Incomer from DG Sets : Two (2) Nos 800 Amp, 50 kA, Four pole , EDO ACB, with ON/OFF/TRIP indication lamp and TNC control switch, complete as required and as per approved SLD. Each DG supply breaker shall be provided with the following: One (1) No. Multifunction meter suitable for measurement of voltage, currents, Power Factor, Frequency,Power , Energy, with one (1) set of CTs (3 Nos.) 800/5A Class 1.0, 15VA . One (1) Set of indication lamps for ON/OFF/ Trip/ trip circuit healthy. One (1) Set of Phase indication lamps with control MCB. One (1) Microprocessor based relay for short circuit, over current and earth fault protection . One (1) No. Reverse Power Relay equivalent. One (1) No. Under Voltage relay. One (1) No. Over Voltage relay. One (1) No Trip circuit supervision relay One (1) No Master trip relay One (1) No Auxiliary relay as required shall be provided with in the scope of item. Note:- The transformer and DG Set incomers shall be suitably interlocked to operate automatically for transfer of load from normal to DG Supply and vise-versa. This will be controlled by PLC Panel of DG Synchronization Panel.
1.04 | iii. Bus Coupler : One (1) Nos. 800A , 50 KA, Four pole , EDO ACB, with ON/OFF indication lamp and TNC control switch, Under Voltage & shunt trip release, anti pumping protection etc. complete as required . iv. Busbar : 1200A , 50 kA TP + N Al. Busbar insulated with heat shrinkable sleeves and shall be colour coded. The neutral busbar shall be 50% rated. Separate earth busbar of sutaible rating shall be provided on the rear bottom of the panel.
1.05 | vi. Outgoings : Section- I: One (1) No. 800A, 50 kA, 4P ACB EDO with Microprocessor based release for short circuit, over current protection . Two (3) Nos. 200A, 35 kA, 4P MCCB with variable thermal magnetic for short circuit, over current protection. Two (2) Nos. 63A, 35 kA, 4P MCB Two (2) Nos. 32A, 35 kA, 4P MCB Section - II One (1) No. 800A, 50 kA, 4P ACB EDO with Microprocessor based release for short circuit, over current protection. Two (3) Nos. 200A, 35 kA, 4P MCCB with variable thermal magnetic for short circuit, over current protection. Two (2) Nos. 63A, 35 kA, 4P MCB Two (2) Nos. 32A, 35 kA, 4P MCB NOTE:- 1) All out going feeders will be provided with MFM with RS 485 connectivity, CTs of suitable range and ON/OFF indicating lamps . 2) Incoming and Out going feeders will be with Sandwiched Bus Trunking and UG Cables as per Schematics 3) PLC based interlocking will be provided in all incomings and bus-couplers. (Rate Should be quoted for the complete item S.N. 1, 1.01,1.02,1.03,1.04 & 1.05 Here) | 1.00 | Set |  | 3150000.00 | 3150000.00 | 2085402.00 | 2085402.00 | 2085402.00 | Mona Generator Services Pvt. Ltd.
2.00 | D.G. Set - Radiator Cooled (Silent Type ) Supplying, Shifting, installation, testing and commissioning of 3 phase 415 volts 50 Hz, 1500 RPM , radiator cooled with acoustic enclosure Diesel Generator Set of following (Prime Power) ratings. The engine shall be complete with following accessories. The alternator shall be self excited, self regulated, brush-less and continuously rated for below mentioned capacity at 0.8 P.F., 3 phase 415 volts, 50 Hz, 4 wire system and shall be provided with static excitation unit. The DG Sets shall be subjected to all necessary tests as per relevant standards, technical specifications and tender conditions with all labour and materials, as per approved drawings, specifications of this tender and directions of Engineer-in-Charge. Diesel Engine Diesel Engine 4 stroke radiator cooled, electric start, of suitable BHP at 1500 rpm suitable for output of alternator, capable of taking 10% over loading for one hour after 12 hours of continuous operation. The engine will be fitted with class A1 electronic governor and complete with all standard accessories and as per detailed specifications (as per BS:5514). The engine shall not be derated up to 50 deg C temperature. Engine mounted instrument panel fitted with and having digital/Analog display for following:- Start-stop switch Water temperature indication Lubrication oil pressure indication Battery charging indication RPM indication Over speed trip indication Low lub, oil trip indication Engine Hours indication Alternator Synchronous alternator rated 250 KVA at 415 volts , 3 phase, 50 Hz, AC supply with 0.8 lagging power factor. The alternator shall have SPDP enclousre, brushless, continuous duty, self-excited and self-regulated through AVR conforming to IS : 4722/BS 2613 or BS:500 suitable for tropical conditions and with class-F/H insulation. Alternator shall be suitable for connection with conventional type aluminium bus duct of required capacity. The alternator shall not be derated up to 50 deg C. .
2.01 | Base Frame Both the engine and alternator shall be mounted on suitable base frame made of MS channel with necessary reinforcement which shall be installed on suitable RCC foundation and vibration isolation arrangement as per recommendations of manufacturer. The DG set shall be installed at ground level. Fuel Tank Daily service fuel tank built in the accoustics enclosure of suitable capacity fabricated out of MS sheet complete with all standard accessories and fuel piping between fuel tank and diesel engine with pipes of suitable dia. Complete with valves, level indications & accessories as required as per specifications. In addition one fuel tank of 990 Liters capacity made of 4 mm thick MS sheet will be installed at 1.5 m height above ground level on MS structure.This tank will be connected with day tank provided inside the enclosure of DG Sets. Tank shall have 450 mm ID manhole cover, flanged connection for inlet, outlet, drain, overflow, vent and provision for level controller. This tank will be complete with all accessories, level indication, connecting pipe line and protection from weather with suitable canopy arrangment. Exhaust system Dry exhaust mainfold with residential type silencer . Starting system: 12V/24V DC starting system comprising of starter motors: complete with suitable nos. and AH of batteries as recommended by manufacturer for at least three cranking attempts.
2.02 | Accoustic Enclosure Accoustic and weather proof enclosure suitable for the DG Set with arrangement for fresh air intake for cooling of the engine & alternator, extraction, discharging hot air into the atmosphere as per specifications & CPCB norms. The enclosure shall be provided with fans at the rear to ensure that adequate cooling air is made available to the engine and the temperature within the enclosure is limited to 5 deg C above ambient . The opeartion of the fans shall be fully automatic as per specification. Control Panel Control Panel - Suitable for auto starting and auto operation of DG set and with protections for engine and alternator. The panel will sense normal supply and control operation of DG Sets and breakers. Manual fuel filling arrangment includinmg Hand operated Gear pump, barrel, suitable flexible pipe etc shall be provided . The DG Sets shall be in a postion to take up full load within 15 Secs of Power failure. DG Set Rating as follows: 250 KVA ( Prime Power) Radiator Cooled DG Set with Acoustic enclosure. (Rate Should be quoted for the complete item S.N. 2, 2.01, & 2.02 Here) | 1.00 | Set |  | 1850000.00 | 1850000.00 | 1983248.00 | 1983248.00 | 1850000.00 | Aditya Techno Products Private Limited
3.00 | Design, supply, erection, testing and commissioning of exhaust piping of 150 mm dia size MS B Class exhaust pipes, SS belwo, bends, silencer insulation with welding joint including bends, clamps, dash fastener, flanges, nuts, bolts, insulation of exhaust pipe using 50 mm thick loosely bound resin mattress/mineral wool/rock wool density not less than 120 kg/mtr cube, wire chicken mesh over insulation and cladding aluminium sheet of 0.6 mm thick etc complete as required and as per specifications. | 10.00 | Mtr |  | 3737.00 | 37370.00 | 5200.00 | 52000.00 | 37370.00 | Aditya Techno Products Private Limited
4.00 | Design, supply & fixing of self supporting structure sutaible for pipes for exhaust of DG sets complete as required. | 250.00 | Kg |  | 136.00 | 34000.00 | 105.00 | 26250.00 | 26250.00 | Mona Generator Services Pvt. Ltd.
5.00 | Providing and laying in position cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) in foundation of pump, DG set etc including form work etc as required. | 5.00 | Cum |  | 7781.00 | 38905.00 | 7500.00 | 37500.00 | 37500.00 | Mona Generator Services Pvt. Ltd.
6.01 | Perforated Type Cable Trays (Hot Dipped Galvanized Iron Cable Tray) Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray (galvanisation thickness not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc. as required. a. 100 mm width X 50 mm depth X 1.6 mm thickness | 15.00 | RM |  | 520.00 | 7800.00 | 400.00 | 6000.00 | 6000.00 | Mona Generator Services Pvt. Ltd.
6.02 | b. 300 mm width X 50 mm depth X 1.6 mm thickness | 5.00 | RM |  | 966.00 | 4830.00 | 1250.00 | 6250.00 | 4830.00 | Aditya Techno Products Private Limited
7.00 | Supply of Indoor type air cooled constant current regulator of micro processor controlled, thristor type suitable for operation on 230/415 volts, 50Hz input AC supply with 6.6A output having 5 steps variation of current output and able to communicate with PC or PLC controlled system, with digital output ammeter (0-10A), overcurrent, overvoltage, open circuit and earth fault protection and earth leakage meter, two stage earth leakage detector, positive back indication equipment's, individual lamp control and monitoring system module, hours run counter, LCD display, complete as required for the following rating and confirm to specifications enclosed.should have proviion of MAFI compitability 4 kw | 1.00 | Each |  | 254964.00 | 254964.00 | 240000.00 | 240000.00 | 240000.00 | Mona Generator Services Pvt. Ltd.
8.00 | Installation, testing & commissioning of 4 KW microprocessor controlled CCRs including providing earth connection with GI strip of size 25mm x 5mm, all necessary arrangement, end termination with plug and recepticle etc. for commissioning of CCR etc. as required. | 1.00 | Job |  | 30385.00 | 30385.00 | 40000.00 | 40000.00 | 30385.00 | Aditya Techno Products Private Limited
9.01 | Supply of following size of 1.1 KV grade, ARMOURED,XLPE insulated PVC sheated Aluminium conductor cable confirming to IS: 7098 part -I amended upto date. A. 3.5x150 Sqmm | 200.00 | RM |  | 700.00 | 140000.00 | 565.00 | 113000.00 | 113000.00 | Mona Generator Services Pvt. Ltd.
9.02 | B. 4x25 Sqmm | 100.00 | RM |  | 187.00 | 18700.00 | 156.00 | 15600.00 | 15600.00 | Mona Generator Services Pvt. Ltd.
9.03 | C. 4x10 Sqmm | 200.00 | RM |  | 128.00 | 25600.00 | 107.00 | 21400.00 | 21400.00 | Mona Generator Services Pvt. Ltd.
10.01 | Laying of one number PVC insulated and PVC sheathed/ XLPE power cable 1.1 KV grade of following size in the existing RCC/HUME/METAL/HDPE Pipe as required. A. Upto 35 Sqmm | 200.00 | RM |  | 36.00 | 7200.00 | 30.00 | 6000.00 | 6000.00 | Mona Generator Services Pvt. Ltd.
10.02 | B. Above 95 Sqmm and upto 185sqmm | 200.00 | RM |  | 91.00 | 18200.00 | 60.00 | 12000.00 | 12000.00 | Mona Generator Services Pvt. Ltd.
10.03 | C. Above 185 Sqmm and upto 400 Sqmm | 30.00 | RM |  | 146.00 | 4380.00 | 100.00 | 3000.00 | 3000.00 | Mona Generator Services Pvt. Ltd.
11.01 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. A. 3.5x150 Sqmm | 8.00 | SET |  | 1052.00 | 8416.00 | 650.00 | 5200.00 | 5200.00 | Mona Generator Services Pvt. Ltd.
11.02 | 3.5x300 Sqmm | 3.00 | SET |  | 1919.00 | 5757.00 | 1450.00 | 4350.00 | 4350.00 | Mona Generator Services Pvt. Ltd.
11.03 | B. 4x10 Sqmm | 4.00 | SET |  | 271.00 | 1084.00 | 400.00 | 1600.00 | 1084.00 | Aditya Techno Products Private Limited
11.04 | C. 4x25 Sqmm | 4.00 | SET |  | 340.00 | 1360.00 | 300.00 | 1200.00 | 1200.00 | Mona Generator Services Pvt. Ltd.
12.00 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 Meter long etc. with charcoal/ coke and salt as required. | 2.00 | Each |  | 18871.00 | 37742.00 | 9900.00 | 19800.00 | 19800.00 | Mona Generator Services Pvt. Ltd.
13.00 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 Meter long etc. with charcoal/ coke and salt as required. | 4.00 | Each |  | 11408.00 | 45632.00 | 7000.00 | 28000.00 | 28000.00 | Mona Generator Services Pvt. Ltd.
14.00 | Providing and fixing 25mm x 5mm copper strip on surface or in recess for connections etc as required. | 20.00 | RM |  | 1134.00 | 22680.00 | 950.00 | 19000.00 | 19000.00 | Mona Generator Services Pvt. Ltd.
15.00 | Providing and fixing 25mm x 5mm GI strip on surface or in recess for connections etc as required. | 50.00 | RM |  | 136.00 | 6800.00 | 180.00 | 9000.00 | 6800.00 | Aditya Techno Products Private Limited
16.00 | Providing and fixing 50mm x 5mm GI strip on surface or in recess for connections etc as required. | 30.00 | RM |  | 285.00 | 8550.00 | 180.00 | 5400.00 | 5400.00 | Mona Generator Services Pvt. Ltd.
17.00 | Supply and laying 80 mm dia medium class GI pipe direct in ground including execavation existing pavement size of 75cm (depth), and refilling etc as required. | 20.00 | RM |  | 1132.00 | 22640.00 | 790.00 | 15800.00 | 15800.00 | Mona Generator Services Pvt. Ltd.
18.00 | Execution of works as per requirement of site from CPWD schedule of rates (DSR 2018 E&M) as per CPWD specifications complete as required. [Total amount of Rs. 1,00,000 (excluding GST) is kept for DSR items 2018 E&M.] Note : Rate of DSR items shall be quoted against total amount of Rs. 1,00,000.00(One Lakh) in figures excluding GST which shall be converted in the percentage (above/below) and rate of DSR items shall be taken exclusive of GST(basic rate) on which payment shall be made considering percentage (above/below) rate quoted against Rs. 1,00,000.00. | 1.00 | Job |  | 139905.00 | 139905.00 | 100000.00 | 100000.00 | 100000.00 | Mona Generator Services Pvt. Ltd.
| Total in Figures |  |  |  |  | 5922900.00 |  | 4857000.00
Lowest Amount Quoted BY: Mona Generator Services Pvt. Ltd.(4857000.00)

## BOQ Summary
BOQ Summary Details Tender Title: Electrical Substation Work at Moradabad Airport Tender ID: 2023_AAI_140789_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Mona Generator Services Pvt. Ltd. | 4857000.00 | L1
| 2 | Aditya Techno Products Private Limited | 5922900.00 | L2