## BoQ1
Government eProcurement System Created By: KAMBLE TANAJI Created Date/Time: 20-Mar-2023 06:05 PM Tender Title: Provision of kitchen exhaust system and providing of fire rated painting and fire sealants to existing fire evacuation /ventilation ducts. Tender ID: 2023_AAI_144148_1
Tender Inviting Authority: AGM (E-E)-I, AAI, PUNE AIRPORT, PUNE 411032
Name of Work: Construction of New Integrated Passenger Terminal Building, Reconstruction of Old Terminal Building, Modification of Existing expanded Terminal Building at Civil Enclave Pune Airport, Pune. Sub Head: Provision of kitchen exhaust system and providing of fire rated painting and fire sealants to existing fire excavation /ventilation ducts
Contract No: 2023_AAI_144148
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Bharti Refrigeration Works(GSTN-06AEMPB0002P2ZS) |  | Surendra Infrastructure Pvt. Ltd.(GSTN-19AAJCS7963C1ZY)
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply, installation, testing and commissioning of Fire Rated rectangular factory fabricated 16G Mild Steel kitchen exhaust ducts, welded construction with transverse joints having MS structural steel (TDF not allowed) complete with gaskets, supports, seismic support and all other accessories as required suitable for 50 mm wg external static pressure as per the technical specification. The duct shall be provided with fire rated coating and rockwool insulation of density 105 kg/m3 with aluminum foil, 50mm thick suitable for 2 hours fire rating in the terminal building including repair / re-installation of false ceiling, wall opening and making good etc complete as required. | 325.00 | Sqm | 100.00 | 4394.00 | 1428050.00 | 1937.00 | 629525.00 | 629525.00 | Surendra Infrastructure Pvt. Ltd.
2.00 | Supply and providing of fire rated coating suitable for 2 hours fire rating as per BS 476 part 24, fire sealant on the joints etc on existing HVAC / ventilation/exhaust ducts installed in terminal building including repair / re-installation of false ceiling, etc making good etc complete as required. | 8300.00 | Sqm |  | 1815.00 | 15064500.00 | 1850.00 | 15355000.00 | 15064500.00 | Bharti Refrigeration Works
3.00 | Supply, Installation, Testing and Commissioning of dry Scrubber each comprising of extract air intake section, electrostatic precipitation technology, dry type air cleaner to remove oil, smoke and fumes from exhaust air, with auto wash system, adsorber module etc as per the Specifications. The Unit shall comprise of: a.) Electrostatic section shall be made of 16 gauge galvanized sheet, high bake epoxy powder coated, washable type aluminium mesh filters, stainless steel spiked ionizers to create high voltage DC field, aluminium collector plates which should be alternatively charged positive and negative with large collecting area with minimum 14.13" deep cell, to work as magnet for charged smoke and oil particles. Average efficiency of 90-95% in single pass as per ASHRAE test method. Electrostatic Precipitator should be able to charge particles from 0.01 micron to 10 microns through solid state power supply. Collector cell should be of permanent type and incorporate slide out facility for easy removal for cleaning. Power supplies shall be 100% solid state UL Listed. Module of capacity 3900 CFM & above shall be equipped with Pulse width modulating (PWM). The system should be fitted with interlock switch for safety .The units should be BMS compatible for Run, Wash, Fault feedback, dry contact point. The system should allow connection to a fan section to achieve not more than 650 FPM velocity across the air cleaner. The units shall be with Auto Wash system including pump motor set, tank different wash and having detergent wash, soak, rinse, fan force dry cycles using Programmable Logic Controller (PLC). To re-energize the air cleaning system after the wash system has completed a remote mounted Sleep Mode Reset Switch (momentary contact push button type) shall be supplied to be installed at the kitchen or shall be reenergized through Building Management System. The units shall also be provided with V Shaped Adsorber Module. The system shall be per specification. Operating Voltage : 220V, 50 Hz Ionizing Voltage : 12.0 to 13 KVDC Collector Cell Voltage : 6 to 6.5 KVDC b.) Fan section shall comprise of double skinned panels of 25±2 mm thick and shall be made of 0.6mm Pre-coated GSS on outside and 0.6mm Galvanized sheet inside with 275 GSM galvanized coating for corrosion resistance and with CFC free PUF insulation of 40±5% kg/m3 injected in between. Fans shall be backward curved Aerofoil design blades Plenum plug fan so as to give maximum efficiency for given duty condition & low noise (less than 70 dBA at 1mtr distance). Fans impeller shall be selected for minimum efficiency of 70%. Fan wheels shall be made of MS epoxy coated. Fan motors shall be energy efficient with IE-3 grade and shall be suitable for 415±10% volts, 50 cycles, three phases, totally enclosed fan-cooled class H, with IP-55 protection. Drive to fan shall be provided through Direct drive arrangement. Motor shall be suitable for operating through VFD. Motor shall be assembled in such a way that it does not come in air stream. Air Moving capacities shall be as follows:12000 CFM -- 80 mm WG SP | 1.00 | Nos |  | 810178.00 | 810178.00 | 740625.00 | 740625.00 | 740625.00 | Surendra Infrastructure Pvt. Ltd.
4.00 | Supply, installation, testing and commissioning of factory built double skin type floor mounted air handling unit(fan section only) made of 25 mm thick panels consisting of pre plasticized G.I. casing of thickness 0.6 mm outside layer and 0.6mm thick minimum plane GI inside layer with polyurethane foam (PUF) insulation of density 40 ± 2 kg/m3 factory injected between them by injection moulding machine, complete with blower section with blower DIDW forward curved centrifugal fan, space provision for Electronic Air Cleaner , MERV8 filters, vibration isolators and fire retardant canvass connection , squirrel cage induction motor belt driven package with TEFC drive motor (IE-3), mounted within the housing and all other accessories etc. complete as required confirming to specification. The fan motor shall be suitable for 415 ± 10% Volts, 50Hz, AC power supply. 12000 CFM 80 mm WG SP | 1.00 | Nos |  | 277844.00 | 277844.00 | 744700.00 | 744700.00 | 277844.00 | Bharti Refrigeration Works
| Total in Figures |  |  |  |  | 17580572.00 |  | 17469850.00
Lowest Amount Quoted BY: Surendra Infrastructure Pvt. Ltd.(17469850.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of kitchen exhaust system and providing of fire rated painting and fire sealants to existing fire evacuation /ventilation ducts. Tender ID: 2023_AAI_144148_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Surendra Infrastructure Pvt. Ltd. | 17469850.00 | L1
| 2 | Bharti Refrigeration Works | 17580572.00 | L2