## BoQ1
Government eProcurement System Created By: SINDHU L S Created Date/Time: 06-Apr-2023 05:14 PM Tender Title: Facility Management Contract of 500 KWp Grid (22 KV) Connected Solar Power Plant at Puducherry Airport Tender ID: 2023_AAI_146405_1
Tender Inviting Authority: SENIOR MANAGER (ENGG-ELECTRICAL), AAI, RHQ-SR, CHENNAI AIRPORT, CHENNAI - 600 027.
Name of Work: FMC OF 500 KWp GRID [22 KV] CONNECTED SPV PP AT PUDUCHERRY AIRPORT
Contract No: 2023_AAI_146405_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Item Code | vk sam engineering(GSTN-33AMZPS4037L1ZA) |  | Imperial Solar Solutions(GSTN-NA) |  | DElite System Engineering (India) Pvt. Ltd.(GSTN-NA)
[5 empty] | Rate Without Tax | Rate With Tax | Rate Without Tax | Rate With Tax | Rate Without Tax | Rate With Tax | L1 Rate Without Tax | L1 Bidder Without Tax | L1 Rate With Tax | L1 Bidder With Tax
1.00 | SH I O&M
1.01 | Facility Management Contract for Monitoring & GENERAL Maintenance of 22 KV Grid Connected 500 KWp SPV PP at Puducherry Airport comprising of Solar PV Modules, DC DBs/JBs, Power Conditioning Units, String Monitoring Units, Lightning and Earthing Protection System, AC DC Cables, SCADA System, Weather Monitoring System, Transformer, 22 KV Panels etc., with One Skilled Person and One Helper on General Duty on Day Time as per the direction of EIC, Monitoring, Control and Maintenance for 100% Serviceability including Co-ordination with 22 KV Main Sub-Station of Terminal Building including Routine Cleaning of Modules as required. * It shall be noted that the BOQ item no.1 shall not accept quote less than minimum wages as on date of publication of tender (Ref pg.no. SCC 6 of tender document).
1.02 | I YEAR | 12.00 | Months | SH-I Item No. 1 (a) | 540000.00 | 637200.00 | 1452864.00 | 1714379.52 | 539988.00 | 637185.84 | 539988.00 | DElite System Engineering (India) Pvt. Ltd. | 637185.84 | DElite System Engineering (India) Pvt. Ltd.
1.03 | II YEAR | 12.00 | Months | SH-I Item No. 1 (b) | 621000.00 | 732780.00 | 1452864.00 | 1714379.52 | 539988.00 | 637185.84 | 539988.00 | DElite System Engineering (India) Pvt. Ltd. | 637185.84 | DElite System Engineering (India) Pvt. Ltd.
1.04 | III YEAR | 12.00 | Months | SH-I Item No. 1 (c) | 714144.00 | 842689.92 | 1525500.00 | 1800090.00 | 539988.00 | 637185.84 | 539988.00 | DElite System Engineering (India) Pvt. Ltd. | 637185.84 | DElite System Engineering (India) Pvt. Ltd.
2.00 | SH II AMC
2.01 | Overhauling and Servicing of 800 Amp 22 KV HT VCBs (Make : Schneider) by Deploying Authorised Service Personnel of Manufacturer/Service Dealer/ Specialised Agency experienced in similar nature of work, provided at Solar Substation (2 Panels) and Main SS (1 Panel) including drawing out of the VCB, opening the same, Inspection, Servicing, Cleaning of Contact Surfaces, Overhauling of Operating Mechanism, Lubrication of Moving Parts, Cleaning of CTs, PTs, Busbars and Chambers, Checking of Busbars and bus links, Replacement of Gasket of Panel, Checking of Electrical and Mechanical Operation, measuring of Contact Resistance, Checking of IR values, Testing of ON OFF Time, replacement of minor defective spares supplied by AAI (excluding supply of spares), Testing and Commissioning etc., as required. ISC of VCBs [Main Power House Schneider Make VCBs-1 No. and Solar SS Schneider Make VCBs- 2 Nos.(Total 3 Nos.)]
2.02 | I YEAR | 1.00 | Job | SH-II Item No. 1 (a) | 12100.00 | 14278.00 | 169400.00 | 199892.00 | 19000.00 | 22420.00 | 12100.00 | vk sam engineering | 14278.00 | vk sam engineering
2.03 | II YEAR | 1.00 | Job | SH-II Item No. 1 (b) | 13750.00 | 16225.00 | 185240.00 | 218583.20 | 19000.00 | 22420.00 | 13750.00 | vk sam engineering | 16225.00 | vk sam engineering
2.04 | III YEAR | 1.00 | Job | SH-II Item No. 1 (c) | 18700.00 | 22066.00 | 202664.00 | 239143.52 | 19000.00 | 22420.00 | 18700.00 | vk sam engineering | 22066.00 | vk sam engineering
2.05 | Calibration of Relays [(Electro-Mechanical/ Static/ Digital/ Microprocessor Based Relays)-(O/C and E/F)/] provided in HV Panels (3 Panels), Testing of Insulation Values, Pick-up Value, Timing, Burden, etc., i/c adjustment of Settings if required at site, Relay Co-ordination with immediate Up and Down Circuit etc., as required, conforming to IS 9124 - 1979 by Secondary Injection Test as required.
2.06 | I YEAR | 1.00 | Job | SH-II Item No. 2 (a) | 3850.00 | 4543.00 | 121000.00 | 142780.00 | 7999.00 | 9438.82 | 3850.00 | vk sam engineering | 4543.00 | vk sam engineering
2.07 | II YEAR | 1.00 | Job | SH-II Item No. 2 (b) | 4950.00 | 5841.00 | 132000.00 | 155760.00 | 7999.00 | 9438.82 | 4950.00 | vk sam engineering | 5841.00 | vk sam engineering
2.08 | III YEAR | 1.00 | Job | SH-II Item No. 2 (c) | 6380.00 | 7528.40 | 144100.00 | 170038.00 | 7999.00 | 9438.82 | 6380.00 | vk sam engineering | 7528.40 | vk sam engineering
2.09 | Calibration of Auxillary Relays/Master Trip Relay provided in HV Panels (3 Panels), Testing of Insulation values, Pick-up Value, Drop Off, Burden etc., as required, conforming to IS 9124 - 1979 by Secondary Injection Test as required.
2.10 | I YEAR | 1.00 | Job | SH-II Item No. 3 (a) | 550.00 | 649.00 | 163768.00 | 193246.24 | 7999.00 | 9438.82 | 550.00 | vk sam engineering | 649.00 | vk sam engineering
2.11 | II YEAR | 1.00 | Job | SH-II Item No. 3 (b) | 770.00 | 908.60 | 347090.00 | 409566.20 | 7999.00 | 9438.82 | 770.00 | vk sam engineering | 908.60 | vk sam engineering
2.12 | III YEAR | 1.00 | Job | SH-II Item No. 3 (c) | 935.00 | 1103.30 | 565550.00 | 667349.00 | 7999.00 | 9438.82 | 935.00 | vk sam engineering | 1103.30 | vk sam engineering
2.13 | Testing of 22 KV CTs (3 Nos. in one panel) of Current Rating of Upto 400 Amps associated with Relays (OC/EF/Master) provided in HV Panels (3 Panels), Tesing of Polarity, Ratio, Insulation values, Testing of Ammeter connected in the Panel, Marking of available CT Ratio, Checking of Trip Circuit and Breaker Operation/Tripping etc., as required, conforming to IS 9124 - 1979 by Primary Injection Test (Maximum upto 50% of Rating of CTs-Testing at 25% and 50% of Original Rating) as required.
2.14 | I YEAR | 1.00 | Job | SH-II Item No. 4 (a) | 9900.00 | 11682.00 | 78628.00 | 92781.04 | 15000.00 | 17700.00 | 9900.00 | vk sam engineering | 11682.00 | vk sam engineering
2.15 | II YEAR | 1.00 | Job | SH-II Item No. 4 (b) | 12375.00 | 14602.50 | 159782.00 | 188542.76 | 15000.00 | 17700.00 | 12375.00 | vk sam engineering | 14602.50 | vk sam engineering
2.16 | III YEAR | 1.00 | Job | SH-II Item No. 4 (c) | 16500.00 | 19470.00 | 256491.00 | 302659.38 | 15000.00 | 17700.00 | 15000.00 | DElite System Engineering (India) Pvt. Ltd. | 17700.00 | DElite System Engineering (India) Pvt. Ltd.
2.17 | Filtration of Transformer Oil of following Equipments conforming to IS 6792/72 and IS 1866 as required with up to date amendments, including transporting Filtration Plant and BDV Test Kit, Replacement of Silica Gel, Acidity Testing of Oil at Chemical Testing Lab, Submission of Reports, Checking of Cable Tightness, Gasketting of Cable End Boxes etc. as required. 630 KVA, 380-415 V/22 KV, 3 Phase, 50 Hz, Step Up, OUTDOOR TYPE, Star/Delta connected Inverter Rated Solar Transformer at Solar SS. (Oil capacity 830 Ltrs [Make : Voltamp]
2.18 | I YEAR | 1.00 | Job | SH-II Item No. 5 (a) | 16500.00 | 19470.00 | 136000.00 | 160480.00 | 12000.00 | 14160.00 | 12000.00 | DElite System Engineering (India) Pvt. Ltd. | 14160.00 | DElite System Engineering (India) Pvt. Ltd.
2.19 | II YEAR | 1.00 | Job | SH-II Item No. 5 (b) | 19800.00 | 23364.00 | 149600.00 | 176528.00 | 12000.00 | 14160.00 | 12000.00 | DElite System Engineering (India) Pvt. Ltd. | 14160.00 | DElite System Engineering (India) Pvt. Ltd.
2.20 | III YEAR | 1.00 | Job | SH-II Item No. 5 (c) | 26400.00 | 31152.00 | 164560.00 | 194180.80 | 12000.00 | 14160.00 | 12000.00 | DElite System Engineering (India) Pvt. Ltd. | 14160.00 | DElite System Engineering (India) Pvt. Ltd.
2.21 | Supply of Transformer Oil conforming to IS 335/1983 for topping up of oil for Transformer during filtration of Oil and for replacement of Oil for the Transformers. (As per Requirement only for 3 Years Period) | 200.00 | Ltr | SH-II Item No. 6 | 30800.00 | 36344.00 | 107252.00 | 126557.36 | 39800.00 | 46964.00 | 30800.00 | vk sam engineering | 36344.00 | vk sam engineering
2.22 | Testing of 630 KVA, 380-415 V/22 KV, 3 Phase, 50 Hz, Step Up, OUTDOOR TYPE, Star/Delta connected Inverter Rated Solar Transformer at Solar SS i/c testing of Insulation resistance, Magnetising current, winding resistance with mico-Ohm meter and Magnetic balance, etc., as required.
2.23 | I YEAR | 1.00 | Job | SH-II Item No. 7 (a) | 10505.00 | 12395.90 | 140800.00 | 166144.00 | 15000.00 | 17700.00 | 10505.00 | vk sam engineering | 12395.90 | vk sam engineering
2.24 | II YEAR | 1.00 | Job | SH-II Item No. 7 (b) | 13200.00 | 15576.00 | 153781.00 | 181461.58 | 15000.00 | 17700.00 | 13200.00 | vk sam engineering | 15576.00 | vk sam engineering
2.25 | III YEAR | 1.00 | Job | SH-II Item No. 7 (c) | 17490.00 | 20638.20 | 168060.00 | 198310.80 | 15000.00 | 17700.00 | 15000.00 | DElite System Engineering (India) Pvt. Ltd. | 17700.00 | DElite System Engineering (India) Pvt. Ltd.
2.26 | Comprehensive Annual Maintenance Contract of Solar Radiation and Environment Monitoring System consists of Instruments/ Sensors/ Computer Hardware and Software including Pyranometer, Temperature Module, Wind Speed and Direction Module, Relative Humidity and Rain Fall/Precipitation Instruments etc., including Servicing or Carrying out Preventive Maintenance once in six months, Breakdown Maintenance, Cleaning, Checking of Operation, providing and replacement of spares as required, Testing and Commissioning etc., as required.
2.27 | I YEAR | 1.00 | Year | SH-II Item No. 8 (a) | 22000.00 | 25960.00 | 127162.00 | 150051.16 | 15000.00 | 17700.00 | 15000.00 | DElite System Engineering (India) Pvt. Ltd. | 17700.00 | DElite System Engineering (India) Pvt. Ltd.
2.28 | II YEAR | 1.00 | Year | SH-II Item No. 8 (b) | 26400.00 | 31152.00 | 127162.00 | 150051.16 | 15000.00 | 17700.00 | 15000.00 | DElite System Engineering (India) Pvt. Ltd. | 17700.00 | DElite System Engineering (India) Pvt. Ltd.
2.29 | III YEAR | 1.00 | Year | SH-II Item No. 8 (c) | 34100.00 | 40238.00 | 127162.00 | 150051.16 | 15000.00 | 17700.00 | 15000.00 | DElite System Engineering (India) Pvt. Ltd. | 17700.00 | DElite System Engineering (India) Pvt. Ltd.
2.30 | Comprehensive Annual Maintenance Contract of SCADA consists of Instruments/ Sensors/ Computer Hardware and Software etc., including Servicing or Carrying out Preventive Maintenance once in six months, Breakdown Maintenance, Updation of Software as required, Cleaning, Checking of Operation/ Stimulation/ Monitoring/ Data, etc., providing and replacement of spares as required, Testing and Commissioning etc., as required.
2.31 | I YEAR | 1.00 | Year | SH-II Item No. 9 (a) | 10450.00 | 12331.00 | 143000.00 | 168740.00 | 20000.00 | 23600.00 | 10450.00 | vk sam engineering | 12331.00 | vk sam engineering
2.32 | II YEAR | 1.00 | Year | SH-II Item No. 9 (b) | 13200.00 | 15576.00 | 143000.00 | 168740.00 | 20000.00 | 23600.00 | 13200.00 | vk sam engineering | 15576.00 | vk sam engineering
2.33 | III YEAR | 1.00 | Year | SH-II Item No. 9 (c) | 17500.00 | 20650.00 | 143000.00 | 168740.00 | 20000.00 | 23600.00 | 17500.00 | vk sam engineering | 20650.00 | vk sam engineering
2.34 | Comprehensive Annual Maintenance Contract of 2 Nos. of 5 KVA UPS consists of UPS and Batteries etc., including Servicing or Carrying out Preventive Maintenance once in six months, Breakdown Maintenance, Checking of Operation, Checking of Wiring and Termination etc., providing and replacement of spares for UPS (Except Batteries) as required, Testing and Commissioning etc., as required.
2.35 | I YEAR | 1.00 | Year | SH-II Item No. 10 (a) | 9900.00 | 11682.00 | 93688.00 | 110551.84 | 7000.00 | 8260.00 | 7000.00 | DElite System Engineering (India) Pvt. Ltd. | 8260.00 | DElite System Engineering (India) Pvt. Ltd.
2.36 | II YEAR | 1.00 | Year | SH-II Item No. 10 (b) | 13200.00 | 15576.00 | 101957.00 | 120309.26 | 7000.00 | 8260.00 | 7000.00 | DElite System Engineering (India) Pvt. Ltd. | 8260.00 | DElite System Engineering (India) Pvt. Ltd.
2.37 | III YEAR | 1.00 | Year | SH-II Item No. 10 (c) | 16000.00 | 18880.00 | 111054.00 | 131043.72 | 7000.00 | 8260.00 | 7000.00 | DElite System Engineering (India) Pvt. Ltd. | 8260.00 | DElite System Engineering (India) Pvt. Ltd.
2.38 | Inspection and Servicing of 500 kWp Solar Power Panels on Half yearly basis including Servicing/Carrying out Preventive Maintenance/Breakdown Maintenance of Panels, Junction Boxes, DC Cabling, Earthing, LPS etc., including Checking Wiring, Cabling, Tightness of Cables, IP Protection of JB/CB, providing and fixing Gaskets as and when required etc., Testing and Commissioning etc., as required.
2.39 | I YEAR | 2.00 | Job | SH-II Item No. 11 (a) | 56980.00 | 67236.40 | 154010.00 | 181731.80 | 18000.00 | 21240.00 | 18000.00 | DElite System Engineering (India) Pvt. Ltd. | 21240.00 | DElite System Engineering (India) Pvt. Ltd.
2.40 | II YEAR | 2.00 | Job | SH-II Item No. 11 (b) | 71060.00 | 83850.80 | 154010.00 | 181731.80 | 18000.00 | 21240.00 | 18000.00 | DElite System Engineering (India) Pvt. Ltd. | 21240.00 | DElite System Engineering (India) Pvt. Ltd.
2.41 | III YEAR | 2.00 | Job | SH-II Item No. 11 (c) | 94050.00 | 110979.00 | 154010.00 | 181731.80 | 18000.00 | 21240.00 | 18000.00 | DElite System Engineering (India) Pvt. Ltd. | 21240.00 | DElite System Engineering (India) Pvt. Ltd.
2.42 | Cleaning of cable trenches by lifting the cables, supporting the cables, removing waste materials I/c malba, debris etc., and transporting and dumping the same to waste dumping yard etc. as required. | 60.00 | Mtr | SH-II Item No. 12 | 12000.00 | 14160.00 | 34107.60 | 40246.97 | 18000.00 | 21240.00 | 12000.00 | vk sam engineering | 14160.00 | vk sam engineering
2.43 | Providing one Skilled Wireman and two Unskilled Khalasi to attend any urgent Preventive Maintenance/ Breakdown Maintenance/ Emergency Work at Electrical Installations provided in Solar Substation with necessary T&P as and when required. | 72.00 | Days | SH-II Item No. 13 | 108000.00 | 127440.00 | 248608.80 | 293358.38 | 143928.00 | 169835.04 | 108000.00 | vk sam engineering | 127440.00 | vk sam engineering
2.44 | Hire Charges for deploying Excavater (JCB) i/c Operator for tracing the cable faults Providing Labour for tracing the cable faults, excavation and refilling of Cable trench after work etc., as required.. | 48.00 | Hrs | SH-II Item No. 14 | 144000.00 | 169920.00 | 449249.76 | 530114.72 | 57600.00 | 67968.00 | 57600.00 | DElite System Engineering (India) Pvt. Ltd. | 67968.00 | DElite System Engineering (India) Pvt. Ltd.
2.45 | Touble shooting for SCADA by deputing required skilled technician, identification of fault, and giving service report. | 3.00 | Day | SH-II Item No. 15 | 45000.00 | 53100.00 | 26685.99 | 31489.47 | 53997.00 | 63716.46 | 26685.99 | Imperial Solar Solutions | 31489.47 | Imperial Solar Solutions
2.46 | Supply of following size of XLPE armoured cable with copper conductor of 1100V garde.( IS:7098) a) 7core x 1.5 sqmm | 300.00 | Mtr | SH-II Item No. 16 | 105000.00 | 123900.00 | 66222.00 | 78141.96 | 59700.00 | 70446.00 | 59700.00 | DElite System Engineering (India) Pvt. Ltd. | 70446.00 | DElite System Engineering (India) Pvt. Ltd.
2.47 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1KV grade of following size in the existing RCC/ HUME/ METAL pipe as required. | 300.00 | mtr | SH-II Item No. 17 | 21000.00 | 24780.00 | 73713.00 | 86981.34 | 12000.00 | 14160.00 | 12000.00 | DElite System Engineering (India) Pvt. Ltd. | 14160.00 | DElite System Engineering (India) Pvt. Ltd.
2.48 | Excavation for cable trenches in soft soil, depth upto 0.75 m including dressing of sides lift upto 1.5 m, including getting out the excavated soil, refilling with sand and or good soil after laying of cable/ pipe etc in layers of 20 cm, ramming and disposal of surplus excavated soil as directed, within a lead of 50 metres. | 45.00 | cum | SH-II Item No. 18 | 22500.00 | 26550.00 | 258514.20 | 305046.76 | 80955.00 | 95526.90 | 22500.00 | vk sam engineering | 26550.00 | vk sam engineering
| Total in Figures |  |  |  | 2952939.00 | 3484468.02 | 10713310.35 | 12641706.22 | 2496938.00 | 2946386.84

## BOQ Summary
BOQ Summary Details Tender Title: Facility Management Contract of 500 KWp Grid (22 KV) Connected Solar Power Plant at Puducherry Airport Tender ID: 2023_AAI_146405_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | DElite System Engineering (India) Pvt. Ltd. | 2946386.84 | L1
| 2 | vk sam engineering | 3484468.02 | L2
| 3 | Imperial Solar Solutions | 12641706.22 | L3