## BoQ1
Government eProcurement System Created By: Sanjib Kumar Dey Created Date/Time: 23-Mar-2023 03:38 PM Tender Title: Modification of existing panels for water pump at New Quarter, Kolkata Airport Tender ID: 2023_AAI_146618_1
Tender Inviting Authority: Asstt. Gen. Manager (E-E), AAI, RHQ,ER
Name of Work: Modification of existing panels for water pump at New Quarter, Kolkata Airport.
Contract No: AAI/ER /KOL /EE/NIT-14/2022 -23/
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | M/s LEESHA ELECTRICALS(GSTN-27ABAPW8550C1ZK) |  | T K MAZUMDER(GSTN-19AADFT2150K1Z3) |  | ANIRBAN ENTERPRISE(GSTN-19AHNPB5949D1Z6) |  | SOM ENGINEERING WORKS(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | FOR 15,16 &17 NO PUMP HOUSE:-Design, fabrication, assembling, wiring, supply, installation, testing and commissioning of motor control centre, IP42, sutaible for 415 Volt, 3phase,4waire, 50Hz AC supply shall be fabricated as wall mounted, dust and vermin proof, indoor, compartmentalised, including cleaning & finishing complete with 7 tank process, powder coated, painting with reinforcement of suitable size angle iron, channel ‘T’ sections irons and /or flats wherever necessary. Cable gland plates shall be provided on top as well as at the bottom of the panels. Panels shall be treated with all anticorrosive process before painting as per specifications with 2 coats of red oxide primer and final approved shade of powder coated paint. Entire panel shall have a commom copper bus bar of size 25mm X 5mm at the rear with 2 Nos. copper earth stud. Lifting hooks shall also be provided. Incoming-2 Nos. 125A, 4P MCCB, 25 KA, thermal magnetic based release rotary type handle and spreader link (Ics = Icu = 100%) with O/L , S/C & E/F protection as per specification with door interlocking& mechanical interlocking between 2 incoming MCCB(2 hole,1 Key operation,C Lock) and with following accessories.1 No. Digital MFM meter and 3 nos. CTs of ratio 150/5A , Class 0.5 accuracy and 10 VA burden. digital multifunction meter suitable to measure voltage, Ampere, Frequency, Power Factor with RS-485 Port-2 sets2 Set of ON/ OFF/TRIP(Red-Green-amber) Indicating LED Lamps with 2 Amp 10 KA MCB.2 Set of phase indicating LED lamps(R-Y-B) with 2 amp 10 KA back up MCB. Bus Bar- 4P Copper bus bars of 150A capacity with heat shrinkable coloured sleeves and i/c, SMC bus bars supports at required intervals complete for cross section, size supports & their spacing etc. for withstanding fault level of 25KA for 1 sec. Outgoings- 1 Nos. suitable rating 50 A MPCB 50 KA for 18.5 KW(25 HP) Star Delta starter having 40A TP AC3 duty power contactors ,Single phase preventer,Star-Delta Timer, off timer. Each compartment shall contain auto / manual selector swtich and indicating lamps with for ON/OFF/TRIP indication and Motor START /STOP push bottom switch. 1 Nos. suitable rating 50 A MPCB 50 KA for 11 KW(15 HP) Star Delta starter having 25A TP AC3 duty power contactors ,Single phase preventer,Star-Delta Timer, off timer. Each compartment shall contain auto / manual selector swtich and indicating lamps with for ON/OFF/TRIP indication and Motor START /STOP push bottom switch. Spare MCCB of following capacities: 2 Nos. 100A, 4P MCCB, 25 KA, thermal magnetic based release rotary type handle and spreader link (Ics = Icu = 100%) with with O/L,S/C & E/F protection,ON-OFF indication lamp.Necessary cable alleys, internal wiring, and interlocking, earthing for all equipment shall also be included. Notes : a. All MPCBs / MCCBs shall be of 50 / 25 KA breaking capacity respectively. b. Provision shall be made to ensure system protection from dry running of the pump c. All incomers shall be electrical and mechanical interlocked with suitable accessories. d. Provision of pump running hour meter | 3.00 | Job | 100.00 | 225500.00 | 676500.00 | 293250.00 | 879750.00 | 285000.00 | 855000.00 | 311190.00 | 933570.00 | 676500.00 | M/s LEESHA ELECTRICALS
2.00 | FOR 3 & 4 NO. SEWARAGE MONOBLOCK PUMP HOUSE- Design, fabrication, assembling, wiring, supply, installation, testing and commissioning of motor control panel, IP42, sutaible for 415 Volt, 3phase,4waire, 50Hz AC supply shall be fabricated as wall mounted, dust and vermin proof, indoor, compartmentalised, including cleaning & finishing complete with 7 tank process, powder coated, painting with reinforcement of suitable size angle iron, channel ‘T’ sections irons and /or flats wherever necessary. Cable gland plates shall be provided on top as well as at the bottom of the panels. Panels shall be treated with all anticorrosive process before painting as per specifications with 2 coats of red oxide primer and final approved shade of powder coated paint. Entire panel shall have a commom copper bus bar of size 25mm X 5mm at the rear with 2 Nos. earth stud. Lifting hooks shall also be provided. Incoming- 2 Nos. 125A, 4P MCCB, 25 KA, thermal magnetic based release rotary type handle and spreader link (Ics = Icu = 100%) with O/L , S/C & E/F protection as per specification with door interlocking& mechanical interlocking between 2 incoming MCCB(2 hole,1 Key operation,C Lock) and with following accessories. 1 No. Digital MFM meter and 3 nos. CTs of ratio 150/5A , Class 0.5 accuracy and 10 VA burden. digital multifunction meter suitable to measure voltage, Ampere, Frequency, Power Factor with RS-485 Port-2 sets. 2 Set of ON/ OFF/TRIP(Red-Green-amber) Indicating LED Lamps with 2 Amp 10 KA MCB. 2 Set of phase indicating LED lamps(R-Y-B) with 2 amp,10 KA back up MCB. Bus Bar- 4P Copper bus bars of 150A capacity with heat shrinkable coloured sleeves and i/c, SMC bus bars supports at required intervals complete for cross section, size supports & their spacing etc. for withstanding fault level of 25KA for 1 sec. Outgoings- 2 Nos. suitable rating 50 A MPCB 50 KA for 5.5 KW(7.5 HP) Star Delta starter having 15A TP AC3 duty power contactors ,Single phase preventer,Star-Delta Timer, off timer. Each compartment shall contain auto / manual selector swtich and indicating lamps with for ON/OFF/TRIP indication and Motor START /STOP push bottom switch. Spare MCCB of following capacities: 2 Nos. 100A, 4P MCCB, 25 KA, thermal magnetic based release rotary type handle and spreader link (Ics = Icu = 100%) with with O/L , S/C & E/F protection,ON-OFF indication lamp. Necessary cable alleys, internal wiring, and interlocking, earthing for all equipment shall also be included. Notes : a. All MPCBs / MCCBs shall be of 50 / 25 KA breaking capacity respectively. b. Provision shall be made to ensure system protection from dry running of the pump. c. All incomers shall be electrical and mechanical interlocked with suitable accessories. d. Provision of pump running hour meter | 2.00 | Nos | 100.00 | 205000.00 | 410000.00 | 155250.00 | 310500.00 | 265000.00 | 530000.00 | 272140.00 | 544280.00 | 310500.00 | T K MAZUMDER
3.00 | Supply of following size 1.1 kv grade, PVC insulated and PVC sheathed copper flat cable conforming to IS: 694 with up to date amendments etc. complete as required
3.01 | 3C x 4 Sq. mm. | 300.00 | Metre | 10.00 | 190.00 | 57000.00 | 166.00 | 49800.00 | 135.00 | 40500.00 | 118.45 | 35535.00 | 35535.00 | SOM ENGINEERING WORKS
3.02 | 3CX6 Sq.mm | 300.00 | Metre | 10.00 | 250.00 | 75000.00 | 286.00 | 85800.00 | 185.00 | 55500.00 | 174.07 | 52221.00 | 52221.00 | SOM ENGINEERING WORKS
4.00 | Providing, installation, testing and commissioning of dual plate wafer type 100mm dia non-return valve PN 16 of CI body of following sizes confirming to IS: 5312 complete with neoprene rubber gasket, bolts, nuts, washers etc. as required. | 2.00 | Each | 10.00 | 3950.00 | 7900.00 | 10450.00 | 20900.00 | 5000.00 | 10000.00 | 2369.00 | 4738.00 | 4738.00 | SOM ENGINEERING WORKS
5.00 | Supply of 8mm dia steel ropes suitable for holding submersible pump motor setsets etc. complete as required. (Make-Usha Martin or Equivalent Make as AAI) | 200.00 | Mtr. | 10.00 | 40.00 | 8000.00 | 103.87 | 20774.00 | 105.00 | 21000.00 | 123.60 | 24720.00 | 8000.00 | M/s LEESHA ELECTRICALS
6.00 | Fabrication, treatment & painting of damaged portion of cabinet Box in the existing LT panel as per the site requirement upto the satisfaction of Engg-in- charge etc. complete as required. | 40.00 | Sq.Mtr. | 10.00 | 4900.00 | 196000.00 | 890.00 | 35600.00 | 350.00 | 14000.00 | 2678.00 | 107120.00 | 14000.00 | ANIRBAN ENTERPRISE
7.00 | Scrabing,cleaning and painting of street light CC collar i/c loop-in-loop out box with two coats of sperior qualitity synthetic enamel paint of approved colour etc. all as required Note: CC collars to be painted with alternate strips of different colour as per the direction of the Engineer-in-Charge. | 10.00 | Job | 10.00 | 195.00 | 1950.00 | 600.00 | 6000.00 | 1000.00 | 10000.00 | 2678.00 | 26780.00 | 1950.00 | M/s LEESHA ELECTRICALS
8.00 | Dismantling of Existing Pump Control Panel including dis-connection as directed by EIC etc. complete as required. | 5.00 | Job | 10.00 | 495.00 | 2475.00 | 700.00 | 3500.00 | 3000.00 | 15000.00 | 1998.20 | 9991.00 | 2475.00 | M/s LEESHA ELECTRICALS
9.00 | DSR item ( Rate will be considered % above / below of or equal to 100% of DSR 2018 E&M rate). NOTE:-The execution of Delhi Schedule of Rates (E&M) 2018 Items as when required basis. Example for quoting the rate:- (i)Agency Quoting Rs.4,50,000.00 in the Rate stands for 10% below the Estimate amounting of Rs.5,00,000.00 net amount will be 4,50,000‬.00 and payment will be made 10% below on DSR 2018 rate against items. (ii)Agency Quoting Rs. 550000.00 in the Rate stands for 10% above the Estimate amounting of Rs.5,00,000 net amount will be 550000.00 and payment will be made 10% above on DSR 2018 rate against items.‬‬‬‬‬‬‬‬‬‬‬‬‬‬‬‬ (For Payment calculation please refer relevant Technical specification of Tender Document) | 1.00 | Job | 10.00 | 264376.00 | 264376.00 | 410000.00 | 410000.00 | 475000.00 | 475000.00 | 199933.00 | 199933.00 | 199933.00 | SOM ENGINEERING WORKS
| Total in Figures |  |  |  |  | 1699201.00 |  | 1822624.00 |  | 2026000.00 |  | 1938888.00
Lowest Amount Quoted BY: M/s LEESHA ELECTRICALS(1699201.00)

## BOQ Summary
BOQ Summary Details Tender Title: Modification of existing panels for water pump at New Quarter, Kolkata Airport Tender ID: 2023_AAI_146618_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | M/s LEESHA ELECTRICALS | 1699201.00 | L1
| 2 | T K MAZUMDER | 1822624.00 | L2
| 3 | SOM ENGINEERING WORKS | 1938888.00 | L3
| 4 | ANIRBAN ENTERPRISE | 2026000.00 | L4