## BoQ1
Government eProcurement System Created By: A DHANUSKODI Created Date/Time: 15-May-2023 11:28 AM Tender Title: Provision of Perimeter Lighting at Tuticorin Airport Tender ID: 2023_AAI_146971_1
Tender Inviting Authority: Airports Authority of India, Tuticorin Airport, Tuticorin - 628103.
Name of Work: Provision of Perimeter Lighting at Tuticorin Airport.
Contract No: 2023_AAI_146971_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | MIDAS ELECTRICALS PVT LTD(GSTN-33AAOCS7691A1Z6) |  | Bajaj Electricals Limited(GSTN-27AAACB2484Q1Z8) |  | HPL Electric and Power Limited(GSTN-06AAACH0165J2ZT) |  | Instapower Ltd(GSTN-05AAACI9712L1ZG)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply of following size of XLPE insulated PVC sheathed Aluminium conductor armoured power cable of 1.1 KV grade conforming to IS-7098 Part-I amended upto date etc. complete as required.
1.01 | 3.5 core x 400 mm2 | 3500.00 | Metre |  | 1625.00 | 5687500.00 | 1574.00 | 5509000.00 | 1900.00 | 6650000.00 | 2488.00 | 8708000.00 | 5509000.00 | Bajaj Electricals Limited
1.02 | 3.5 core x 240 mm2 | 4260.00 | Metre |  | 1040.00 | 4430400.00 | 1007.00 | 4289820.00 | 1150.00 | 4899000.00 | 1584.00 | 6747840.00 | 4289820.00 | Bajaj Electricals Limited
1.03 | 3.5 core x 95 mm2 | 3580.00 | Metre |  | 444.00 | 1589520.00 | 422.00 | 1510760.00 | 350.00 | 1253000.00 | 594.00 | 2126520.00 | 1253000.00 | HPL Electric and Power Limited
1.04 | 4 core x 10 mm2 | 18900.00 | Metre |  | 115.00 | 2173500.00 | 111.00 | 2097900.00 | 165.00 | 3118500.00 | 190.00 | 3591000.00 | 2097900.00 | Bajaj Electricals Limited
2.00 | Supply of LED Flood Light Luminaire having minimum 3300 lumens with minimum efficacy of 110 lumen/Watt, CCT 5700K and made of pressure diecast aluminium housing body, front glass, IP 66 suitable for operation at 230 V +/- 10%, Single phase AC supply complete etc. as required. | 650.00 | Each |  | 1650.00 | 1072500.00 | 1100.00 | 715000.00 | 1350.00 | 877500.00 | 1386.00 | 900900.00 | 715000.00 | Bajaj Electricals Limited
3.00 | Supply, Installation, Testing and Commissioning of LT Outdoor Type Main Feeder Pillar made out of 3mm thick CRCA Sheet Steel for outer Shell (width not less than 450 mm) and 2mm thick CRCA Sheet for inner partition, dust tight, vermin proof, totally enclosed, cubicle type, floor mounting, free standing suitable for operation at 433 V, 3 Phase, 4 Wire, 50 Hz, AC System with One Set of 400 Amps Al. Bus Bars with at Par Neutral Bus Bar as required complete with all accessories, interconnection, connection, earthing, painting, provided with bottom base channel and locking arrangements including excavation for foundation, providing foundation of suitable RCC pedestal up to 900 mm (600 mm BGL and 300 mm AGL), fixing of panel etc. complete as required and comprising of the following: a) Two Nos. of 250 A, 50 KA, 4P MCCB with Microprocessor Based Releases (L&T with MTX 2.0 / Equivalent) for OC/SC/EF Protection and ROM as INCOMER with Castle key interlocking arrangement, resin cast C.T. operated Digital Meter (EM 6400 of Conzerve/Equivalent), ON/OFF/TRIP Indication Lamps and Phase Indication Lamps as required. b) Two Nos. of 250 A, 25 KA, 4P MCCB with TM Releases for OC/SC Protection and ROM as Outgoings with ON/OFF/TRIP Indication Lamps and Phase Indication Lamps as required. c) Three Nos. of 100 A, 36 KA, 4P MCCB with TM Releases for OC/SC Protection and ROM as Outgoings with ON/OFF/TRIP Indication Lamps and Phase Indication Lamps as required. d) Two Nos. of 63 A, 25 KA, 4P MCCB with TM Releases for OC/SC Protection and ROM as Outgoings each having 4P Contactor of 40 Amps rating and 24 Hours Digital Timer for Automatic Control of Perimeter Lighting, ON/OFF/TRIP Indication Lamps and Phase Indication Lamps as required. e) All accessories such as fuses, auxillary contactors, auxillary switches etc. as required. | 4.00 | Job |  | 155000.00 | 620000.00 | 472153.00 | 1888612.00 | 52000.00 | 208000.00 | 350000.00 | 1400000.00 | 208000.00 | HPL Electric and Power Limited
4.00 | Supply, Installation, Testing and Commissioning of LT Outdoor Type Sub Feeder Pillar made out of 3mm thick CRCA Sheet Steel for outer Shell (width not less than 400 mm) and 2mm thick CRCA Sheet for inner partition, dust tight, vermin proof, totally enclosed, cubicle type, floor mounting, free standing suitable for operation at 433 V, 3 Phase, 4 Wire, 50 Hz AC System with one Set of 200 Amps Al. Bus Bars with at Par Neutral Bus Bars as required. complete with all accessories, interconnection, connection, earthing, painting, provided with bottom base channel and locking arrangements including excavation for foundation, providing foundation of suitable RCC pedestal up to 750 mm (500 mm BGL and 250 mm AGL), fixing of panel etc. complete as required and comprising of the following: a) One No. of 100 A, 36 KA, 4P MCCB with TM Releases for OC/SC Protection and ROM as INCOMER with resin cast C.T. operated Digital VAF Metre (EM 6459 of Conzerve/Equivalent), ON/OFF/TRIP Indication Lamps and Phase Indication Lamps as required. b) Two Nos of 63 A, 25 KA, 4P MCCB with TM Releases for OC/SC Protection and ROM as Outgoings each having 4P Contactor of 40 Amps rating and 24 Hours Digital Timer for Automatic Control of PeriMetre Lighting, ON/OFF/TRIP Indication Lamps and Phase Indication Lamps as required. c) Two Nos of 40 A, 25 KA, 4P MCCB with TM Releases for OC/SC Protection and ROM as Outgoings ON/OFF/TRIP Indication Lamps and Phase Indication Lamps as required. d) Two Nos. of 63 A, 25 KA, 4P MCCB with TM Releases for OC/SC Protection and ROM as Outgoings each having 4P Contactor of 40 Amps rating and 24 Hours Digital Timer for Automatic Control of Perimeter Lighting, ON/OFF/TRIP Indication Lamps and Phase Indication Lamps as required | 4.00 | Job |  | 135000.00 | 540000.00 | 297294.00 | 1189176.00 | 405000.00 | 1620000.00 | 211200.00 | 844800.00 | 540000.00 | MIDAS ELECTRICALS PVT LTD
5.00 | Fabrication and Supply of tubular swaged pole consisting of one section with 5.4 mm thick & 114.3 mm outer dia MS pole for 1 Mtr length with door and lock provision, providing and fixing 1 No. 5-32 Amps 'C' Series DP MCB and 63A 4 way connector inside the door, 16mm thick base plate of dimension 250mm x 250mm, 4 Nos of 12mm dia 500 mm long GI foundation bolts and nuts, Bottom Section welded with Top section of tubular swaged pole of 4.85 mm thick & 88.9 mm outer dia for length upto 1.0 Mtr welded with MS C channel of suitable size for mounting LED fixture, providing mounting arragement for LED fixture and painted with one coat of zinc chromate primer and two coats of polyurethane paint of approved colour complete as required | 575.00 | Job |  | 7500.00 | 4312500.00 | 7095.00 | 4079625.00 | 5400.00 | 3105000.00 | 7260.00 | 4174500.00 | 3105000.00 | HPL Electric and Power Limited
6.00 | ITC of 2m height tubular swaged pole with base plate after providing RCC foundation of size 500 mm x 500 mm & 450 mm depth below ground level and 300 mm height above ground level with cement concrete ratio 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) after PCC base of size 600 mm x 600 mm & 150 mm depth with cement concrete ratio 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size) including excavation, shuttering, positioning template and fixing foundation bolts and nuts as supplied i/c securing with holding clamps, providing and fixing 2 Nos. of PE 63 PN 6 40mm OD HDPE Pipe of required length in foundation for loop in loop out cable, refilling, levelling surface, installation of LED light fixture, supply and laying of copper cable of size 3 x 1.5 mm2 of required length from MCB to LED light fixture mounted at the top including the numbering of poles using sticker etc. complete as required and as per instructions of Engineer-In-Charge. | 575.00 | Job |  | 3500.00 | 2012500.00 | 5504.00 | 3164800.00 | 5400.00 | 3105000.00 | 1980.00 | 1138500.00 | 1138500.00 | Instapower Ltd
7.00 | Supply and Installation of Thermo plastic polycarbonate Junction box complying IP54 protection of minimum size 680mm x 1035mm x 400mm with 4 Nos 50mm x 10mm copper bus bar to terminate 3.5 x 400 mm2 Aluminium conductor cable with suitable gland and mounting frame mounted on pedestal complete etc. at a minimum height of 1m above ground level on 2 Nos of MS L angle for both vertical support and flat wall mount support of size 60mm x 60mm x 6mm on a concrete pedestal of size 300mm x 300mm x 600mm (Depth) with CC ratio of 1:2:4 etc. as required. | 6.00 | Job |  | 6000.00 | 36000.00 | 93161.00 | 558966.00 | 99000.00 | 594000.00 | 2376.00 | 14256.00 | 14256.00 | Instapower Ltd
8.00 | Supply and Installation of Thermo plastic polycarbonate Junction box complying IP54 protection of minimum size 680mm x 1035mm x 400mm with 4 Nos 50mm x 10mm copper bus bar to terminate 3.5 x 240 mm2 Aluminium conductor cable with suitable gland and mounting frame mounted on pedestal complete etc. at a minimum height of 1m above ground level on 2 Nos of MS L angle for both vertical support and flat wall mount support of size 60mm x 60mm x 6mm on a concrete pedestal of size 300mm x 300mm x 600mm (Depth) with CC ratio of 1:2:4 etc. as required. | 7.00 | Job |  | 5500.00 | 38500.00 | 93161.00 | 652127.00 | 81000.00 | 567000.00 | 26977.00 | 188839.00 | 38500.00 | MIDAS ELECTRICALS PVT LTD
9.00 | Supply and Installation of Thermo plastic polycarbonate Junction box complying IP65 & IK10 protection of minimum size 380mm x 658mm x 232mm with 30mm x 10mm copper bus bar to terminate 3.5 x 95 mm2 Aluminium conductor cable with suitable gland and mounting frame mounted on pedestal complete etc. at a minimum height of 1m above ground level on 2 Nos of MS L angle for both vertical support and flat wall mount support of size 60mm x 60mm x 6mm on a concrete pedestal of size 300mm x 300mm x 600mm (Depth) with CC ratio of 1:2:4 etc. as required. | 2.00 | Job |  | 4500.00 | 9000.00 | 93161.00 | 186322.00 | 140000.00 | 280000.00 | 47288.00 | 94576.00 | 9000.00 | MIDAS ELECTRICALS PVT LTD
10.00 | Supply and laying of 150 mm dia 'B' Class GI Pipe in concrete/bitumen for cable crossing/laying by cutting the bitumen/concrete of suitable size to a depth of minimum 200mm for laying the pipe, threading, cutting, jointing of pipe & filling the gaps with bitumen mix/concrete and making good the surface matching with original finish etc. as required and as per the instruction of Engineer-in-charge. | 50.00 | Metre |  | 2000.00 | 100000.00 | 1920.00 | 96000.00 | 3600.00 | 180000.00 | 858.00 | 42900.00 | 42900.00 | Instapower Ltd
11.00 | Supplying and laying of HDPE pipe of 125 mm OD ISI marked of PE 80 PN6 grade conforming to IS 4984 along with all accessories like socket, bend etc. complete with fitting and cutting, jointing etc. direct in ground at a depth of 0.80 m below the ground level i/c excavation and refilling the trench but excluding sand cushioning and protective covering etc. as required. | 3150.00 | Metre |  | 550.00 | 1732500.00 | 590.00 | 1858500.00 | 580.00 | 1827000.00 | 745.00 | 2346750.00 | 1732500.00 | MIDAS ELECTRICALS PVT LTD
12.00 | Supplying and laying of HDPE pipe of 110 mm OD ISI marked of PE 80 PN6 grade conforming to IS 4984 along with all accessories like socket, bend etc. complete with fitting and cutting, jointing etc. direct in ground at a depth of 0.80 m below the ground level i/c excavation and refilling the trench but excluding sand cushioning and protective covering etc. as required. | 3900.00 | Metre |  | 450.00 | 1755000.00 | 488.00 | 1903200.00 | 450.00 | 1755000.00 | 594.00 | 2316600.00 | 1755000.00 | MIDAS ELECTRICALS PVT LTD, HPL Electric and Power Limited
13.00 | Supplying and laying of HDPE pipe of 63 mm OD ISI marked of PE 80 PN6 grade conforming to IS 4984 along with all accessories like socket, bend etc. complete with fitting and cutting, jointing etc. direct in ground at a depth of 0.80m below the ground level i/c excavation and refilling the trench but excluding sand cushioning and protective covering etc. as required. | 3000.00 | Metre |  | 400.00 | 1200000.00 | 234.00 | 702000.00 | 207.00 | 621000.00 | 330.00 | 990000.00 | 621000.00 | HPL Electric and Power Limited
14.00 | Supplying and laying of HDPE pipe of 40 mm OD ISI marked of PE 63 PN6 grade conforming to IS 4984 along with all accessories like socket, bend etc. complete with fitting and cutting, jointing etc. direct in ground at a depth of 0.80m below the ground level i/c excavation and refilling the trench but excluding sand cushioning and protective covering etc. as required. | 18210.00 | Metre |  | 350.00 | 6373500.00 | 163.00 | 2968230.00 | 162.00 | 2950020.00 | 198.00 | 3605580.00 | 2950020.00 | HPL Electric and Power Limited
15.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC / HUME / METAL / HDPE pipe as required:
15.01 | 3.5 core x 400 mm2 | 3150.00 | Metre |  | 500.00 | 1575000.00 | 166.00 | 522900.00 | 180.00 | 567000.00 | 176.00 | 554400.00 | 522900.00 | Bajaj Electricals Limited
15.02 | 3.5 core x 240 mm2 | 3900.00 | Metre |  | 400.00 | 1560000.00 | 128.00 | 499200.00 | 140.00 | 546000.00 | 176.00 | 686400.00 | 499200.00 | Bajaj Electricals Limited
15.03 | 3.5 core x 95 mm2 | 3000.00 | Metre |  | 250.00 | 750000.00 | 102.00 | 306000.00 | 100.00 | 300000.00 | 75.00 | 225000.00 | 225000.00 | Instapower Ltd
15.04 | 4 x 10 mm2 | 18210.00 | Metre |  | 150.00 | 2731500.00 | 28.00 | 509880.00 | 50.00 | 910500.00 | 48.00 | 874080.00 | 509880.00 | Bajaj Electricals Limited
16.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required.
16.01 | Above 185 mm2 and upto 400 mm2 | 100.00 | Metre |  | 550.00 | 55000.00 | 320.00 | 32000.00 | 135.00 | 13500.00 | 150.00 | 15000.00 | 13500.00 | HPL Electric and Power Limited
16.02 | Upto 35 mm2 | 40.00 | Metre |  | 350.00 | 14000.00 | 192.00 | 7680.00 | 90.00 | 3600.00 | 36.00 | 1440.00 | 1440.00 | Instapower Ltd
17.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed/XLPE aluminium conductor cable of 1.1 KV grade as required:
17.01 | 3.5 core x 400 mm2 | 16.00 | Set |  | 3950.00 | 63200.00 | 5760.00 | 92160.00 | 560.00 | 8960.00 | 2053.00 | 32848.00 | 8960.00 | HPL Electric and Power Limited
17.02 | 3.5 core x 240 mm2 | 20.00 | Set |  | 3250.00 | 65000.00 | 4096.00 | 81920.00 | 360.00 | 7200.00 | 1355.00 | 27100.00 | 7200.00 | HPL Electric and Power Limited
17.03 | 3.5 core x 95 mm2 | 10.00 | Set |  | 1320.00 | 13200.00 | 2048.00 | 20480.00 | 144.00 | 1440.00 | 776.00 | 7760.00 | 1440.00 | HPL Electric and Power Limited
18.00 | Supplying and making end termination with aluminium lugs for following size of PVC insulated and PVC sheathed/XLPE aluminium conductor cable of 1.1 KV grade as required: 4 x 10 mm2 | 1164.00 | Set |  | 438.00 | 509832.00 | 102.00 | 118728.00 | 100.00 | 116400.00 | 330.00 | 384120.00 | 116400.00 | HPL Electric and Power Limited
19.00 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal / coke and salt as required. | 16.00 | Job |  | 7500.00 | 120000.00 | 12800.00 | 204800.00 | 7000.00 | 112000.00 | 9048.00 | 144768.00 | 112000.00 | HPL Electric and Power Limited
20.00 | Supplying and laying 25 mm x 5 mm GI strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of brass nut bolt & spring washer spaced at 50mm) | 32.00 | Metre |  | 160.00 | 5120.00 | 320.00 | 10240.00 | 45.00 | 1440.00 | 213.00 | 6816.00 | 1440.00 | HPL Electric and Power Limited
21.00 | Providing and fixing 25 mm x 5 mm G.I. strip on surface or in recess for connections etc. as required. | 16.00 | Metre |  | 160.00 | 2560.00 | 243.00 | 3888.00 | 36.00 | 576.00 | 1533.00 | 24528.00 | 576.00 | HPL Electric and Power Limited
22.00 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess or ground for loop earthing along with existing cable as required. | 17176.00 | Metre |  | 25.00 | 429400.00 | 21.00 | 360696.00 | 27.00 | 463752.00 | 55.00 | 944680.00 | 360696.00 | Bajaj Electricals Limited
23.00 | Supplying and making cable route marker with cement concrete 1:2:4 (1 cement: 2 coarse sand: 4 graded stone aggregate 20mm nominal size) of size 60 cm x 60 cm at the bottom and 50 cm x 50 cm at the top with a thickness of 10 cm including inscription duly engraved as required. | 20.00 | Each |  | 3000.00 | 60000.00 | 1024.00 | 20480.00 | 630.00 | 12600.00 | 772.00 | 15440.00 | 12600.00 | HPL Electric and Power Limited
24.00 | Providing cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) to make platform around the installed perimeter poles including excavation to required depth, plastering, finishing etc. as per the direction of Engineer-in-charge as required. | 67.25 | Cum |  | 4500.00 | 302625.00 | 10240.00 | 688640.00 | 5000.00 | 336250.00 | 158.00 | 10625.50 | 10625.50 | Instapower Ltd
25.00 | Carrying out site survey of perimeter lighting system regarding the routes of main feeder, sub feeder and loop-in loop out cables from various power houses / main feeder pillars / sub feeder pillars for distribution of power supply, location of all main feeder pillars, sub feeder pillars and perimeter light poles with Profile level and WGS Coordinates (i.e. Longitude and Latitude), submission of complete layout showing all such installations in hard copy and soft copy (Autocad, PDF and KML file) etc. complete as required. | 1.00 | Job |  | 150000.00 | 150000.00 | 115207.00 | 115207.00 | 50000.00 | 50000.00 | 400000.00 | 400000.00 | 50000.00 | HPL Electric and Power Limited
26.00 | SITC of 18W LED, (4 ft.) with LED lamp & batten for LED tube made of extruded aluminium / poly carbonate housing with integrated electronic driver suitable for operation on 220V, 50 Hz AC supply etc. with minimum 5 years OEM warranty as required. | 8.00 | Job |  | 500.00 | 4000.00 | 850.00 | 6800.00 | 540.00 | 4320.00 | 594.00 | 4752.00 | 4000.00 | MIDAS ELECTRICALS PVT LTD
27.00 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with piano type switch, phenolic laminated sheet, suitable size M.S./ PVC box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required. (GROUP C) | 16.00 | Point |  | 1250.00 | 20000.00 | 2560.00 | 40960.00 | 1100.00 | 17600.00 | 2400.00 | 38400.00 | 17600.00 | HPL Electric and Power Limited
28.00 | Supplying and fixing DP sheet steel enclosure confirming to IP 20 and IK 08 on surface/ recess along with 16 amps 240 volts “C” curve DP MCB complete with connections, testing and commissioning etc. as required. | 8.00 | Job |  | 1019.00 | 8152.00 | 2560.00 | 20480.00 | 500.00 | 4000.00 | 1545.00 | 12360.00 | 4000.00 | HPL Electric and Power Limited
29.00 | Wiring for circuit/submain wiring along with earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/recessed PVC conduit as required. 2 x 2.5 sq.mm + 1 x 2.5 sq.mm earth wire | 40.00 | Metre |  | 240.00 | 9600.00 | 260.00 | 10400.00 | 400.00 | 16000.00 | 485.00 | 19400.00 | 9600.00 | MIDAS ELECTRICALS PVT LTD
30.00 | Supplying and fixing PVC box suitable for fixing 2 sets of piano type 5/6 A switch and socket on surface or in recess etc. as required. | 8.00 | Each |  | 350.00 | 2800.00 | 896.00 | 7168.00 | 500.00 | 4000.00 | 68.00 | 544.00 | 544.00 | Instapower Ltd
31.00 | Supplying and fixing following piano type switch / socket on the existing switch box/ cover including connections etc. as required. 5/6 A switch | 16.00 | Each |  | 100.00 | 1600.00 | 320.00 | 5120.00 | 100.00 | 1600.00 | 68.00 | 1088.00 | 1088.00 | Instapower Ltd
32.00 | Supplying and fixing following piano type switch / socket on the existing switch box / cover including connections etc. as required. 3 pin 5/6 A socket outlet | 16.00 | Each |  | 200.00 | 3200.00 | 448.00 | 7168.00 | 200.00 | 3200.00 | 95.00 | 1520.00 | 1520.00 | Instapower Ltd
33.00 | SITC of 230V/50hz for 450mm (18") sweep wall mounted air circulator fan of approved make. | 8.00 | Job |  | 9500.00 | 76000.00 | 9601.00 | 76808.00 | 6000.00 | 48000.00 | 3300.00 | 26400.00 | 26400.00 | Instapower Ltd
34.00 | Laying of one number armoured XLPE insulated and PVC sheathed power cable of 1.1 KV grade of following size on wall surface as required. Upto 35 sq.mm | 40.00 | Metre |  | 300.00 | 12000.00 | 192.00 | 7680.00 | 50.00 | 2000.00 | 75.00 | 3000.00 | 2000.00 | HPL Electric and Power Limited
35.00 | Hire charges for providing one vehicle with driver (4 wheel, AC Bolero or equivalent) for attending the project execution and supervision of Perimeter Lighting system complete with required fuel, oil, insurance, road tax etc. in good condition on all days including Sundarys, Holidays and National Holidays complete as required. | 6.00 | Month |  | 85000.00 | 510000.00 | 98566.00 | 591396.00 | 360000.00 | 2160000.00 | 65000.00 | 390000.00 | 390000.00 | Instapower Ltd
| Total in Figures |  |  |  |  | 42736709.00 |  | 37738917.00 |  | 39321958.00 |  | 44084030.50
Lowest Amount Quoted BY: Bajaj Electricals Limited(37738917.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of Perimeter Lighting at Tuticorin Airport Tender ID: 2023_AAI_146971_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Bajaj Electricals Limited | 37738917.00 | L1
| 2 | HPL Electric and Power Limited | 39321958.00 | L2
| 3 | MIDAS ELECTRICALS PVT LTD | 42736709.00 | L3
| 4 | Instapower Ltd | 44084030.50 | L4