## BoQ1
Government eProcurement System Created By: Saubhik Pan Created Date/Time: 20-Apr-2023 05:47 PM Tender Title: Replacement of ILS System at Dibrugarh Airport SH Electrical Works for relocation of ILS Tender ID: 2023_AAI_147433_1
Tender Inviting Authority: Asstt. General Manager (Engg. Elect.), AAI, Dibrugarh Airport.
Name of Work: Replacement of ILS System at Dibrugarh Airport. SH: Electrical Works for relocation of ILS.
Contract No: AAI/DIB/ENGG-E/ILS/2022-23
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | M/s Lalowari Electricals(GSTN-18AAUPL4407G1ZG) |  | jaydeep agency corporation(GSTN-24ACIPP6157B1ZQ) |  | REWINDER TECHNO ELECTRICALS(GSTN-18AAFFR7457K1ZL) |  | Awasthi Electric Works(GSTN-09ABAPA1866D1Z5)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply of 1.5TR Hi-wall split AC unit (5-star rating - Inverter type), Copper Condensing unit (Outdoor Unit) including stabilizer and all standard accessories. | 4.00 | Each |  | 35183.00 | 140732.00 | 45000.00 | 180000.00 | 60000.00 | 240000.00 | 45000.00 | 180000.00 | 140732.00 | M/s Lalowari Electricals
2.00 | ITC of Hi-wall split AC Unit, Copper Condensing unit (Outdoor Unit), Voltage stabilizer, suitable rating SPN MCB, by making required support structure as per site requirement, Gas charging the system with refrigerent, including covering the Copper piping with nitrile rubber insulation with suitable size, PVC pipe Lifting / Shifting of Outdoor & Indoor units upto site location etc., complete as required. | 10.00 | Each |  | 4871.00 | 48710.00 | 2200.00 | 22000.00 | 500.00 | 5000.00 | 3500.00 | 35000.00 | 5000.00 | REWINDER TECHNO ELECTRICALS
3.00 | Supply of 4' x 1' wall mounted LED luminarie of 18-25W including all required accessories. Make & Model as directed by Engg-in-Charge. | 16.00 | Each |  | 839.00 | 13424.00 | 1800.00 | 28800.00 | 500.00 | 8000.00 | 2500.00 | 40000.00 | 8000.00 | REWINDER TECHNO ELECTRICALS
4.00 | Installation of 4' x 1' wall mounted LED luminarie including all required accessories etc., complete as required. | 30.00 | Each |  | 131.00 | 3930.00 | 50.00 | 1500.00 | 100.00 | 3000.00 | 250.00 | 7500.00 | 1500.00 | jaydeep agency corporation
5.00 | Installation of Outdoor LED luminarie including all required accessories. etc. complete as required. | 8.00 | Each |  | 196.00 | 1568.00 | 150.00 | 1200.00 | 100.00 | 800.00 | 250.00 | 2000.00 | 800.00 | REWINDER TECHNO ELECTRICALS
6.00 | Supply of portable LED Emergency light (rechargeable) of min. 5 watt with all accessories required to hung the light at a required height. Make & Model to be approved by Engg-in-Charge before supply. | 4.00 | Each |  | 1388.00 | 5552.00 | 2400.00 | 9600.00 | 100.00 | 400.00 | 3500.00 | 14000.00 | 400.00 | REWINDER TECHNO ELECTRICALS
7.00 | Installation of portable LED Emergency light with all accessories required to hung the light at a required height etc., complete as required. | 4.00 | Each |  | 131.00 | 524.00 | 100.00 | 400.00 | 100.00 | 400.00 | 250.00 | 1000.00 | 400.00 | jaydeep agency corporation, REWINDER TECHNO ELECTRICALS
8.00 | Supply of 1200 mm Sweep, Ceiling fan included required down rod and other standard accessories etc. for operation on 230V, 50 Hz, AC supply, etc. complete as required. | 2.00 | Each |  | 1887.00 | 3774.00 | 3200.00 | 6400.00 | 1000.00 | 2000.00 | 1750.00 | 3500.00 | 2000.00 | REWINDER TECHNO ELECTRICALS
9.00 | Installation of Ceiling fan including providing two module stepped type electronic fan regulator along with the PVC box and modular plate etc. complete as required. | 2.00 | Each |  | 702.00 | 1404.00 | 100.00 | 200.00 | 202.50 | 405.00 | 750.00 | 1500.00 | 200.00 | jaydeep agency corporation
10.00 | Supply of 4C x 16 sq.mm size, FRLS, 1.1KV grade, multicore PVC insulated and PVC sheathed armoured Copper conductor cable as per IS standards with upto date amendents as required. | 70.00 | Mtr |  | 1024.00 | 71680.00 | 1200.00 | 84000.00 | 450.00 | 31500.00 | 800.00 | 56000.00 | 31500.00 | REWINDER TECHNO ELECTRICALS
11.00 | Supply of 3.5C x 120 sq.mm size, 1.1KV grade, multicore XLPE insulated and PVC sheathed Aluminium conductor armoured power cable as per IS 7098:1998 (Part-I) with upto date amendents as required. | 2350.00 | Mtr |  | 632.00 | 1485200.00 | 825.00 | 1938750.00 | 1160.00 | 2726000.00 | 695.00 | 1633250.00 | 1485200.00 | M/s Lalowari Electricals
12.00 | Laying of one number PVC insulated and PVC sheathed/XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL pipe as required.
13.00 | Upto 35sq.mm | 65.00 | Mtr |  | 24.00 | 1560.00 | 30.00 | 1950.00 | 10.00 | 650.00 | 30.00 | 1950.00 | 650.00 | REWINDER TECHNO ELECTRICALS
14.00 | Above 95sqmm and upto 185sqmm | 2300.00 | Mtr |  | 49.00 | 112700.00 | 40.00 | 92000.00 | 10.00 | 23000.00 | 50.00 | 115000.00 | 23000.00 | REWINDER TECHNO ELECTRICALS
15.00 | Supply and Laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, joining etc. direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required.
16.00 | 63 mm dia (OD 63mm & ID-51 mm nominal) | 2200.00 | Mtr |  | 216.00 | 475200.00 | 250.00 | 550000.00 | 150.00 | 330000.00 | 250.00 | 550000.00 | 330000.00 | REWINDER TECHNO ELECTRICALS
17.00 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for 3.5 x 120 sq.mm PVC insulated and PVC sheathed /XLPE aluminium conductor cable of 1.1 KV grade as required. | 6.00 | Nos. |  | 3445.00 | 20670.00 | 2200.00 | 13200.00 | 2000.00 | 12000.00 | 3250.00 | 19500.00 | 12000.00 | REWINDER TECHNO ELECTRICALS
18.00 | Supplying and making end termination with brass compression gland and aluminium lugs for 3.5 x 120 sq.mm PVC/XLPE insulated and PVC sheathed aluminium conductor cable of 1.1 KV grade as required. | 8.00 | Set |  | 496.00 | 3968.00 | 750.00 | 6000.00 | 500.00 | 4000.00 | 650.00 | 5200.00 | 3968.00 | M/s Lalowari Electricals
19.00 | Design, Fabrication, Supply, Installtion, Testing and Commissioning of cubicle type, dust and vermin proof, indoor LT panel, IP 42 suitable for 415V ± 10%, 3 phase, 4 wire, 50Hz AC supply system fabricated in compartmentalised modular design as required from CRCA steel of 2mm thick for frame work and covers, 3mm thick for gland plate including supply & Installation of following Switchgears, metering Instrucments and accessories in the LT Panel as per specifications. INCOMER: 63A, DP MCB -1No. OUTGOING: 20A, DP MCB with provision of SPD of T3/40KA - 08 Nos. 10A, DP MCBwith provision of SPD of T3/40KA - 06 Nos. Neutral & Earth Bars. | 2.00 | Each |  | 37338.00 | 74676.00 | 95000.00 | 190000.00 | 50000.00 | 100000.00 | 45000.00 | 90000.00 | 74676.00 | M/s Lalowari Electricals
20.00 | Design, Fabrication, Supply, Installtion, Testing and Commissioning of cubicle type, floor mounting, dust and vermin proof, indoor LT panel, IP 42 suitable for 415V ± 10%, 3 phase, 4 wire, 50Hz AC supply system fabricated in compartmentalised modular design from CRCA steel of 2mm thick for frame work and covers, 3mm thick for gland plate including supply & Installation of following Switchgears, metering Instrucments and accessories in the LT Panel as per specifications. INCOMER 2 Nos. 63A, 4P, 25KA, MCCB with microprocessor based release unit with adjustable setting with O/L, S/C & E/F protection. 01 No. ATS (Automatic Transfer Switch) 63A, FP, 16KA complete as required.The ATS shall have all the four poles fully rated with Auto/Manual option. The ATS shall be supplied with an integrated controller and no external wiring harness shall be acceptable. 1 Nos. 63A, TPN, 16KA, MCCB with microprocessor based release unit with adjustable setting with O/L, S/C & E/F protection. Incomer shall have the following items: 0-500V Digital Voltameter, 96mm square flush pattern, with selector switch and 3 No. Phase Indicating LED lamps with back up 2A MCB - 1 set; 0-100A Digital Ammeter with selector switch and one set of suitable resin cast CTs of ratio 100/5A, Class I accuracy and 15VA burden - 1 set; Multifunction meter - 1set; Power data logger which can store data upto 03 days - 1 set; Surge Protection Device (SPD) of T2/50KA capacity with TPN MCB - 1 set.
21.00 | BUSBARS TPN Aluminium bus bars of minimum capcaity 100A with heat shrinkable coloured sleeves including SMC bus bars supports at required intervals complete for cross section, size supports & their spacing etc. for withstanding fault level of 25KA for 1 sec. OUTGOING 63A, 4P, MCCB - 1 No. with SPD of T2/50KA capacity with backup TPN MCB 63A, 4P, MCCB - 1 No. 40A, TPN, MCB - 1 No. 32A, DP, RCBO (100mA) - 4 No. 20A, DP, MCB - 7 No. 10A, DP, MCB - 6 No. Note: All breakers breaking capacities shall be Icu=Ics. All thermal based release MCCBs shall be comparatmenalised and provided with inbuilt O/L, S/C protection & E/F module with CBCT or Earth fault relay with required CT releases shall be provided. All MCCBs shall be provided with ON, OFF & TRIP indication lamp (LED type) with 2A SP MCB and 1 set Rotary operating mechanism and terminal expansion spreaders . | 2.00 | Each |  | 137721.00 | 275442.00 | 220000.00 | 440000.00 | 170000.00 | 340000.00 | 525000.00 | 1050000.00 | 275442.00 | M/s Lalowari Electricals
22.00 | Supply and fixing of suitable size PVC box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 5/6 & 15/16 amps modular socket outlet and 15/16 amps modular switch with indicator, connection etc. as required. | 50.00 | Nos. |  | 464.00 | 23200.00 | 250.00 | 12500.00 | 500.00 | 25000.00 | 900.00 | 45000.00 | 12500.00 | jaydeep agency corporation
23.00 | Wiring for circuit/ submain wiring along with earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required.
24.00 | 2 X 2.5 sq. mm + 1 X 2.5 sq. mm earth wire | 150.00 | Mtrs |  | 201.00 | 30150.00 | 200.00 | 30000.00 | 100.00 | 15000.00 | 250.00 | 37500.00 | 15000.00 | REWINDER TECHNO ELECTRICALS
25.00 | 2 X 4 sq. mm + 1 X 4 sq. mm earth wire | 150.00 | Mtrs |  | 247.00 | 37050.00 | 300.00 | 45000.00 | 100.00 | 15000.00 | 300.00 | 45000.00 | 15000.00 | REWINDER TECHNO ELECTRICALS
26.00 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with modular switch, modular plate, suitable PVC box and earthing the point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable etc. as required. Group C | 16.00 | Points |  | 1051.00 | 16816.00 | 2000.00 | 32000.00 | 500.00 | 8000.00 | 1200.00 | 19200.00 | 8000.00 | REWINDER TECHNO ELECTRICALS
27.00 | Wiring for group controlled (looped) light point/fan point/exhaust fan point/ call bell point (without independent switch etc.) with 1.5 sq. mm FRLS PVC insulated copper conductor single core cable in surface/ recessed medium class PVC conduit, and earthing the point with 1.5 sq. mm FRLS PVC insulated copper conductor single core cable etc. as required.Group C | 14.00 | Points |  | 621.00 | 8694.00 | 1400.00 | 19600.00 | 500.00 | 7000.00 | 1300.00 | 18200.00 | 7000.00 | REWINDER TECHNO ELECTRICALS
28.00 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 6.00 | Set |  | 5472.00 | 32832.00 | 7890.00 | 47340.00 | 4000.00 | 24000.00 | 10000.00 | 60000.00 | 24000.00 | REWINDER TECHNO ELECTRICALS
29.00 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required | 4.00 | Set |  | 10388.00 | 41552.00 | 11500.00 | 46000.00 | 6000.00 | 24000.00 | 20000.00 | 80000.00 | 24000.00 | REWINDER TECHNO ELECTRICALS
30.00 | Supplying and laying 25 mm X 5 mm copper strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 Sets of brass nut bolt & spring washer spaced at 50mm) | 30.00 | Mtrs |  | 745.00 | 22350.00 | 1000.00 | 30000.00 | 500.00 | 15000.00 | 1200.00 | 36000.00 | 15000.00 | REWINDER TECHNO ELECTRICALS
31.00 | Supplying and laying 25 mm X 5 mm G.I strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with G.I. nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 Sets of G.I. nut bolt & spring washer spaced at 50mm) | 50.00 | Mtrs |  | 101.00 | 5050.00 | 200.00 | 10000.00 | 250.00 | 12500.00 | 325.00 | 16250.00 | 5050.00 | M/s Lalowari Electricals
32.00 | Providing and fixing 25 mm X 5 mm copper strip on surface or in recess for connections etc. as required | 30.00 | Mtrs |  | 882.00 | 26460.00 | 1050.00 | 31500.00 | 500.00 | 15000.00 | 1025.00 | 30750.00 | 15000.00 | REWINDER TECHNO ELECTRICALS
33.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required | 30.00 | Mtrs |  | 173.00 | 5190.00 | 225.00 | 6750.00 | 250.00 | 7500.00 | 200.00 | 6000.00 | 5190.00 | M/s Lalowari Electricals
34.00 | Supplying, installation, testing and commissioning of micro processor based intelligent addressable main fire alarm panel, central processing unit with following loop modules and capable of supporting not less than 240 devices (including detectors) and minimum 120 detectors per loop and loop length up to 2 km, network communication card, minimum 320 character graphics/ LCD display with touch screen or other keypad and minimum 4000 events history log in the non volatile memory (EPROM), power supply unit (230 ± 5 % V, 50 hz), 48 hrs back-up with 24 volt sealed maintenance free batteries with automatic charger. The panel shall have facility to connect printer to printout log and facility to have seamless integration with analog/digital voice evacuation system and shall be complete with all accessories . The panel shall be compatible for IBMS system with open protocol Bacnet/ Modbus over IP complete as per specifications.
35.00 | one loop panel | 2.00 | Each |  | 131641.00 | 263282.00 | 38500.00 | 77000.00 | 100000.00 | 200000.00 | 120000.00 | 240000.00 | 77000.00 | jaydeep agency corporation
36.00 | Supply & fixing of Photoelectric, Multi sensor smoke detectors along with mounting base with unique optical sensing chamber, visible LED's complete with all accessories including connections etc. as required. (As per approved makes list) | 8.00 | Each |  | 2200.00 | 17600.00 | 4200.00 | 33600.00 | 2000.00 | 16000.00 | 3100.00 | 24800.00 | 16000.00 | REWINDER TECHNO ELECTRICALS
37.00 | Supplying, installation, testing & commissioning of response indicator on surface/recessed MS Box having two LED, metallic cover complete with all connections etc as required. | 4.00 | Each |  | 205.00 | 820.00 | 1200.00 | 4800.00 | 700.00 | 2800.00 | 750.00 | 3000.00 | 820.00 | M/s Lalowari Electricals
38.00 | Supplying & laying of 2 x 1.5 sqmm fire survival armoured cable, 600 / 1000V rated with annealed copper conductor havingh glass mica fire barrier tape covered by extruded layer of Cross Linkable Ethylene Propylene Rubber (EPR) insulation and LSZH inner bedding, steel wire armouring & LSZH outer sheath as required. | 80.00 | Mtrs |  | 272.00 | 21760.00 | 128.00 | 10240.00 | 200.00 | 16000.00 | 110.00 | 8800.00 | 8800.00 | Awasthi Electric Works
39.00 | Supply and installation of ABC Fire extinguishers of 6 kg capacity (high quality) as per latest IS standards including the supporting stand and accessories etc. complete as required. | 4.00 | Nos. |  | 6790.00 | 27160.00 | 6500.00 | 26000.00 | 1000.00 | 4000.00 | 4400.00 | 17600.00 | 4000.00 | REWINDER TECHNO ELECTRICALS
40.00 | SITC of auto dialer (Voice and SMS) having facitlity of storing voice message & min. 10 contact numbers with all necessary accessories including SIM, 1 year recharge, connections beween fire alarm panel etc, complete as required. | 2.00 | Job |  | 14015.00 | 28030.00 | 42500.00 | 85000.00 | 5000.00 | 10000.00 | 9500.00 | 19000.00 | 10000.00 | REWINDER TECHNO ELECTRICALS
41.00 | Supply and Installation of Intelligent timer for cyclical operation of 2 AC units at 4-8hrs including required wiring and other accessories etc. comple as required. | 4.00 | Job |  | 2943.00 | 11772.00 | 4800.00 | 19200.00 | 2000.00 | 8000.00 | 10000.00 | 40000.00 | 8000.00 | REWINDER TECHNO ELECTRICALS
42.00 | Design, Fabrication, Supply, Installation, Testing and Commissioning of cubicle type, floor mounting, dust and vermin proof, outdoor LT panel, IP 54 suitable for 415V ± 10%, 3 phase, 4 wire, 50Hz AC supply system fabricated in compartmentalised modular design from CRCA steel of 2mm thick for frame work and covers, 3mm thick for gland plate including supply & Installation of following Switchgears, metering Instruments and accessories in the LT Panel as per specifications. INCOMER 2 Nos. 100A, 4P, 25KA, MCCB with thermal magnetic based release unit with O/L, S/C & E/F protection. 01 No. Manual Changeover switch, 100A, 4P with source status & phase indication LED lamps with back up 6A, SP, MCB Each Incomer shall have the following items: 0-500V Digital Voltmeter, 96mm square flush pattern, with selector switch and 3 No. Phase Indicating lamps with back up 6A, SP, MCB - 1 set 0-100A Digital Ammeter with selector switch and one set of 3Nos CTs of ratio 100/5A, Class I accuracy and 15VA burden - 1 set BUSBARS TPN Aluminium bus bars of minimum capcaity 100A with heat shrinkable coloured sleeves with SMC bus bars supports as required., for withstanding fault level of 25KA for 1 sec. OUTGOING 40A, 4P, MCB with Astro Timer with ON/OFF indication lamps including provision of Contactor 3P, 40A with start, stop push button & auto/manual selection- 3 sets 40A, 4P, MCB - 2 Nos. Neutral & Earth Bars. Note: All MCCBs shall be provided with ON, OFF indication lamp with 6A, SP MCB and 1 set Rotary operating mechanism and terminal expansion spreaders . All incomers and outgoings shall be compartmentalized. | 3.00 | Job |  | 78095.00 | 234285.00 | 260000.00 | 780000.00 | 65000.00 | 195000.00 | 272500.00 | 817500.00 | 195000.00 | REWINDER TECHNO ELECTRICALS
| Total in Figures |  |  |  |  | 3594767.00 |  | 4912530.00 |  | 4446955.00 |  | 5370000.00
Lowest Amount Quoted BY: M/s Lalowari Electricals(3594767.00)

## BOQ Summary
BOQ Summary Details Tender Title: Replacement of ILS System at Dibrugarh Airport SH Electrical Works for relocation of ILS Tender ID: 2023_AAI_147433_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | M/s Lalowari Electricals | 3594767.00 | L1
| 2 | REWINDER TECHNO ELECTRICALS | 4446955.00 | L2
| 3 | jaydeep agency corporation | 4912530.00 | L3
| 4 | Awasthi Electric Works | 5370000.00 | L4