## BoQ1
Government eProcurement System Created By: Sanjib Kumar Dey Created Date/Time: 31-Mar-2023 03:53 PM Tender Title: Replacement of Normal DG set to Silent DG set and Modification of existing Panel Tender ID: 2023_AAI_147505_1
Tender Inviting Authority: AGM(E-E), AAI, RHQ, ER
Name of Work: Replacement of Normal DG Set to Silent DG set and Modification of existing panel at Bagjola Tx. Station.
Contract No: AAI/ER/KOL/EE/NIT-15/2022-23
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | DOSHI ELECTRIC ENGG. CO.(GSTN-24AAEFD3355K1ZI) |  | M/s J.K. Electric Engineering Works(GSTN-19AAHFJ4404E1ZL) |  | Youngmen Traders(GSTN-19AEIPB6323B1ZZ) |  | Mona Generator Services Pvt. Ltd.(GSTN-07AAFCM4263P1ZZ)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Design, Supply, Assembling, Installation , Teating & Commissioning of oil filled 250KVA, 6.6/0.415KV + 5%, 3 Phase, 50Hz, Dyn 11 vector group copper wound class F for natural easter oil immersed (IS: 16659:2017), KNAN cooled complete with all fittings such as Air cell oil conservator, Silica Gel Breather Thermometer PRV etc. having impedance as per IS-2026 and conforming green initiative EEL1, Griha rated associated with winding temperature indicator / digital controller, temperature detector outdoor type Transformer. The transformer shall be provided with +5% to -10% in steps of 2.5% each On load tap changer on HT side. The transformer shall has bydirectional rollers, winding temperature indicator and Buchholz Relay with wiring upto the marshaling box and also shall have min 8mm thick Non-magnetic Gland Plate, on-line Health Monitoring system, Provision for intigration with NIFPS. Transformer shall has first filling of oil, weather proof cable end boxes on HV side suitable for 3C X 120sq.mm XLPE cable of 11KV grade and 630Amp aluminum bus trunking arrangement of LV side with neutral brought out separately, provision of surge arrestor on HT side including supplying and grouting suitable MS channels with all accessories for mounting arrangement and confirming to relevant standard as amended upto date & as per Technical specification and as Directed by E.I.C. Note: Before quoting the price Agency should visit the site of execution, understand the requrement and go through the entire Tender document. No deviation will be accepted after placeing of purchase order. | 1.00 | Job |  | 1400000.00 | 1400000.00 | 800000.00 | 800000.00 | 1180000.00 | 1180000.00 | 1750000.00 | 1750000.00 | 800000.00 | M/s J.K. Electric Engineering Works
2.00 | Supply, Installation , Teasting & Commissioning of indoor type floor mounted metal clad , 11KV Switch Board VCB Panel with 02 Nos VCBs, totally enclosed & fully interlocked, truck mounting, horizontal draw out, horizontal isolation type vaccum breaker as per IS/IEC 62271-100 (2007) for breakers 200 (2003), for panels / IS3247 as amended up to date , having capacities as mentioned below, free standing extensible on both sides , single break, trip free mechanism, motorised charged and auto / manually closed breaker suitable for use on 11KV , 3 Phase , 50Hz short circuit fault level of 500MVA, complete with self contained short time current 26.3kA for 3sec, Internal Arc Test for AFLR 26.3kA for 1sec at individual compartments i.e. busbar VCB and cable compartment , rack in and rack out machanism, air insulated but encapsulated copper bus bars capacity meeting fault level current , DC power pack, breaker featured with mechanical ON/OFF indicator with hand trip device , Breaker control TNC switch and all accessories as shunt trip coil, and auxiliary switch of 4NO + 4NC, motorised and manually operated spring assisted closing mechanism, emergency trip push button, interconnections, space heater, earthing etc. and equipped with following switchgears and accessories, connections suitable for cable upto 3C X 120sqmm XLPE cable of 11KV grade (cable entry from bottom), Separate earthing switch shall be provided for cable earthing. The earthing trunk shall be so designed that it is impossible to earth a live. cable terminatiuons suitable for 3C X 120sq.mm. XLPE 11KV Cable including obtaining necessary approval form CEA before energisation of VCB and getting the end termination done by CESC etc. as required. | 1.00 | Job |  | 1400000.00 | 1400000.00 | 1500000.00 | 1500000.00 | 1450000.00 | 1450000.00 | 1075000.00 | 1075000.00 | 1075000.00 | Mona Generator Services Pvt. Ltd.
3.00 | NON-ESSENTIAL MAIN LT PANEL :- Design, manufacture and supply main LT Panel, cubicle & modular type, made of 2 mm thick sheet steel for frame work and covers, 3mm thick for gland plates, totally enclosed, IP 54, free standing, floor mounting, dust and vermin proof, indoor, compartmentalised, including cleaning & finishing complete with 7 tank process, powder coated, painting, suitable for operation on 3 Phase and neutral, 415v, 50 Hz AC system with Alluminium busbars extensible on both sides, fabrication shall be done in transportation sections, entire panel shall have a common copper earth bar of size 25mm x 5mm at the rear with 2 nos. earth stud, control wiring with 2.5 sq.mm. PVC insulated copper conductor, cable alloys, cable gland plates in two half, interconnections including supply & installation of following items and as per technical specification: (A) INCOMER :- i) 2 nos. 320A MCCB, FP, fault braking capacity (Ics=Icu upto 433V) 50 kA, with thermal magnetic release having short circuit (Ics=Icu), over current, earth fault with Electrically and Manually interlocking arrangements with extended rotary handle ii) 2 nos. Digital Voltmeter, accuracy class 1, suitable range for 3 phase, 4 wire operation with LED display and built-in selector switch along with 2 nos. of 6 Amp SP / MCBs., iii) 2 sets Indication Lamps, LED type for R,Y,B and breaker 'ON' , 'OFF', 'TRIP' indications with 6 Amp MCBs for protection., iii) Digital Multifunctional Meter of suitable range fitted with RS485 Port and compatrible for intregation with data logger system along with 2 nos. of 2 Amp SP / MCBs - 2 sets. ( B) Bus Bars :- 1 set of high conductivity Alluminium bus bars of 400A , 4P with heat shrinkable coloured sleeves and i/c DMC/SMC busbars supports at required intervals. (C) Bus coupler:- i) 1 No.320A MCCB FP, 50 kA, with thermal magnetic release type for interconnection between 02 Nos Incomers with extended rotary handleii) 1 Set Indication Lamps, LED type for 'ON' , 'OFF', 'TRIP' indications with 6 Amp SP/MCBs, auxiliary contact contactors for positive electrical interlocking of breakers etc. as required. (D) Accessories for Electrical & Mechanical Interlocking :- Electrical & mechanical interlocking arrangement among 2 nos. Incomers and 1 no. Bus coupler including interconnections etc. as required. (E) Outgoing :- i) 2 Nos. MCCB, 250A, 35 kA, Four Pole , With Thermal magnatic release having Over Current and , Short Circuit Current Settings,(Ics=Icu) . ii) 2 Nos. MCCB, 200A, 35 kA, Four Pole, with Thermal magnatic release having Over Current and , Short Circuit Current Settings,(Ics=Icu). iii) 2 Nos. MCCB, 125A, 35 kA, Four Pole, with Thermal magnatic release having Over Current and , Short Circuit Current Settings, (Ics=Icu). vi) 06 Sets (1 Set for each Outgoing MCCB) of Indicating lamps, LED type, for breaker "ON", "OFF", "TRIP" indication with HRC control fuses/MCBs., vii) 06 Sets (1 set for each MCCB) of Extended Rotary operating mechanism, terminal extension spreaders . | 1.00 | Set |  | 700000.00 | 700000.00 | 800000.00 | 800000.00 | 550000.00 | 550000.00 | 688495.00 | 688495.00 | 550000.00 | Youngmen Traders
4.00 | ESSENTIAL LT PANEL :- Design, manufacture supply LT Panel, cubicle & modular type, made of 2 mm thick sheet steel for frame work and covers, 3mm thick for gland plates, totally enclosed, IP 54, free standing, floor mounting, dust and vermin proof, indoor, compartmentalised, including cleaning & finishing complete with 7 tank process, powder coated, painting, suitable for operation on 3 Phase and neutral, 415v, 50 Hz AC system with Alluminium busbars extensible on both sides, fabrication shall be done in transportation sections, entire panel shall have a common copper earth bar of size 25mm x 5mm at the rear with 2 nos. earth stud, control wiring with 2.5 sq.mm. PVC insulated copper conductor, cable alloys, cable gland plates in two half, interconnections including supply & installation of following items and as per technical specification: (A) INCOMER:- i) 2 Nos. FP 250A,35KA MCCB with thermal magnetic release having short circuit (Ics=Icu), over current, earth fault with Electrically and Manually interlocking arrangements along with extended rotary handle , ii) Digital Multifunctional Meter of suitable range fitted with RS485 Port and compatrible for intregation with data logger system along with 2 nos. of 6 Amp SP / MCBs - 2 set. iii) 2 Sets Indication Lamps, LED type, R,Y,B and breaker 'ON', 'OFF', 'TRIP' lamps each with 2 Amp. SP MCB, (B) Bus coupler:- i) 1 No.250A MCCB FP, 35 kA, with thermal magnetic release type for interconnection between 02 Nos Incomers with extended rotary handle , ii) 1 Set Indication Lamps, LED type for 'ON' , 'OFF', 'TRIP' indications with 2 Amp SP/MCBs, auxiliary contact contactors for positive electrical interlocking of breakers etc. as required. (C) Accessories for Electrical & Mechanical Interlocking :- Electrical & mechanical interlocking arrangement as per drawing and specifications among 2 nos. Incomers and 1 no. Bus coupler including interconnections etc. as required. (D) Alluminium Bus Bars :- 1 set of high conductivity Alluminium bus bars of Size 40 x 10mm , 4P with heat shrinkable coloured sleeves and i/c DMC/SMC busbars supports at required intervals. (D) Outgoing :- i) 04 Nos-200A,415V, 35 KA Rating 4P MCCB with thermal magnetic release having short circuit (Ics=Icu), over current, earth fault along with extended rotary handle. (ii) 06 Nos 125A, 415V, 35 KA Rating 4P MCCB with thermal magnetic release having short circuit (Ics=Icu), over current, earth fault along with extended rotary handle (iii) 10 Sets of Indicating lamps, LED type, for breaker "ON", "OFF", "TRIP" indication with 2 Amp SP MCBsminal extension spreaders and 'ON' (Red) indication lamp (LED type) with 2 Amp SP control fuse/MCBs | 1.00 | Set |  | 620000.00 | 620000.00 | 600000.00 | 600000.00 | 500000.00 | 500000.00 | 798465.00 | 798465.00 | 500000.00 | Youngmen Traders
5.00 | 160 KVA SILENT TYPE DG SET WITH DG SET CONTROL MODULE :- Supply, installation, testing and commissioning of 160 KVA Silent type D.G Set with DG set controller module mounted on DG set, having AMF control Panel(separate), auto load management, inbuilt metering & protection, communicable port (RS485) etc. and acoustic enclosure conforming to latest environment protection regulations for emmission and noise levels complete with Diesel Engine of suitable BHP (considering de-rating factor if any) at 1500 RPM, water / oil cooled Radiator, four stroke, electric start, turbo-charged & after cooled conforming to BS: 5514 with all standard accessories,coupled with Alternator of 160 KVA rating, brushless, self excited, self regulated and suitable for continuous operation , generating 415 V+/-5% Volts at 0.8 PF ( lag), 50Hz, 3 phase, 4 wire system generally conforming to BS: 2613 & IS: 4722. Both Engine and Alternator shall be mounted on common channel iron base frame, with Internal Fuel tank and fuel pipe line upto 10 meter ( to be concealed under floor), exhaust pipe line upto 15 meter ( to be erected with sufficient M.S supports and insulated, hood on top). Antivibration mountings, residential type silencer, electric starter, batteries & battery charger, other standard accessories etc complete as required. ( Refer Technical specification) | 2.00 | Each |  | 1500000.00 | 3000000.00 | 1100000.00 | 2200000.00 | 1100000.00 | 2200000.00 | 1660000.00 | 3320000.00 | 2200000.00 | M/s J.K. Electric Engineering Works, Youngmen Traders
6.00 | Design, SITC of automatic mains change over panel (AMF) made out of 14 SWG sheet steel powder coated capable to deliver and transfer the full load from the normal source to DG emergency source within a switch over time of 3 to 15 seconds with three attempts. The Panel is suitable for continuous rating and have the following accessories. The automatic main transfer panel shall be provided with the protection gear, instruments and accessories as per Technical specification. a) 4 pole 250 A MCCB unit - 2 Nos. b) The main & Generator power contactor shall be of 4 poles 320 A (min) - 2 Nos. c) 4 pole, 320 A common copper busbar. d) By-pass arrangement for main and DG with 4 pole on load changeover switches 320 Amp (min) 2 numbers in a sub compartment e) AC & DC voltmeters (Digital) and AC & DC ammeters (Digital) with selector switches, HRC control fuses and CTs as required. f) Digital energy meter and frequency meter g) Battary charger (for boost & tickle charging) with selector switches for volts & current & ON / OFF in a compartment. h) Audio visual signal indicator with macro processor based relay to indicate the abnormality of engine and various faults in a sub compartment. (for engine low lube oil pressure, high cylinder head temp. DG set fails to start, OL/OC/EF/UV/OV/Signal phasing etc) indication for load on mains, load on Genset. i) Push buttons for engine start, stop ,test, accept, reset, contactor ON, contactor OFF. j) Selector switches - auto/ manual/ test & off, Source selection switch for volt & current and control supply ON/OFF switch etc. k) 12/24 V DC control circuit, line voltage monitor, three attempts starter, relays for over current, earth fault, under voltage, over voltage, reverse power and all other required components & circuit. i) Interconnection between DG set and AMF panel with copper conductor / control cable as per site requirement. | 2.00 | Each |  | 450000.00 | 900000.00 | 850000.00 | 1700000.00 | 300000.00 | 600000.00 | 419449.00 | 838898.00 | 600000.00 | Youngmen Traders
7.00 | Supply, installation, testing and commissioning of Desiccant type table top Dehumidifier manufactured by an ISO 9001:2015 and ISO14001:2015CE certified Indigenous manufacturer having own in-house manufacturing facility of desiccant rotor and after-sales-service set-up in Kolkata/Eastern Region of capacity 600CMH (360CFM) including angle iron support for fixing in the wall suitable for operation 415Volts, 50 Hz, 3Phase AC supply of collected load 8 KW (approx.) made of Robust stainless steel frame with double skin insulated construction casing frame work SS tubular industrial quality EU-4filter, proces blower and motor, requisit number of dampers high efficiency desiccant roter comforming to sefety standard as per UL1995CSA C22.2 No.236-11,DIN EN ISO846, ASTM E84-13A. The Dehumidifier must consist of built in sensors, 100% electrical regeneration system and PLC based control panel with HMI and 7" touch screen for temp & RH display , fault management with Modbus / Backnet BMS connectivity and all above components housed in a vapour tight complying to SMA CNA Class 6 integrated engineered unit mounted on a common frame work and assembled & functionally tested at manufacturer's plant, approx dimension 0.89 mtr. (L) into 0.63 mtr. (W) into 0.49 mtr. (H) approx. weight 500kg complete as required as per Technical specsification or Similer to Make: Bry-Air, Model no. FFB -600 | 2.00 | Set |  | 400000.00 | 800000.00 | 500000.00 | 1000000.00 | 350000.00 | 700000.00 | 400000.00 | 800000.00 | 700000.00 | Youngmen Traders
8.00 | Supply of following sizes of XLPE insulated PVC sheathed aluminium conductor armoured power cable of 11 KV grade (11 KV earthed system) conforming to IS : 7098 ( Part-II) amended upto date.
8.10 | 3 Core x 120 Sq.mm. | 100.00 | Mtr. |  | 1000.00 | 100000.00 | 1326.00 | 132600.00 | 700.00 | 70000.00 | 796.00 | 79600.00 | 70000.00 | Youngmen Traders
9.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 11 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required.
9.10 | Upto 120 sq. mm | 50.00 | Mtr. |  | 400.00 | 20000.00 | 400.00 | 20000.00 | 250.00 | 12500.00 | 270.00 | 13500.00 | 12500.00 | Youngmen Traders
10.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 11KV grade of following size in the existing RCC/ HUME/ METAL pipe as required.
10.10 | Upto 120 sq. mm | 50.00 | Mtr. |  | 60.00 | 3000.00 | 40.00 | 2000.00 | 40.00 | 2000.00 | 50.00 | 2500.00 | 2000.00 | M/s J.K. Electric Engineering Works, Youngmen Traders
11.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 11KV grade of following size in the existing masonry open duct as required.
11.10 | Upto 120 sq. mm | 40.00 | Mtr. |  | 80.00 | 3200.00 | 40.00 | 1600.00 | 20.00 | 800.00 | 35.00 | 1400.00 | 800.00 | Youngmen Traders
12.00 | Supplying and making indoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for following size of 3 core, XLPE aluminium conductor cable of 11 KV grade as required
12.10 | For 3 Core 120 Sq.mm cable | 4.00 | Sets |  | 4500.00 | 18000.00 | 7000.00 | 28000.00 | 6000.00 | 24000.00 | 7500.00 | 30000.00 | 18000.00 | DOSHI ELECTRIC ENGG. CO.
13.00 | Laying and fixing of one number armoured PVC insulated and PVC sheathed/XLPE power cable 1.1 kV of following size in the existing cable Trays/ Surface including providing suitable size clamp to secure the cable in tray/ surface as required.
13.10 | Above 35 Sq.mm. and upto 95 sq.mm (clampad with 25x3mm MS flat clamp) | 50.00 | Mtr |  | 120.00 | 6000.00 | 80.00 | 4000.00 | 70.00 | 3500.00 | 70.00 | 3500.00 | 3500.00 | Youngmen Traders, Mona Generator Services Pvt. Ltd.
13.20 | Above 185 sq.mm and upto 400 sq.mm (clampad with 40x3mm MS flat clamp) | 50.00 | Mtr. |  | 140.00 | 7000.00 | 130.00 | 6500.00 | 125.00 | 6250.00 | 155.00 | 7750.00 | 6250.00 | Youngmen Traders
14.00 | Laying of one number PVC insulated and PVC sheathed/XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ STONEWARE/ METAL/CORRUGATED PIPE as required.
14.10 | Above 35 Sq.mm. and upto 95 sq.mm | 20.00 | Mtr. |  | 60.00 | 1200.00 | 40.00 | 800.00 | 35.00 | 700.00 | 35.00 | 700.00 | 700.00 | Youngmen Traders, Mona Generator Services Pvt. Ltd.
14.20 | Above 185 sq.mm and upto 400 sq.mm | 40.00 | Mtr. |  | 80.00 | 3200.00 | 40.00 | 1600.00 | 40.00 | 1600.00 | 110.00 | 4400.00 | 1600.00 | M/s J.K. Electric Engineering Works, Youngmen Traders
15.00 | Laying of one number PVC insulated and PVC sheathed/XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required.
15.10 | Above 35 Sq.mm and upto 95 sq.mm | 80.00 | Mtr. |  | 60.00 | 4800.00 | 35.00 | 2800.00 | 20.00 | 1600.00 | 40.00 | 3200.00 | 1600.00 | Youngmen Traders
15.20 | Above 185 Sq.m and upto 400 sq.mm | 160.00 | Mtr. |  | 80.00 | 12800.00 | 65.00 | 10400.00 | 35.00 | 5600.00 | 100.00 | 16000.00 | 5600.00 | Youngmen Traders
16.00 | Supplying and making end termination with brass compression gland and Aluminum lugs for following size of XLPE insulated PVC sheathed aluminium conductor armoured power cable of 1.1 KV grade as required.
16.10 | 3.5 Core 240 Sq.mm. | 6.00 | Sets |  | 1200.00 | 7200.00 | 950.00 | 5700.00 | 400.00 | 2400.00 | 11392.00 | 68352.00 | 2400.00 | Youngmen Traders
16.20 | 3.5 Core 70 Sq.mm. | 6.00 | Sets |  | 800.00 | 4800.00 | 400.00 | 2400.00 | 300.00 | 1800.00 | 495.00 | 2970.00 | 1800.00 | Youngmen Traders
17.00 | Supply and making cable route marker with cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) of size 60 cm X 60 cm at the bottom and 50 cm X 50 cm at the top with a thickness of 10 cm including inscription duly engraved as required. | 6.00 | Each |  | 300.00 | 1800.00 | 550.00 | 3300.00 | 200.00 | 1200.00 | 1500.00 | 9000.00 | 1200.00 | Youngmen Traders
18.00 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 6.00 | Sets |  | 18000.00 | 108000.00 | 14000.00 | 84000.00 | 11000.00 | 66000.00 | 13500.00 | 81000.00 | 66000.00 | Youngmen Traders
19.00 | Supplying and laying 25 mm X 5 mm copper strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of brass nut bolt & spring washer spaced at 50mm) | 20.00 | Mtrs. |  | 1200.00 | 24000.00 | 850.00 | 17000.00 | 750.00 | 15000.00 | 975.00 | 19500.00 | 15000.00 | Youngmen Traders
20.00 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 10.00 | Sets |  | 8000.00 | 80000.00 | 6000.00 | 60000.00 | 5500.00 | 55000.00 | 7100.00 | 71000.00 | 55000.00 | Youngmen Traders
21.00 | Supplying and laying 25 mm X 5 mm G.I strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with G.I. nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of G.I. nut bolt & spring washer spaced at 50mm) | 20.00 | Mtrs. |  | 200.00 | 4000.00 | 130.00 | 2600.00 | 115.00 | 2300.00 | 165.00 | 3300.00 | 2300.00 | Youngmen Traders
22.00 | Providing and fixing 25 mm X 5 mm copper strip in 40 mm dia G.I. pipe from earth electrode including connection with brass nut, bolt, spring, washer excavation and re-filling etc. as required. | 60.00 | Mtrs. |  | 1800.00 | 108000.00 | 1350.00 | 81000.00 | 1100.00 | 66000.00 | 1275.00 | 76500.00 | 66000.00 | Youngmen Traders
23.00 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc.as required. | 60.00 | Mtrs. |  | 700.00 | 42000.00 | 600.00 | 36000.00 | 400.00 | 24000.00 | 465.00 | 27900.00 | 24000.00 | Youngmen Traders
24.00 | Providing and fixing 25 mm X 5 mm copper strip on surface or in recess for connections etc. as required. | 20.00 | Mtrs. |  | 1100.00 | 22000.00 | 900.00 | 18000.00 | 800.00 | 16000.00 | 955.00 | 19100.00 | 16000.00 | Youngmen Traders
25.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | 30.00 | Mtrs. |  | 200.00 | 6000.00 | 130.00 | 3900.00 | 115.00 | 3450.00 | 145.00 | 4350.00 | 3450.00 | Youngmen Traders
26.00 | Supply and fixing of flame retardant electrical insulation mat CPRI approved of 3.0 mm thick size 1 meter x 2 meter to withstand upto 33 kV conforming to IS 15652:2006 with upto date amendments and having minimum width 1000mm (+ 20mm). The sufficient of adhesive / compound shall be supplied to fix the insulation mat on the front/rear side of electrical installation. Mat shall be ISI marked. Its leakage curent at 11 KV shall not be more than 10 MA. The mat shall be welded by hot gas welding with filler matrial method by making V grove cut at joints with suitable welding cord of insulating material of matching colour to provide a seamless jointed surface as per IS :8002. | 6.00 | Each |  | 1500.00 | 9000.00 | 2200.00 | 13200.00 | 3600.00 | 21600.00 | 3000.00 | 18000.00 | 9000.00 | DOSHI ELECTRIC ENGG. CO.
27.00 | SITC of roxylene based high standerd, high efficient, world class, superior quality, innovative, light weight, space saving, tailor made, most flexible (modular design with peel-able multidiameter technology to adjust the various diameter, single/ multiple cable & conduit) rectangular, round steel framed, transit / entry (Through walls, cable tranches, cable pit, panels etc) sealing solution including frame, modules, wedge / compression unit, stay plate, and lubricant gel all as a standard kit, suitable for a new as well as preinstallation following sites with required sizes cutout including numbers of cable entry with diameter as required.
27.10 | HT cable entry at Badu having cutout size 120mm , cable Diameter 56 mm-01 nos and 04 nos 30x3 earth strip. | 1.00 | Job |  | 45000.00 | 45000.00 | 51000.00 | 51000.00 | 45000.00 | 45000.00 | 3200.00 | 3200.00 | 3200.00 | Mona Generator Services Pvt. Ltd.
27.20 | HT cable entry-2 at Rx Old power house having cutout size 450x450mm , cable Diameter 57,36,18, mm-03 nos. (01no.each size) | 1.00 | Job |  | 45000.00 | 45000.00 | 51000.00 | 51000.00 | 45000.00 | 45000.00 | 3600.00 | 3600.00 | 3600.00 | Mona Generator Services Pvt. Ltd.
27.30 | LT cable entry at Badu Room Entry -1 having cutout size 670x500mm , cable Diameter 54 mm 02 nos, 52 mm 02 nos, 23 mm 04 nos, 18 mm-04 nos. and 02 nos 6mm GI wire, 02nos 30x3 earth strip. | 1.00 | Job |  | 130000.00 | 130000.00 | 150000.00 | 150000.00 | 120000.00 | 120000.00 | 2800.00 | 2800.00 | 2800.00 | Mona Generator Services Pvt. Ltd.
27.40 | LT cable entry at Badu Room Entry -2 having cutout size 400x200mm , cable Diameter 23 mm 04 Nos, 6 mm 06 Nos, 18 mm 01 Nos. | 1.00 | Job |  | 45000.00 | 45000.00 | 51000.00 | 51000.00 | 45000.00 | 45000.00 | 1850.00 | 1850.00 | 1850.00 | Mona Generator Services Pvt. Ltd.
27.50 | LT cable entry at Bagjola power house entry-1 having cutout size 330x160mm, cable Diameter 38mm 03nos, 28mm 02nos, 21mm 01no, 6mm 01no. | 1.00 | Job |  | 45000.00 | 45000.00 | 49000.00 | 49000.00 | 40000.00 | 40000.00 | 1850.00 | 1850.00 | 1850.00 | Mona Generator Services Pvt. Ltd.
27.60 | LT cable entry at Bagjola power house entry-2 having cutout size 370x260mm, cable Diameter 45mm 03nos, 32mm 01no, 25mm 03nos, and 01 no. 5mm GI wire. | 1.00 | Job |  | 90000.00 | 90000.00 | 105000.00 | 105000.00 | 75000.00 | 75000.00 | 1850.00 | 1850.00 | 1850.00 | Mona Generator Services Pvt. Ltd.
28.00 | Constructing brick masonry chamber of size 1000x1000x700mm (L X B X D) of size in cement mortar 1:4 (1 cement :4 coarse sand ) inside cement plaster 15 mm thick with cement mortar 1:3 (1 cement: 3 Coarse sand) finished with floating coat of neat cement foundation concrete 1:3:6( 1 cement: 3 coarse sand:6 graded stone aggregate 40 mm nominal size) all complete as per standard design with cover of 75 mm thick ness made by RCC in cement mortar 1:2:4 ( 1 cement: 2 coarse sand:4 graded stone aggregate 40 mm nominal size) in two piece with 12 mm rod handle in order to easy handling. | 1.00 | Job |  | 20000.00 | 20000.00 | 15000.00 | 15000.00 | 8000.00 | 8000.00 | 15850.00 | 15850.00 | 8000.00 | Youngmen Traders
29.00 | Design, Supply, Installation & Commissioning of LED Glow Sign Board (48 sqft) made with Alluminium frame fixing on the existing RCC structure with milky white acrylic latter of suitable site of AAI VHF Old remote station as per drawing attached and instruction of EIC. Make of ACP and wire etc. conforming to AAI approved make and for LED as per NIT technical specification. | 1.00 | Job |  | 77000.00 | 77000.00 | 160000.00 | 160000.00 | 65000.00 | 65000.00 | 65000.00 | 65000.00 | 65000.00 | Youngmen Traders, Mona Generator Services Pvt. Ltd.
30.00 | Design, Supply, Installation & Commissioning of LED Glow Sign Board (96 sqft) made with Alluminium frame fixing on the existing RCC structure with milky white acrylic latter of suitable site of AAI Badu Rx station as per drawing attached and instruction of EIC. Make of ACP and wire etc. conforming to AAI approved make and for LED as per NIT technical specification. | 1.00 | Job |  | 148500.00 | 148500.00 | 200000.00 | 200000.00 | 125000.00 | 125000.00 | 120000.00 | 120000.00 | 120000.00 | Mona Generator Services Pvt. Ltd.
31.00 | Design, Supply, Installation & Commissioning of LED Glow Sign Board (96 sqft) made with Alluminium frame fixing on the existing RCC structure with milky white acrylic latter of suitable site of AAI Bagjola Tx station as per drawing attached and instruction of EIC. Make of ACP and wire etc. conforming to AAI approved make and for LED as per NIT technical specification. | 1.00 | Job |  | 130000.00 | 130000.00 | 210000.00 | 210000.00 | 135000.00 | 135000.00 | 120000.00 | 120000.00 | 120000.00 | Mona Generator Services Pvt. Ltd.
32.00 | SITC of Flex Retrofit of size 4 ft x 1.5 ft with backlit LED lights in SS frame for Bagjola Emergency Gate exit providing complete as required conforming to AAI approved make and for LED as per NIT technical specification. | 1.00 | Job |  | 22000.00 | 22000.00 | 15000.00 | 15000.00 | 15000.00 | 15000.00 | 55000.00 | 55000.00 | 15000.00 | M/s J.K. Electric Engineering Works, Youngmen Traders
33.00 | RCC foundation with necessary arrangements etc. as required as per RCC Foundation Drawing in technical specification for installation of 2.5 mtr long MS pipe as per site requrement. | 8.00 | Job |  | 6000.00 | 48000.00 | 6000.00 | 48000.00 | 4500.00 | 36000.00 | 6500.00 | 52000.00 | 36000.00 | Youngmen Traders
34.00 | SITC of 100mm dia Heavy duty MS pipe 2.5 mtr. Length with square size MS base plate (2nos) of attached drawing with the existing RCC structure for installation of Airport LED signage etc. as required as per site requrement. | 8.00 | Job |  | 3000.00 | 24000.00 | 20000.00 | 160000.00 | 4000.00 | 32000.00 | 8300.00 | 66400.00 | 24000.00 | DOSHI ELECTRIC ENGG. CO.
35.00 | Excavation of the cable trenches in hard rock not exceeding 1.5 metres in width, and lift upto 1.5 metres, including getting out the excavated soil and disposal of excavated soil as directed within a lead of 50 metres. | 20.00 | Cum |  | 1000.00 | 20000.00 | 350.00 | 7000.00 | 600.00 | 12000.00 | 450.00 | 9000.00 | 7000.00 | M/s J.K. Electric Engineering Works
36.00 | Cement concrete flooring 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate) finished with a floating coat of neat cement, including cement slurry, but excluding the cost of nosing of steps etc. complete.
36.10 | 40 mm thick with 20 mm nominal size stone aggregate | 50.00 | Sq.mtr. |  | 400.00 | 20000.00 | 500.00 | 25000.00 | 450.00 | 22500.00 | 400.00 | 20000.00 | 20000.00 | DOSHI ELECTRIC ENGG. CO., Mona Generator Services Pvt. Ltd.
37.00 | Providing brick work (in width 225 mm or more) with F.P.S. bricks of class designation 7.5 in cement mortar 1:4 (1 cement : 4 coarse sand) at all levels. | 5.00 | Cum |  | 8500.00 | 42500.00 | 8000.00 | 40000.00 | 8000.00 | 40000.00 | 6000.00 | 30000.00 | 30000.00 | Mona Generator Services Pvt. Ltd.
38.00 | Providing 15mm thick cement plaster of mix 1:4 (1 cement : 4 fine sand) at all levels. | 25.00 | Sq.Mtr. |  | 300.00 | 7500.00 | 220.00 | 5500.00 | 225.00 | 5625.00 | 230.00 | 5750.00 | 5500.00 | M/s J.K. Electric Engineering Works
39.00 | Providing, laying and fixing following dia G.I. pipe (medium class) in ground complete with G.I. fittings including trenching (75 cm deep)and re-filling etc as required
39.10 | 50mm dia | 12.00 | Mtr. |  | 800.00 | 9600.00 | 800.00 | 9600.00 | 650.00 | 7800.00 | 560.00 | 6720.00 | 6720.00 | Mona Generator Services Pvt. Ltd.
40.00 | Providing & Fixing of MS chennel Iron made of 100mm X 50mm X 6mm(9.56 kg per meter ) on the side wall of existing bricks wall of Cable trenches i/c Painting etc as required. | 250.00 | Kg. |  | 125.00 | 31250.00 | 108.00 | 27000.00 | 65.00 | 16250.00 | 115.00 | 28750.00 | 16250.00 | Youngmen Traders
41.00 | Providing & fixing of MS Checker plate of thickness 10 mm as per IS: 3502: 2009 for covering of cable trenches i/c painting of approved colour etc. as required. | 300.00 | Kg. |  | 150.00 | 45000.00 | 108.00 | 32400.00 | 65.00 | 19500.00 | 110.00 | 33000.00 | 19500.00 | Youngmen Traders
| Total in Figures |  |  |  |  | 10461350.00 |  | 10548900.00 |  | 8492975.00 |  | 10477000.00
Lowest Amount Quoted BY: Youngmen Traders(8492975.00)

## BOQ Summary
BOQ Summary Details Tender Title: Replacement of Normal DG set to Silent DG set and Modification of existing Panel Tender ID: 2023_AAI_147505_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Youngmen Traders | 8492975.00 | L1
| 2 | DOSHI ELECTRIC ENGG. CO. | 10461350.00 | L2
| 3 | Mona Generator Services Pvt. Ltd. | 10477000.00 | L3
| 4 | M/s J.K. Electric Engineering Works | 10548900.00 | L4