## BoQ1
Government eProcurement System Created By: Dillip Kumar Pradhan Created Date/Time: 03-May-2023 04:43 PM Tender Title: Miscellaneous GLF works Tender ID: 2023_AAI_149225_1
Tender Inviting Authority: AIRPORTS AUTHORITY OF INDIA
Name of Work: M.O. GLF at NSCBI Airport, Kolkata dg. 2022-23. SH:- Miscellaneous GLF works.
Contract No:
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Youngmen Traders(GSTN-19AEIPB6323B1ZZ) |  | M/s J.K. Electric Engineering Works(GSTN-19AAHFJ4404E1ZL)
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Fabrication & supply of 330mmx330mm size MS collar of suitable height as per site requirement (for increasing the height of the existing isolating transformer housing box) made out of 6mm thick MS sheet on four sides, 10mm thick MS sheet on top & bottom, with a provision of 50mm dia pipe entry hole on three sides, 225mm dia round opening on top & bottom with six nos holes on edges of top & bottom plates, suitable for holding the taxiway/runway edge light fittings on top and bottom bolted to the existing box including painting the collar with one coat of primer & two coats of black enamel paint etc. complete as required & as per enclosed specifications. | 400.00 | kg. |  | 85.00 | 34000.00 | 78.00 | 31200.00 | 31200.00 | M/s J.K. Electric Engineering Works
2.00 | Installation of MS collar (supplied against item no.1) by providing & fixing of 12 nos. M-10 bolts including minor civil works as per site requirement, making pedestal of 0.30mt all around the box by making suitable slope by providing 1:2:4 cement concrete etc. complete as required & as per direction of Engineer-in-charge. | 20.00 | Jobs |  | 800.00 | 16000.00 | 500.00 | 10000.00 | 10000.00 | M/s J.K. Electric Engineering Works
3.00 | Dismantling of existing elevated light fittings and reinstallation of the same i/c connecting with isolating transformer etc. as required. | 20.00 | Nos. |  | 75.00 | 1500.00 | 40.00 | 800.00 | 800.00 | M/s J.K. Electric Engineering Works
4.00 | Dry brick pitching (laid flat) on surface including supply of bricks and preparing the surface complete as required. | 200.00 | sq. mt. |  | 490.00 | 98000.00 | 500.00 | 100000.00 | 98000.00 | Youngmen Traders
5.00 | Excavation of soft soil including dressing of sides and ramming of bottoms, lift upto 1.5 m including getting out the excavated soil and disposal of surplus excavated soil as directed, within a lead of 50 metres . | 100.00 | Cum |  | 120.00 | 12000.00 | 100.00 | 10000.00 | 10000.00 | M/s J.K. Electric Engineering Works
6.00 | Providing & laying in position 1:2:4 cement concrete (1 cement : 2 course sand : 4 graded stone aggregate 20mm. nominal size) over brick soling as per site requirement and as directed by engg.-in-charge. | 50.00 | Cum |  | 4800.00 | 240000.00 | 5000.00 | 250000.00 | 240000.00 | Youngmen Traders
7.00 | Providing & laying 12mm thick cement plaster of mix 1:3 (1 cement : 3 coarse sand) finished with a floating coat of neat cement etc. as required. | 200.00 | sq. mt. |  | 250.00 | 50000.00 | 150.00 | 30000.00 | 30000.00 | M/s J.K. Electric Engineering Works
8.00 | Providing brick work ( in width 225 mm or more) with F.P.S bricks of class designation of 7.5 in cement mortar 1:4 (1 cement: 4 coarse sand ) in all levels | 15.00 | Cum |  | 4800.00 | 72000.00 | 4500.00 | 67500.00 | 67500.00 | M/s J.K. Electric Engineering Works
9.00 | Removing of existing broken bolt from the transformer housing boxes, making new holes by drilling, tapping etc. as required i/c supply and fixing of suitable size SS bolt, washer etc as required i/c necessary T&P such as Drilling machine, Tapping machine etc. as required. | 150.00 | jobs |  | 75.00 | 11250.00 | 40.00 | 6000.00 | 6000.00 | M/s J.K. Electric Engineering Works
10.00 | Providing cover plates of following sizes fabricated from 10mm thick MS plate, suitable for Isolating transformer housing boxes i/c making 6nos holes on the edges, drilling, tapping, finishing, i/c pencil grinding (bevelling) of outer edge to get a 'C' shaped finished surface and carrying the same to site and placing them properly over round opening of collars, housing boxes etc. i/c painting etc. as required and as per direction of Engineer-in-charge. (a) 300 mm dia circular base plate | 50.00 | Jobs |  | 900.00 | 45000.00 | 850.00 | 42500.00 | 42500.00 | M/s J.K. Electric Engineering Works
11.00 | Providing cover plates of following sizes fabricated from 10mm thick MS plate, suitable for Isolating transformer housing boxes i/c making holes, drilling, tapping, finishing and fixing the same with 6 nos. 1.5" long, M-10 S.S. bolts, plain washers, spring washers etc. i/c painting etc. as required and as per direction of Engineer-in-charge. (b) 330 mm x 330 mm square base plate | 30.00 | Jobs |  | 900.00 | 27000.00 | 850.00 | 25500.00 | 25500.00 | M/s J.K. Electric Engineering Works
12.00 | Dismantling of various sizes C.I./M.S. transformer housing box from concrete/bituminous foundation i/c disposal of debris etc. as reqd. | 20.00 | Jobs |  | 150.00 | 3000.00 | 100.00 | 2000.00 | 2000.00 | M/s J.K. Electric Engineering Works
13.00 | Installation of MS housing box of size750 mm x 330 mm x 400 mm (H) (to be supplied by AAI) in soil by providing brick soling (size 950mm x 530mm) at the bottom & using cement concrete of ratio 1:2:4 all around & bottom of the box of 100 mm thick and making pedestal of 300mm & 100mm thick all around the box by making suitable slope i/c centering & shuttering etc. as required | 20.00 | jobs |  | 1600.00 | 32000.00 | 1500.00 | 30000.00 | 30000.00 | M/s J.K. Electric Engineering Works
14.00 | Providing, laying and fixing following dia GI pipe (medium class) in ground complete with GI fittings including trenching (up to 75 cm deep) and refilling etc. as required. (a) 40 mm dia GI Pipe | 50.00 | mtr |  | 500.00 | 25000.00 | 425.00 | 21250.00 | 21250.00 | M/s J.K. Electric Engineering Works
15.00 | Supply of DWC pipe of following size alongwith necessary accessories like connectors /couplers /bends / tee etc. and with pulling rope fitted inside complete as required and as per the technical specifications etc. complete as required. (a) OD 50 mm/ ID 38 mm | 500.00 | Mtr |  | 55.00 | 27500.00 | 70.00 | 35000.00 | 27500.00 | Youngmen Traders
16.00 | Laying of DWC HDPE Pipe of size of 50 mm OD/38 mm ID in the shoulder/runway/taxiway for GLF work i/c machine cutting of runway/taxiway/shoulder surface of width 110 mm and upto 150 mm deep, and taking the excavated material out of the area within a lead of 2 kms and refilling & making good the same by concreting as per the site requirement. | 100.00 | mtr |  | 250.00 | 25000.00 | 130.00 | 13000.00 | 13000.00 | M/s J.K. Electric Engineering Works
17.00 | Laying of DWC HDPE Pipe of size of 50 mm OD/38 mm ID in the soil for GLF work upto 750 mm deep with excavation, back filling & making good the same as per site requirement | 400.00 | mtr |  | 75.00 | 30000.00 | 50.00 | 20000.00 | 20000.00 | M/s J.K. Electric Engineering Works
18.00 | Scrapping, cleaning the surface of existing LT Panels/feeder pillars/CCR's and painting with two coats of synthetic enamel paint over a coat of red lead primer etc. as required. | 200.00 | sqmt |  | 200.00 | 40000.00 | 150.00 | 30000.00 | 30000.00 | M/s J.K. Electric Engineering Works
19.00 | Scrapping, cleaning etc. as required and painting the following light fittings with two coats of approved make Aviation Yellow synthetic enamel paint,over base plate said painting should be done after applying one coat of red lead primer. (a) Approach light fittings | 255.00 | Nos. |  | 130.00 | 33150.00 | 125.00 | 31875.00 | 31875.00 | M/s J.K. Electric Engineering Works
20.00 | Scrapping, cleaning etc. as required and painting the following light fittings with two coats of approved make Aviation Yellow synthetic enamel paint,over base plate said painting should be done after applying one coat of red lead primer. (a) Turn pad/taxi fittings | 400.00 | Nos. |  | 130.00 | 52000.00 | 125.00 | 50000.00 | 50000.00 | M/s J.K. Electric Engineering Works
21.00 | Scrapping, cleaning etc. as required and painting the following light fittings with two coats of approved make Aviation Yellow synthetic enamel paint,over base plate said painting should be done after applying one coat of red lead primer. (a) PAPI fixtures | 16.00 | Nos. |  | 425.00 | 6800.00 | 350.00 | 5600.00 | 5600.00 | M/s J.K. Electric Engineering Works
22.00 | Scrapping, cleaning etc. as required and painting the following light fittings with two coats of approved make Aviation Yellow synthetic enamel paint,over base plate said painting should be done after applying one coat of red lead primer. (a) Landing H | 1.00 | No. |  | 3000.00 | 3000.00 | 2200.00 | 2200.00 | 2200.00 | M/s J.K. Electric Engineering Works
23.00 | Scrapping, cleaning the surface of MS cover plates and exposed surface of MS boxes and painting with two coats of black colour synthetic enamel paint over a coat of red lead primer etc. as required. | 100.00 | sqmt |  | 140.00 | 14000.00 | 100.00 | 10000.00 | 10000.00 | M/s J.K. Electric Engineering Works
24.00 | Writing of maximum 2 inch size letters/numbers on the surface of base plates/cover plates of light fittings and on the body of LT panels, feeder pillars, CCR's by ICI/ DECO or any other approved paint of White/Red/Black colour . | 1000.00 | Nos. |  | 5.00 | 5000.00 | 5.00 | 5000.00 | 5000.00 | Youngmen Traders, M/s J.K. Electric Engineering Works
25.00 | Supply of Base Plate Neoprene Rubber Gasket of 3 mm thickness and containing 6 nos. bolt holes, suitable for elevated type Aeronautical Ground Lights fittings | 30.00 | Nos. |  | 40.00 | 1200.00 | 45.00 | 1350.00 | 1200.00 | Youngmen Traders
26.00 | Supply of Insulation Tester, 2500 Volts, 2 terminals Hand Driven Generator type along with all acccessories and Type test certificate and catalogue to be attached etc as required as per direction of EIC. | 1.00 | each |  | 5800.00 | 5800.00 | 7500.00 | 7500.00 | 5800.00 | Youngmen Traders
27.00 | Supply and fixing of Thermoplastic enclosure( lid made of transparent Polycarbonate and base made of Polystyrene) for external lighting pole junction box having single stainless steel screw operation for opening the full transparent hinged lid with sealing facility through that SS screw in the existing pole. The enclosure should have IP 65 degree of protection accordance to EN 60529, dust proof, water tight, light weight, acid resistant, corrosion proof, insulated and shock proof, fire retardant , self extinguishing, halogen & silica free non- Toxic material, with internally embedded Gasket (made of polyurethane), size of 217x253x115 mm fitted with clamp and GI Strip at the back of the enclosure and along with the components [i.e. (i) one no. 6A DP MCB on a din channel for mounting, (ii) one no. 100A DMC Terminal Board,(iii) one no. 4 Sq mm Earth Terminal) fixed inside the enclosure] etc. as required. | 20.00 | Nos. |  | 4500.00 | 90000.00 | 2200.00 | 44000.00 | 44000.00 | M/s J.K. Electric Engineering Works
28.00 | Fabrication and supply of MS frame of outer dimensions 330mm x 330mm, made out of 40x40x6 mm MS angle, with 8 nos. threaded holes suitable for M-10 SS bolts on the frame with suitable grouting arrangement for brick work including supply of 330mm x 330mm, 10mm thick MS cover plate with 8 nos holes on the MS plate suitable to fix on the frame with 8 nos. SS M-10 bolts | 20.00 | Nos. |  | 3200.00 | 64000.00 | 1300.00 | 26000.00 | 26000.00 | M/s J.K. Electric Engineering Works
29.00 | Dismantling of old/damaged earth pit chamber and reconstruction of the chamber by providing & making brick work, cement concrete etc., and installation of Eathing Pit cover (supplied vide item no.28) over the pipe etc. including neat cement plaster around the MS frame etc. as required. | 10.00 | Nos. |  | 950.00 | 9500.00 | 800.00 | 8000.00 | 8000.00 | M/s J.K. Electric Engineering Works
30.00 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia includimg accessories, by making necessary excavation and installation of Eathing Pit cover (supplied vide item no.28) over the pipe etc., providing one layer of dry brick pitching on an area of 550mm dia at the bottom while keeping an opening of 200 mm dia at the centre for passage of earth pipe and providing cement concrete of ratio 1:2:4 all around the body of the cover of 100 mm thickness and over the brick layer of 50mm thickness, making suitable slope i/c centering & shuttering etc. as required. | 10.00 | Jobs |  | 5500.00 | 55000.00 | 3500.00 | 35000.00 | 35000.00 | M/s J.K. Electric Engineering Works
31.00 | Providing and laying earth connection from earth electrode with 6 S.W.G. dia G.I. Wire in 15 mm. dia G.I. pipe from earth electrode including connection with G.I. thimble excavation and re-filling as required. | 90.00 | meters |  | 155.00 | 13950.00 | 120.00 | 10800.00 | 10800.00 | M/s J.K. Electric Engineering Works
32.00 | Repairing of foundation for PAPI Ckecking Stick Base by installing anchor fastners, providing and laying 12 mm thick cement plaster of mix 1:3 around the foundation (1m x 1 m) etc as required i/c hiring/arrangement of all necessary T&P like portable DG set, Drilling machine etc. as required.. | 16.00 | Jobs |  | 750.00 | 12000.00 | 500.00 | 8000.00 | 8000.00 | M/s J.K. Electric Engineering Works
33.00 | Supply of Calcium Carbonate Powder Type MIKHART 130, to be used as cleaning agent for inset type Airfield Ground Light Fittings in LUMICLEAN equipment as per technical specifications enclosed. | 400.00 | Kgs |  | 580.00 | 232000.00 | 450.00 | 180000.00 | 180000.00 | M/s J.K. Electric Engineering Works
34.00 | Supply of 150 W, 6.6 A AFL lamp, OSRAM make Cat. No. 64361 HLX-A 150-15 PK30D/ NARVA make Cat. No. 58369 PK30D suitable for ATG make elevated type Runway edge light fittings. | 1000.00 | Nos. |  | 900.00 | 900000.00 | 950.00 | 950000.00 | 900000.00 | Youngmen Traders
35.00 | Supply of 45W, 6.6 A single ended bi-pin Halogen lamp, OSRAM make Cat. No. 64321 or Philips/NARVA make Cat. No. 58323 suitable for use in Airfield lighting fittings. | 500.00 | Nos. |  | 425.00 | 212500.00 | 345.00 | 172500.00 | 172500.00 | M/s J.K. Electric Engineering Works
36.00 | Supply of 105 Watt, 6.6 Amps, prefocus dichroic coated reflector lamp, OSRAM make Cat. No. 64339B or Philips/NARVA make Cat. No. 58307, suitable for use in Airfield lighting fittings. | 500.00 | Nos. |  | 950.00 | 475000.00 | 950.00 | 475000.00 | 475000.00 | Youngmen Traders, M/s J.K. Electric Engineering Works
37.00 | Supply of 105 Watt, 6.6 Amps, prefocus dichroic coated reflector lamp, OSRAM make Cat. No. 64339A or Philips/NARVA make Cat. No. 58308, suitable for use in Airfield lighting fittings. | 500.00 | Nos. |  | 950.00 | 475000.00 | 950.00 | 475000.00 | 475000.00 | Youngmen Traders, M/s J.K. Electric Engineering Works
38.00 | Supply of 360° Blue lens (110mm dia) suitable for AMA make Taxi edge light fitting. | 150.00 | Nos. |  | 1600.00 | 240000.00 | 1450.00 | 217500.00 | 217500.00 | M/s J.K. Electric Engineering Works
39.00 | Supply of Green lens for AMA make Threshold fittings. | 50.00 | Nos. |  | 2700.00 | 135000.00 | 2900.00 | 145000.00 | 135000.00 | Youngmen Traders
40.00 | Supply of top filter (dome) for 8 inch dia stand maneouvering lights of ATG make. | 50.00 | Nos. |  | 8400.00 | 420000.00 | 14000.00 | 700000.00 | 420000.00 | Youngmen Traders
41.00 | Supply of Yellow filter (part no.019157) for 8 inch dia stand maneouvering lights of ATG make. | 50.00 | Nos. |  | 7800.00 | 390000.00 | 11000.00 | 550000.00 | 390000.00 | Youngmen Traders
42.00 | Supply of Full Red filter (part no.019155) for 8 inch dia stand stop lights of ATG make. | 30.00 | Nos. |  | 7800.00 | 234000.00 | 9500.00 | 285000.00 | 234000.00 | Youngmen Traders
43.00 | Supply of Full Green Filter (part no.019156) for (ZA280-series) Taxiway Center line lights of ATG make. | 50.00 | Nos. |  | 7800.00 | 390000.00 | 9500.00 | 475000.00 | 390000.00 | Youngmen Traders
44.00 | Supply of Half Green Filter (part no.019159) for (ZA280-series) Taxiway Center line lights of ATG make. | 25.00 | Nos. |  | 5900.00 | 147500.00 | 7000.00 | 175000.00 | 147500.00 | Youngmen Traders
45.00 | Supply of Half Yellow Filter (part no.019160) for (ZA280-series) Taxiway Center line lights of ATG make. | 25.00 | Nos. |  | 5900.00 | 147500.00 | 700.00 | 17500.00 | 17500.00 | M/s J.K. Electric Engineering Works
46.00 | Supply of Red filter for stop bar fittings of ATG make. | 25.00 | Nos. |  | 9500.00 | 237500.00 | 9500.00 | 237500.00 | 237500.00 | Youngmen Traders, M/s J.K. Electric Engineering Works
47.00 | Supply of Red filter for stop bar fittings of Thorn make. | 10.00 | Nos. |  | 7000.00 | 70000.00 | 5000.00 | 50000.00 | 50000.00 | M/s J.K. Electric Engineering Works
48.00 | Supply of EFLA or equivalant make Primary connector kit, Type KD 500/YG, 5 KV grade dry type plug and receptacle of type I, class 'B' primary connector kit with field attachment and suitable for 5 KV grade single core, 6sqmm. copper conductor, copper braided, XLPE insulated PE outer sheathed shielded cable, complete as required confirming to the technical specification. | 200.00 | pairs |  | 1600.00 | 320000.00 | 1900.00 | 380000.00 | 320000.00 | Youngmen Traders
49.00 | Supply of secondary connectors for two core cables (plug), suitable for connecting 2x4 sqmm secondary cable. (EFLA make Model KD 501.1 or equivalant) | 200.00 | Nos. |  | 900.00 | 180000.00 | 950.00 | 190000.00 | 180000.00 | Youngmen Traders
50.00 | Supply of secondary connectors for two core cables (receptacle), suitable for connecting 2x4 sqmm secondary cable. (EFLA make Model KD 502.1 or equivalent). | 200.00 | Nos. |  | 900.00 | 180000.00 | 950.00 | 190000.00 | 180000.00 | Youngmen Traders
51.00 | Supply of wind shock (nylon fabric) for wind direction indicator complying ICAO Annex-14 requirements. | 5.00 | Nos. |  | 6000.00 | 30000.00 | 6500.00 | 32500.00 | 30000.00 | Youngmen Traders
52.00 | Supply and fixing of pastable, antiskid, fire retardant, alkali and acid resistant nominal 2.5 mm +/- 10% thick, ISI marked Elastomeric Insulation Mat of 11 KV, 50 Hz grade and conforming to IS 15652 : 2006; including all sundry materials e.g. adhesive, Poly Urethene resin and sealing compound, sealing tape etc. cutting, filling, cleaning, chipping, minor civil work etc. complete as required. | 200.00 | sqmt |  | 1300.00 | 260000.00 | 1400.00 | 280000.00 | 260000.00 | Youngmen Traders
53.00 | Supply and installation of Bird Scare Spikes including all the consumables such as cable tie etc inside operational area, over elevated approach lights , guidance signage boards etc. as required. | 500.00 | Running Feet |  | 40.00 | 20000.00 | 40.00 | 20000.00 | 20000.00 | Youngmen Traders, M/s J.K. Electric Engineering Works
54.00 | Supply, Installation, Testing and Commissioning of FAA compliant indoor type microprocessor based, air cooled Constant Current Regulator (CCR) of Thyristor control electronic type suitable for use on 240/415V, 50 Hz, input AC supply with below mentioned output power at 6.6A with 5 steps variation of current output (2.8A, 3.4A, 4.1A, 5.2A, 6.6A) suitable for local and remote control operation with 24/48V DC control supply complete with output current indicated on multifunction digital display, over current, over voltage, earth fault protection and earth leakage meter, positive back indication equipment relay contactor etc. as required. (i) 30 KW | 2.00 | job |  | 425000.00 | 850000.00 | 410000.00 | 820000.00 | 820000.00 | M/s J.K. Electric Engineering Works
55.00 | Dismantling of 1 no. PVC/XLPE insulated AFL cable of 5 KV grade of size not exceeding 25 sq.mm from soil i/c excavation, removing protective covering, refilling the trench etc.as required. | 100.00 | mtr |  | 75.00 | 7500.00 | 10.00 | 1000.00 | 1000.00 | M/s J.K. Electric Engineering Works
56.00 | Dismantling of 1 no. PVC/XLPE insulated AFL cable of 5 KV grade of size not exceeding 25 sq.mm in existing GI/ HDPE pipe etc.as required. | 200.00 | mtr |  | 25.00 | 5000.00 | 10.00 | 2000.00 | 2000.00 | M/s J.K. Electric Engineering Works
57.00 | Laying of one no. PVC/XLPE insulated & sheathed AFL cable of 5 KV grade of size not exceeding 25 sq.mm in the existing pipe. | 600.00 | mtr |  | 30.00 | 18000.00 | 10.00 | 6000.00 | 6000.00 | M/s J.K. Electric Engineering Works
58.00 | Laying of one number 2 X 4 sq mm AFL secondary cable along with 1 X 4 sq mm earth cable of voltage grade not exceeding 1.1 KV in the cable duct / masonary trench / RCC / HUME / METAL / GI / HDPE pipes etc. as required. | 100.00 | mtr |  | 30.00 | 3000.00 | 10.00 | 1000.00 | 1000.00 | M/s J.K. Electric Engineering Works
59.00 | Kerf cutting with machine in taxiway/runway/apron of PQC/bituminous surface of depth upto 50 mm and width upto 15 mm for 1 or 2 nos secondary lead along with earth cables and laying of secondary lead and earth cable by wrapping cotton tape i/c refilling the same by suitable sealing material (Polysulphide) etc complete as required and as per instruction of EIC. | 200.00 | mtrs |  | 325.00 | 65000.00 | 200.00 | 40000.00 | 40000.00 | M/s J.K. Electric Engineering Works
60.00 | Dismantling of following dia. Inset type light fixture along with shallow base from bituminious/concrete pavement by cutting core, fill the area with bitumen/cement concrete/early setting cement, cleaning the shallow base and fitting i/c disconnecting Isolating transformer, removal of secondary lead cable and transportaion to AAI store etc. as required. (a) 8" dia inset fitting | 60.00 | Job |  | 1200.00 | 72000.00 | 300.00 | 18000.00 | 18000.00 | M/s J.K. Electric Engineering Works
61.00 | Dismantling of following dia. Inset type light fixture along with shallow base from bituminious/concrete pavement by cutting core, fill the area with bitumen/cement concrete/early setting cement, cleaning the shallow base and fitting i/c disconnecting Isolating transformer, removal of secondary lead cable and transportaion to AAI store etc. as required. (a) 12" dia inset fitting | 30.00 | Job |  | 1200.00 | 36000.00 | 500.00 | 15000.00 | 15000.00 | M/s J.K. Electric Engineering Works
62.00 | Installation, Testing and Commissioning of following dia. inset type GLF fitting with core cutting, aligning and setting i/c providing sealing material and other accessories required for commissiong except fixture, plug & receptacles & isolating transformer etc. as required and as per site conditions. (a) 8" dia inset fitting | 60.00 | Job |  | 4000.00 | 240000.00 | 2200.00 | 132000.00 | 132000.00 | M/s J.K. Electric Engineering Works
63.00 | Installation, Testing and Commissioning of following dia. inset type GLF fitting with core cutting, aligning and setting i/c providing sealing material and other accessories required for commissiong except fixture, plug & receptacles & isolating transformer etc. as required and as per site conditions. (a) 12" dia inset fitting | 30.00 | Job |  | 5000.00 | 150000.00 | 3000.00 | 90000.00 | 90000.00 | M/s J.K. Electric Engineering Works
64.00 | Supply of M-10 SS hardware (set of 6 SS bolts, 6 SS washers) | 2000.00 | Set |  | 40.00 | 80000.00 | 65.00 | 130000.00 | 80000.00 | Youngmen Traders
65.00 | Supply of 18 inch secondary lead with plug at one end for use in airfield lighting | 200.00 | Nos |  | 300.00 | 60000.00 | 170.00 | 34000.00 | 34000.00 | M/s J.K. Electric Engineering Works
66.00 | Supply of 18 inch secondary lead with socket at one end for use in airfield lighting | 200.00 | Nos |  | 300.00 | 60000.00 | 170.00 | 34000.00 | 34000.00 | M/s J.K. Electric Engineering Works
67.00 | Carrying out Photometric measurement of light intensities of Approach lights (inset/elevated fittings) through OEM / Authorized dealer of OEM of Photometric equipment as per CAR Section 4 Series B Part-1, Para 10.5.4 & 10.5.6 and Submission of report. | 433.00 | Nos |  | 465.00 | 201345.00 | 600.00 | 259800.00 | 201345.00 | Youngmen Traders
68.00 | Carrying out Illuminance Check of Mandatory/Instruction/Information signage boards of different sizes through OEM / Authorized dealer of OEM of Photometric equipment as per CAR Section 4 Series B Part-1, Para 5.4.1.7 & Appendix-4 & Submission of reports. | 190.00 | Nos |  | 2100.00 | 399000.00 | 1900.00 | 361000.00 | 361000.00 | M/s J.K. Electric Engineering Works
| Total in Figures |  |  |  |  | 9097495.00 |  | 9111375.00
Lowest Amount Quoted BY: Youngmen Traders(9097495.00)

## BOQ Summary
BOQ Summary Details Tender Title: Miscellaneous GLF works Tender ID: 2023_AAI_149225_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Youngmen Traders | 9097495.00 | L1
| 2 | M/s J.K. Electric Engineering Works | 9111375.00 | L2