## BoQ1
Government eProcurement System Created By: Arun Kumar Majhi Created Date/Time: 09-May-2023 02:41 PM Tender Title: Provision of Parking light and associated works near ATS Complex at NSCBI Airport, Kolkata Tender ID: 2023_AAI_150573_1
Tender Inviting Authority: AIRPORTS AUTHORITY OF INDIA
Name of Work: Provision of Parking light and associated works near ATS Complex at NSCBI Airport, Kolkata.
Tender id: 2023_AAI_150573_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | SHREE GOURI ELECTRIC ENTERPRISE(GSTN-19ADDPB4683J1ZE) |  | M/s J.K. Electric Engineering Works(GSTN-19AAHFJ4404E1ZL) |  | Youngmen Traders(GSTN-19AEIPB6323B1ZZ) |  | MANNA ELECTRONICS AND ELECTRICAL WORKS(GSTN-19AALFM9363P2Z6)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Design, supply and erection of flood lighting system with Single telescopic sections of hot dip galvanized high mast total height of 12 meters and material of construction as per S 355 grade as per BS-EN10 025 (with base plate welded to the bottom sections) and holdings, All sections shall be totally hot dip galvanized fitted at site suitable for wind velocity as per IS 875 part-3 and it shall also include the following accessories etc. complete as required as per the specifications given include making of necessary foundation as per site condition ( Make :- AAI Approved Make ) | 2.00 | Job |  | 150000.00 | 300000.00 | 265000.00 | 530000.00 | 200000.00 | 400000.00 | 209650.00 | 419300.00 | 300000.00 | SHREE GOURI ELECTRIC ENTERPRISE
2.00 | 1.1 (a) Galvanized lantern carriage to hold minimum all required LED light fittings (suitable for 150 Watts LED Flood Light luminaire - 8 Nos ) for desired lux level in the designated area plus two additional light fittings for redundancy including all accessories, counter weights and self balance.
3.00 | 1.2(b) Raising and lowering mechanism consisting of suitable double drum winch assembly, head frame assembly on top with self fabricating bearing and stainless steel shaft non-corrosive, pulley, & stainless steel wire ropes of minimum 6mm dia 316 Grade S.S hoisting (7/19 construction) etc. completes with internally mounted electric driven 3 phase, 415 volts, 50 Hz/1-Phase, 230V, 50Hz operated integral power tool installed inside the base compartment for its operation and also for manual operation.
4.00 | 1.3 (c) Supply, Laying and fixing of 2 runs of flexible round sheath 6 core control cables of appropriate rating from junction box to lantern carriage including wiring with suitable size of 2.5 sq.mm. copper cable for individual wiring of all fittings.
5.00 | 1.4(d) Supply of foundation bolts manufactured from special steel along with GI nuts, GI washer, suitable size anchor plate and template.
6.00 | 1.5(e) Design, casting of open raft type RCC foundation suitable for soil bearing capacity at site. The minimum M20 grade concrete for the high mast considering the safe soil bearing capacity at site as 10 T/sqmtr at 2 meter depth job including all materials and labour and as per site conditions. (The foundation design should be vetted form reputed IIT/ NIT/ any reputed Govt technical institution suitable for wind velocity as per IS 875 part-3 along with desired fittings for 5 average lux level)
7.00 | 1.6 (f) Testing of soil in approved government laboratory to determine bearing capacity.
8.00 | 1.7 (g) Junction box as per specifications
9.00 | 1.8(h) Heavy gauge hot dip galvanized lightening arrester and its necessary connections at the top.
10.00 | 1.9 (i) SITC of 01 no. Aviation Obstruction Light and Installation of required nos of fittings to achieve the desired lux level including its control wiring with copper conductor cable from control box.
11.00 | Supply of 150 W LED Floodlight luminaire with 5700K colour temperature, Efficacy of LED Light Fitting Minimum 110 lm/W, Pf equal to 0.95 or more, THD should be less than 10% , minimum IP 65 protection with housing material made of High Pressure Die Cast Aluminium /Standard Alloy suitable for Outdoor Application with manufacturer Name/Logo enbossed in the housing Body or on Aluminium Plate etc. complete as required, all prewired upto terminal block and suitable for operation on 230 V+/- 10%, 50Hz, single phase AC supply and as per technical specification with all its accessories, driver etc as complete. | 18.00 | Each |  | 6200.00 | 111600.00 | 5800.00 | 104400.00 | 5500.00 | 99000.00 | 5000.00 | 90000.00 | 90000.00 | MANNA ELECTRONICS AND ELECTRICAL WORKS
12.00 | Supply of 12W slim type recessed mounted, with 5700K colour temperature, Efficiency of LED Light Fitting Minimum 100lm/W, Pf equal to 0.95 or more, THD should be less than 10% , minimum IP 20 protection with housing material made of Extruded Aluminium /CRCA/ Standard Alloy suitable for Indoor type application with manufacturer Name/Logo enbossed in the housing Body or on Aluminium Plate etc. complete as required, all prewired upto terminal block and suitable for operation on 230 V+/- 10%, 50Hz, single phase AC supply and as per technical specification with all its accessories, driver etc as complete. | 40.00 | Each |  | 1155.00 | 46200.00 | 680.00 | 27200.00 | 700.00 | 28000.00 | 550.00 | 22000.00 | 22000.00 | MANNA ELECTRONICS AND ELECTRICAL WORKS
13.00 | Supply of 18W slim type recessed mounted, with 5700K colour temperature, Efficiency of LED Light Fitting Minimum 100lm/W, Pf equal to 0.95 or more, THD should be less than 10% , minimum IP 20 protection with housing material made of Extruded Aluminium /CRCA/ Standard Alloy suitable for Indoor type application with manufacturer Name/Logo enbossed in the housing Body or on Aluminium Plate etc. complete as required, all prewired upto terminal block and suitable for operation on 230 V+/- 10%, 50Hz, single phase AC supply and as per technical specification with all its accessories, driver etc as complete. | 40.00 | Each |  | 1613.00 | 64520.00 | 850.00 | 34000.00 | 800.00 | 32000.00 | 660.00 | 26400.00 | 26400.00 | MANNA ELECTRONICS AND ELECTRICAL WORKS
14.00 | Supply, Installation, Testing & Commissioning (foundation i/c)of Out Door type Double Door LT Panel, cubicle type, made out of 2mm thick CRCA sheet, totally enclosed. IP 54, free standing, floor mounting, dust and vermin proof, weather proof, outdoor, compartmentalized, suitable for operation on 3 phase and neutral, 415 V, 50 Hz AC system with aluminium busbars including internal wiring with suitable size wires/cable interconnection, bottom, cable entry provision, duly powder coated painting etc., including with DMC/SMC bus bar supports, common GI earth of size 25mm X 5mm at the rear with 2 nos. earth stud including supply and installation of following switchgears, metering instruments and accessories in the LT Panel and as per specifications. | 1.00 | Job |  | 134000.00 | 134000.00 | 165000.00 | 165000.00 | 135000.00 | 135000.00 | 116000.00 | 116000.00 | 116000.00 | MANNA ELECTRONICS AND ELECTRICAL WORKS
15.00 | Incomer
16.00 | 02 Nos. 63A , 25KA FP,T/M release MCCB with rotary handle, spreader links & Auxiliary Contact. With mechinal interlocking.
17.00 | 02 nos. set RYB indication lamp
18.00 | 02 nos. set ON/OFF indication lamp
19.00 | 02 Multifunction meter
20.00 | Outgoing
21.00 | 1 Nos. Digital Timer with 40 A Contactor Switch
22.00 | 3 Nos. 32 A , C Curve FP MCB attached with timer and Contactor.
23.00 | 3 Nos. 32 A , C Curve FP MCB with suitable arrangement for termination of cable.
24.00 | 1 No. 20 A, C-type DP MCB with 2 Nos. 16A 5-pin Socket with Switch
25.00 | 415V, 3 phase and neutral 100 A aluminium bus bar with colour code & sleeves-1 set
26.00 | 6 nos. set ON/OFF Indication lamp
27.00 | Supply, Installation, Testing & Commissioning (foundation i/c)of Out Door type Double Door LT Panel, cubicle type, made out of 2mm thick CRCA sheet, totally enclosed. IP 54, free standing, floor mounting, dust and vermin proof, weather proof, outdoor, compartmentalized, suitable for operation on 3 phase and neutral, 415 V, 50 Hz AC system with aluminium busbars including internal wiring with suitable size wires/cable interconnection, bottom, cable entry provision, duly powder coated painting etc., including with DMC/SMC bus bar supports, common GI earth of size 25mm X 5mm at the rear with 2 nos. earth stud including supply and installation of following switchgears, metering instruments and accessories in the LT Panel and as per specifications. | 2.00 | Job |  | 57500.00 | 115000.00 | 45000.00 | 90000.00 | 75000.00 | 150000.00 | 55000.00 | 110000.00 | 90000.00 | M/s J.K. Electric Engineering Works
28.00 | Incomer: 1. 32A,4P,25KA, MCB - 01 no. 2. Digital Multifunction meter with alll necessary accessories- 1 No, 3. RYB Indicator Lamp -01 no. 4. ON/OFF indication lamp -01 no. Outgoing: 1. 20A 4P MCB - 2 no., 3. 32A FP AC1 duty contactor - 1 no.,For automatic switching of luminaries through auto/local mode operation by selector switch, For auto mode operation 01 no. manual/auto digital timer switch for automatic switching of luminaries, 4. For local mode operation through ON/OFF push button, also provide power tool control with 2 nos. 9A contactors for raise or lower with push button(s) as required, Incoming and out going 25sq. mm. terminals and provide necessary connectors along with bypass arrangement for contactor etc. as required as per specification given and as per site condition.
29.00 | Supply of following sizes XLPE insulated PVC sheathed armoured aluminium conductor cable of grade 1.1 KV, confirming to IS 7098 Part-I with upto date amendments etc. complete as required.
30.00 | 4c x 16 Sq. mm. | 200.00 | Mtr. |  | 384.00 | 76800.00 | 157.00 | 31400.00 | 125.00 | 25000.00 | 162.00 | 32400.00 | 25000.00 | Youngmen Traders
31.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
32.00 | 4 X 16 sq. mm (28mm) | 6.00 | Each |  | 173.00 | 1038.00 | 125.00 | 750.00 | 325.00 | 1950.00 | 300.00 | 1800.00 | 750.00 | M/s J.K. Electric Engineering Works
33.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required.
34.00 | Upto 35 sq. mm (clamped with 1mm thick saddle) | 130.00 | Mtr. |  | 58.00 | 7540.00 | 30.00 | 3900.00 | 55.00 | 7150.00 | 40.00 | 5200.00 | 3900.00 | M/s J.K. Electric Engineering Works
35.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required.
36.00 | Upto 35 sq. mm | 10.00 | Mtr. |  | 29.00 | 290.00 | 100.00 | 1000.00 | 325.00 | 3250.00 | 300.00 | 3000.00 | 290.00 | SHREE GOURI ELECTRIC ENTERPRISE
37.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL pipe as required.
38.00 | Upto 35 sq. mm | 30.00 | Mtr. |  | 38.00 | 1140.00 | 15.00 | 450.00 | 35.00 | 1050.00 | 27.00 | 810.00 | 450.00 | M/s J.K. Electric Engineering Works
39.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required.
40.00 | Upto 35 sq. mm | 10.00 | Mtr. |  | 38.00 | 380.00 | 15.00 | 150.00 | 25.00 | 250.00 | 20.00 | 200.00 | 150.00 | M/s J.K. Electric Engineering Works
41.00 | Supply and laying of 50mm dia OD ISI marked, HDPE pipe along with all accessories like socket,bend, couplers etc. confirming to IS-4984-1995 with up to date amendments and confirming to tender’s technical specifications, terms & conditions complete with fitting and cutting , jointing etc. in existing trench etc. complete as required. | 20.00 | Mtr. |  | 288.00 | 5760.00 | 100.00 | 2000.00 | 175.00 | 3500.00 | 160.00 | 3200.00 | 2000.00 | M/s J.K. Electric Engineering Works
42.00 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 10.00 | Each |  | 5730.00 | 57300.00 | 3500.00 | 35000.00 | 7000.00 | 70000.00 | 4500.00 | 45000.00 | 35000.00 | M/s J.K. Electric Engineering Works
43.00 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 120.00 | Mtr. |  | 624.00 | 74880.00 | 450.00 | 54000.00 | 475.00 | 57000.00 | 550.00 | 66000.00 | 54000.00 | M/s J.K. Electric Engineering Works
44.00 | Supplying and laying 25 mm X 5 mm G.I strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with G.I. nut, bolt, spring, washer etc. as required. | 10.00 | Mtr. |  | 144.00 | 1440.00 | 130.00 | 1300.00 | 165.00 | 1650.00 | 104.00 | 1040.00 | 1040.00 | MANNA ELECTRONICS AND ELECTRICAL WORKS
45.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | 10.00 | Mtr. |  | 101.00 | 1010.00 | 135.00 | 1350.00 | 125.00 | 1250.00 | 200.00 | 2000.00 | 1010.00 | SHREE GOURI ELECTRIC ENTERPRISE
46.00 | Structural steel work riveted, bolted or welded in built up sections, trusses and framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete. | 100.00 | Kg |  | 91.00 | 9100.00 | 80.00 | 8000.00 | 105.00 | 10500.00 | 100.00 | 10000.00 | 8000.00 | M/s J.K. Electric Engineering Works
47.00 | Providing and laying in position cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) in foundation etc including form work etc as required. | 15.00 | Cum |  | 5760.00 | 86400.00 | 6500.00 | 97500.00 | 6500.00 | 97500.00 | 6000.00 | 90000.00 | 86400.00 | SHREE GOURI ELECTRIC ENTERPRISE
48.00 | Demolishing cement concrete surface/paver blocks manually or by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. Nominal concrete 1:3:6 or richer mix (i/c equivalent design mix) | 10.00 | Cum |  | 768.00 | 7680.00 | 400.00 | 4000.00 | 1200.00 | 12000.00 | 5000.00 | 50000.00 | 4000.00 | M/s J.K. Electric Engineering Works
49.00 | Excavation for cable trenches in soft soil, depth upto 1.2 m including dressing of sides lift upto 1.5 m, including getting out the excavated soil, refilling with sand and or good soil after laying of cable/ pipe etc in layers of 20 cm, ramming, watering and disposal of surplus excavated soil as directed, within a lead of 50 metres. | 8.00 | Cum |  | 384.00 | 3072.00 | 100.00 | 800.00 | 250.00 | 2000.00 | 600.00 | 4800.00 | 800.00 | M/s J.K. Electric Engineering Works
50.00 | Providing, laying and fixing following dia G.I. pipe (medium class) in ground complete with G.I. fittings including trenching (75 cm deep)and re-filling etc as required 50 mm dia | 40.00 | Mtr. |  | 712.00 | 28480.00 | 600.00 | 24000.00 | 600.00 | 24000.00 | 380.00 | 15200.00 | 15200.00 | MANNA ELECTRONICS AND ELECTRICAL WORKS
| Total in Figures |  |  |  |  | 1133630.00 |  | 1216200.00 |  | 1162050.00 |  | 1114350.00
Lowest Amount Quoted BY: MANNA ELECTRONICS AND ELECTRICAL WORKS(1114350.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of Parking light and associated works near ATS Complex at NSCBI Airport, Kolkata Tender ID: 2023_AAI_150573_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | MANNA ELECTRONICS AND ELECTRICAL WORKS | 1114350.00 | L1
| 2 | SHREE GOURI ELECTRIC ENTERPRISE | 1133630.00 | L2
| 3 | Youngmen Traders | 1162050.00 | L3
| 4 | M/s J.K. Electric Engineering Works | 1216200.00 | L4