## BoQ1
Government eProcurement System Created By: Dharam Chand Created Date/Time: 12-Jun-2023 04:46 PM Tender Title: Construction of combined operational offices for DGCA, BCAS, AAIB, AERA, AAI at Safdarjung Airport, New Delhi. SH-Misc. civil works at data center i.e. fire glazing for partition and door, false access flooring, false ceiling and view cutter etc Tender ID: 2023_AAI_154038_1
Tender Inviting Authority:Assistant General Manager (E-C)
Name of Work: CONSTRUCTION OF COMBINED OPERATIONAL OFFICES FOR DGCA, BCAS, AAIB, AERA & AAI AT SAFDARJUNG AIRPORT, NEW DELHI SH : Miscellanous civil works at data centre i.e. fire glazing for partition & door, false access flooring, false ceiling and view cutter etc.
Contract No: 2023_AAI_154038_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | kailash chawla(GSTN-07ADYPC8838P1ZG) |  | CREATORS ENGINEERS AND INTERIORS(GSTN-07AAGFC0762R2Z1) |  | M/S SHRI PARASNATH CONST.CO(GSTN-07ADWPZ8203F2ZC) |  | SAMTA INTERIORS(GSTN-07AALPB7815K1ZJ) |  | Gravity Square Pvt . Ltd.(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Providing and fixing removable raised/false access flooring with system and its components of approved make for different plenum height with possible height adjustment upto 50 mm, comprising of modular load bearing floor panels supported on G.I. rectangular stinger frame work and G.I. Pedestal etc. all complete, as per the architectural drawings, as specified and as directed by Engineer-in-charge consisting of: (a) Providing at required spacing to form modular framework, pedestals made out of GI tube of thickness minimum 2 mm and 25 mm outer diameter, fully welded on to the G.I. Base plate of size 100mm x 100mm x 3mm at the bottom of the pedestal tube, G.I. pedestal head of size 75mmx75mmx3.5 mm welded with GI fully threaded stud 16mm outer diameter with two GI Check nuts screwed on the stud for level adjustment upto 50mm, locking and stabilizing the pedestal head in position at the required level. The pedestals shall be fixed to the subfloor (base) through base plate using epoxy based adhesive of approved make or the machine screw with rawl plug. (b) Stringers system in all steel construction hot dipped galvanized of rectangular size 570x20x30x0.80mm thick having holes at both ends for securing the stringers on to the pedestal head using fully threaded screws ensuring maximum lateral stability in all directions, the grid formed by the pedestal and stringer assembly shall receive the floor panel, this system shall provide adequate solid, rigid support for access floor panel, the system shall provide a minimum clear uninterrupted clearance between the bottom of the floor for electrical conduits and wiring etc. all complete as per the architectural drawings, as specified and as directed by the Engineer-in-charge. (c) Providing and fixing Access Floor panel of 600x600x32 mm medium grade Filled Steel anti static high pressure Lamination of 800H grade (FS800H). Access Floor panel shall be steel welded construction with an enclosed bottom pan with uniform pattern of 64 hemispherical cones. The top and bottom plates of Steel Gauges: top 0.6 mm and bottom 0.7 mm fused spot welded together (minimum 64 welds in each dome and 20 welds along each flange). The panel should be Corroresist epoxy coated for lifetime rust protection and cavity formed by the top and bottom plate is filled with Pyrogrip noncombustible Portland cementitious core mixed with lightweight foaming compound. The access floor shall be factory finished with Anti-static High Pressure laminate with Non Warp technology upto 1mm thickness for superior adhesion and Surface flatness within 0.75mm.The panel is to withstand a Concentrated Load of 363 kgs applied on area 25mm x 25mm without collapse in the centre of the panel which is placed on four steel blocks. The panel will withstand and Uniformly Distributed Load (UDL) minimum 1250 kg/sqm and an impact load of 50kg all complete as per the approved manufacturers specification and as per the direction of Engineer-in-charge. All specification must be printed on the side of the panel to ensure the quality of the product.
1.10 | 450 mm Finished Floor Height (FFH). | 111.25 | sqm | 100.00 | 4000.00 | 445000.00 | 4500.00 | 500625.00 | 5100.00 | 567375.00 | 5000.00 | 556250.00 | 4400.00 | 489500.00 | 445000.00 | kailash chawla
2.00 | Providing and fixing non load bearing fixed frame for fire resistant glazed partition for 120 minutes Fire Rating, made out to a profile of dimension 60mm x 70 mm of 1.6 mm thick galvanised steel sheet as per test evidence suitable for fixing fire rated glass for 120 minutes of both integrity & radiation control (EW120) & minimum 20 minutes of insulation (EI20).The profile has to be fixed to the supporting construction by means of anchor fasteners of size M10 x 80, every 150 mm from the edges and every 500 mm (approx) c/c. Linear measurement of frame shall be measured for payment. The frame shall be filled with mineral wool insulation of density minimum 96kg/ cum. and finished with a approved fire resistant primer or Powder | 103.34 | meter | 100.00 | 1791.00 | 185081.94 | 1350.00 | 139509.00 | 1700.00 | 175678.00 | 1700.00 | 175678.00 | 1450.00 | 149843.00 | 139509.00 | CREATORS ENGINEERS AND INTERIORS
3.00 | Providing and fixing glazing in fire resistant door shutters, fixed panels & partitions etc., with G.I. beading made out of 1.6 mm thick G.I. sheet (zinc coating not less than 120 gm/m²) of size 20 x 33 mm screwed with M4 x 38 mm SS screws at distance 75 mm from the edges and 150 mm c/c , including applying a coat of approved fire resistant primer/ powder coating of not less than 30 micron on G.I. beading, & special ceramic tape of 5 x 20 mm size etc complete in all respect as per NBC 2016, IS 16231 (Part 3):2016 and as per direction of Engineer-in-charge with glass of required thickness having 120 minutes of fire resistance both integrity & radiation control (EW120) and minimum 20 minutes of insulation (EI20). The manufacturer have to give test report/certification of fire glass and the glass should have the stamp showing the value of E, EW & EI. The glass shall be tested in approved NABL accredited lab or by any other accreditation body which operates in accordance with ISO/IEC 17011 and accredits labs as per ISO/IEC 17025 for testing and calibration scopes shall be eligible. The glazing size shall be as per the actual site condition. | 70.15 | sqm | 10.00 | 34200.00 | 2399130.00 | 30900.00 | 2167635.00 | 35000.00 | 2455250.00 | 35800.00 | 2511370.00 | 36500.00 | 2560475.00 | 2167635.00 | CREATORS ENGINEERS AND INTERIORS
4.00 | Providing and fixing fire resistant door frame of section 50 x 60 mm on horizontal side & 35 x 60 mm on vertical sides having built in rebate made out of 1.6 mm thick GI sheet ( Zinc coating not less than 120gm/ sqm) suitable for mounting 120 minutes Fire Rated Glazed Door Shutters. The frame shall be filled with mineral wool Insulation having density minimum 96Kg/cum. The frame will have a provision of G.I. anchor fastners 14 nos ( 5 each on vertical style & 4 on horizontal style of size M10 x 80 ) suitable for fixing in the opening along with factory made template for SS ball bearing hinges of Size 100x89x3mm for fixing of fire rated glazed shutter . The frame shall be finished with a approved fire resistant primer or powder coating of not less than 30 micron in desired shade as per the directions of Engineer - in- Charge . (Cost of SS ball bearing hinges is excluded). | 8.80 | meter | 10.00 | 1500.00 | 13200.00 | 1490.00 | 13112.00 | 1700.00 | 14960.00 | 1675.00 | 14740.00 | 1510.00 | 13288.00 | 13112.00 | CREATORS ENGINEERS AND INTERIORS
5.00 | Providing and fixing 60 mm thick glazed fire resistant door shutters of 120 minutes fire rating confirming to IS:3614 (Part II) or EN1634-1:1999, tested and certified as per laboratory approved by Engineer-in-Charge, with suitable mounting on door frame, consisting of vertical styles, top rail & side rail 60 mm x 60 mm wide and bottom rail of 110 mm x 60 mm made out of 1.6mm thick G.I. sheet (zinc coating not less than 120gm/sqm) duly filled mineral wool insulation having density minimum 96 kg/cum and fixing with necessary stainless steel ball bearing hinges of size 100x89x3mm of approved make, including applying a coat of approved fire resistant primer or powder coating not less than 30 micron etc all complete as per direction of Engineer-in-Charge (panelling to be paid for seperately). | 3.63 | sqm | 10.00 | 8200.00 | 29766.00 | 7900.00 | 28677.00 | 25000.00 | 90750.00 | 7450.00 | 27043.50 | 8500.00 | 30855.00 | 27043.50 | SAMTA INTERIORS
6.00 | Steel work welded in built up sections/ framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer using structural steel etc. as required. In gratings, frames, guard bar, ladder, railings, brackets, gates and similar works | 4314.03 | kg | 10.00 | 105.00 | 452973.15 | 130.00 | 560823.90 | 110.00 | 474543.30 | 123.00 | 530625.69 | 125.00 | 539253.75 | 452973.15 | kailash chawla
7.00 | Designing, fabricating, testing, installing and fixing in position Curtain Wall with Aluminium Composite Panel Cladding, with open grooves for linear as well as curvilinear portions of the building , for all heights and all levels etc. including: (a) Structural analysis & design and preparation of shop drawings for pressure equalisation or rain screen principle as required, proper drainage of water to make it watertight including checking of all the structural and functional design. (b) Providing, fabricating and supplying and fixing panels of aluminium composite panel cladding in pan shape in metalic colour of approved shades made out of 4mm thick aluminium composite panel material consisting of 3mm thick FR grade mineral core sandwiched between two Aluminium sheets (each 0.5mm thick). The aluminium composite panel cladding sheet shall be coil coated, with Kynar 500 based PVDF / Lumiflon based fluoropolymer resin coating of approved colour and shade on face # 1 and polymer (Service) coating on face # 2 as specified using stainless steel screws, nuts, bolts, washers, cleats, weather silicone sealant, backer rods etc. (c) The fastening brackets of Aluminium alloy 6005 T5 / MS with Hot Dip Galvanised with serrations and serrated washers to arrest the wind load movement, fasteners, SS 316 Pins and anchor bolts of approved make in SS 316, Nylon separators to prevent bi-metallic contacts all complete required to perform as per specification and drawing The item includes cost of all material & labour component, the cost of all mock ups at site, cost of all samples of the individual components for testing in an approved laboratory, field tests on the assembled working curtain wall with aluminium composite panel cladding, cleaning and protection of the curtain wall with aluminium composite panel cladding till the handing over of the building for occupation. Base frame work for ACP cladding is payable under the relevant aluminium item.s The Contractor shall provide curtain wall with aluminium composite panel cladding, having all the performance characteristics all complete , as per the Architectural drawings, as per item description, as specified, as per the approved shop drawings and as directed by the Engineer-in-Charge. However, for the purpose of payment, only the actual area on the external face of the curtain wall with Aluminum Composite Panel Cladding (including width of groove) shall be measured in sqm. up to two decimal places. | 679.50 | sqm | 10.00 | 4600.00 | 3125700.00 | 2700.00 | 1834650.00 | 4400.00 | 2989800.00 | 3525.00 | 2395237.50 | 4500.00 | 3057750.00 | 1834650.00 | CREATORS ENGINEERS AND INTERIORS
8.00 | Providing and fixing aluminium work for doors, windows, ventilators and partitions with extruded built up standard tubular sections/ appropriate Z sections and other sections of approved make conforming to IS: 733 and IS: 1285, fixing with dash fasteners of required dia and size, including necessary filling up the gaps at junctions, i.e. at top, bottom and sides with required EPDM rubber/ neoprene gasket etc. Aluminium sections shall be smooth, rust free, straight, mitred and jointed mechanically wherever required including cleat angle, Aluminium snap beading for glazing / paneling, C.P. brass / stainless steel screws, all complete as per architectural drawings and the directions of Engineer-in-charge. (Glazing, paneling and dash fasteners to be paid for separately) : Anodised aluminium (anodised transparent or dyed to required shade according to IS: 1868, Minimum anodic coating of grade AC 15) | 785.35 | kg | 10.00 | 375.00 | 294506.25 | 350.00 | 274872.50 | 450.00 | 353407.50 | 450.00 | 353407.50 | 410.00 | 321993.50 | 274872.50 | CREATORS ENGINEERS AND INTERIORS
9.00 | Providing and Fixing 15 mm thick densified tegular edged eco friendly light weight calcium silicate false ceiling tiles of approved texture of size 595 x 595 mm in true horizontal level, suspended on inter locking metal grid of hot dipped galvanised steel sections (galvanising @ 120 grams per sqm including both side) consisting of main ‘T’ runner suitably spaced at joints to get required length and of size 24x38 mm made from 0.33 mm thick (minimum) sheet, spaced 1200 mm centre to centre, and cross “T” of size 24x28 mm made out of 0.33 mm (Minimum) sheet, 1200 mm long spaced between main’T’ at 600 mm centre to centre to form a grid of 1200x600 mm and secondary cross ‘T’ of length 600 mm and size 24 x28 mm made of 0.33 mm thick (Minimum) sheet to be inter locked at middle of the 1200x 600 mm panel to from grid of size 600x600 mm, resting on periphery walls /partitions on a Perimeter wall angle pre-coated steel of size(24x24X3000 mm made of 0.40 mm thick (minimum) sheet with the help of rawl plugs at 450 mm centre to centre with 25 mm long dry wall screws @ 230 mm interval and laying 15 mm thick densified edges calicum silicate ceiling tiles of approved texture in the grid, including, cutting/ making opening for services like diffusers, grills, light fittings, fixtures, smoke detectors etc., wherever required. Main ‘T’ runners to be suspended from ceiling using G.I. slotted cleats of size 25x35x1.6 mm fixed to ceiling with 12.5 mm dia and 50 mm long dash fasteners, 4 mm G.I. adjustable rods with galvanised steel level clips of size 85 x 30 x 0.8 mm, spaced at 1200 mm centre to centre along main ‘T’, bottom exposed with 24 mm of all Tsections shall be pre-painted with polyster baked paint, for all heights, as per specifications, drawings and as directed by Engineer-in-Charge. | 115.00 | sqm | 10.00 | 1300.00 | 149500.00 | 1300.00 | 149500.00 | 1700.00 | 195500.00 | 1400.00 | 161000.00 | 1500.00 | 172500.00 | 149500.00 | kailash chawla, CREATORS ENGINEERS AND INTERIORS
| Total in Figures |  |  |  |  | 7094857.34 |  | 5669404.40 |  | 7317263.80 |  | 6725352.19 |  | 7335458.25
Lowest Amount Quoted BY: CREATORS ENGINEERS AND INTERIORS(5669404.40)

## BOQ Summary
BOQ Summary Details Tender Title: Construction of combined operational offices for DGCA, BCAS, AAIB, AERA, AAI at Safdarjung Airport, New Delhi. SH-Misc. civil works at data center i.e. fire glazing for partition and door, false access flooring, false ceiling and view cutter etc Tender ID: 2023_AAI_154038_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | CREATORS ENGINEERS AND INTERIORS | 5669404.40 | L1
| 2 | SAMTA INTERIORS | 6725352.19 | L2
| 3 | kailash chawla | 7094857.34 | L3
| 4 | M/S SHRI PARASNATH CONST.CO | 7317263.80 | L4
| 5 | Gravity Square Pvt . Ltd. | 7335458.25 | L5