## BoQ1
Government eProcurement System Created By: RAVICHANDRAN SEETHARAMAN Created Date/Time: 07-Jul-2023 12:12 PM Tender Title: Up-gradation of Passenger Terminal Building and Airside Facilities at Trichy International Airport. S.H. Provision of Landscape Lighting for NITB at Trichy Airport Tender ID: 2023_AAI_155489_1
Tender Inviting Authority: Assistant General Manager (Engg-Elect), AAI, Trichy International Airport, Trichy - 620 007.
Name of Work: Up-gradation of Passenger Terminal Building and Airside Facilities at Tiruchirappalli (Trichy) International Airport. S.H: Provision of Lanscape Lighting Works at Trichy Airport.
Contract No: AAI/TRY/E-E/LANDSCAPE/2023 Dt: 29.05.2023
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Instapower Ltd(GSTN-05AAACI9712L1ZG) |  | BUDHIRAJA ELECTRICALS(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply, installation, testing and commissioning of 20W-33W nominal Decorative luminaire (with integral driver) column of height 1100mm and 115mm Dia, with special visual effect created through a smart mix of white and blue sources distributed up and down inside the column. The light fixture (as per the reference pictuers) shall be made of extruded aluminium housing with polyester powder coating and optics cover shall be impact resistance acrylic, stabilized against UV rays, fixture having IP 66, IK08, operating temperature (-10 to +45 degC nominal). Luminaire comprising LEDs of 4000K CCT and Blue colour. LED shall be compliant with useful L70 life of >50,000 Hrs, driver efficiency shall be 85% including proper heat sink for heat dissipation, suitable to operate on input voltage range of 200V to 240V nominal with minimum 4 KV internal surge protection etc., complete as required. (Make: Wipro Schreder Bora Midi or its equivalent similar to the image provided & meeting the technical specifications.) Note: The scope of work covers providing and fixing of suitable loop-in & loop-out polycarbonate junction box having IP-65 including suitable metallic/PVC gland for cable entry & required end terminations complete with all accessories like connectors suitable for connecting the cables, minor civil works, foundation works for fixing the light fixtures, Driver, JB with suitable supports etc., as required inline with tender specifications. | 25.00 | Nos |  | 38250.00 | 956250.00 | 542720.00 | 13568000.00 | 956250.00 | Instapower Ltd
2.00 | Supply, installation, testing and commissioning of Mono Colour 10W Flood luminaire (with integral driver), Extruded aluminium housing integrated with MC PCB populated with LED and optical lens beam angle (Symmetrical 15 Deg./40 Deg. with 100 lm/w) mounting option of Strap/Spike/Surface, PDC aluminium end caps fixed with silicon gasket to achieve IP66, CRI > 70, SDCM <5, P.F>0.9, Driver efficacy >80, powder coated with pure polyester Eco Gray shade, Toughened clear glass sealed with housing with silicon sealant along with supporting clamp to meet IK06 protection, Constant current IP66 Driver integrated inside of housing etc., complete as required. (Make: Wipro LF39-131-030-30-XX or its equivalent similar to the image provided & meeting the technical specifications.) Note: The scope of work covers providing and fixing of suitable loop-in & loop-out polycarbonate junction box having IP-65 including suitable metallic/PVC gland for cable entry & required end terminations complete with all accessories like connectors suitable for connecting the cables, minor civil works, foundation works for fixing the light fixtures, Driver, JB with suitable supports etc., as required inline with tender specifications. | 80.00 | Nos |  | 6885.00 | 550800.00 | 13250.00 | 1060000.00 | 550800.00 | Instapower Ltd
3.00 | Supply, installation, testing and commissioning of Mono Colour 20W Flood luminaire (with integral driver), CRI>70, SDCM <5, P.F>0.9, Driver efficacy >80, Extruded aluminium housing integrated with MC PCB populated with LED and optical lens beam angle (Symmetrical 15 Deg./30 Deg/60 deg. with 100 lm/w) mounting option of Strap/ Spike/Surface, PDC aluminium end caps fixed with silicon gasket to achieve IP66, powder coated with pure polyester Eco Gray shade, Toughened clear glass sealed with housing with silicon sealant along with supporting clamp to meet IK06 protection, Constant current IP66 Driver integrated inside of housing etc., complete as required. (make: wipro LF39-271-030-30-XX or its equivalent similar to the image provided & meeting the technical specifications.) Note: The scope of work covers providing and fixing of suitable loop-in & loop-out polycarbonate junction box having IP-65 including suitable metallic/PVC gland for cable entry & required end terminations complete with all accessories like connectors suitable for connecting the cables, civil works, foundation works for fixing the light fixtures, Driver, JB with suitable supports etc., as required inline with tender specifications. | 40.00 | Nos |  | 10710.00 | 428400.00 | 15741.00 | 629640.00 | 428400.00 | Instapower Ltd
4.00 | Supply, installation, testing and commissioning of Mono Colour 40W Flood luminaire (with integral driver), CRI>70, SDCM <5, P.F>0.9, Driver efficacy >80, Extruded aluminium housing integrated with MC PCB populated with LED and optical lens beam angle (Symmetrical 15 Deg./30 Deg/60 deg. with 100 LPW) mounting option of Strap/Spike/Surface. PDC aluminium end caps are fixed with silicon gasket to achieve IP66. Luminaire is powder coated with pure polyester Eco Gray shade. Toughened clear glass is sealed with housing with silicon sealant with supporting clamp to meet IK06 protection Constant current IP66 Driver integrated inside of housing etc., complete as required. (make: wipro LF39-521-030-30-XX or its equivalent similar to the image provided & meeting the technical specifications.) Note: The scope of work covers providing and fixing of suitable loop-in & loop-out polycarbonate junction box having IP-65 including suitable metallic/PVC gland for cable entry & required end terminations complete with all accessories like connectors suitable for connecting the cables, civil works, foundation works for fixing the light fixtures, Driver, JB with suitable supports etc., as required inline with tender specifications. | 160.00 | Nos |  | 12240.00 | 1958400.00 | 14413.00 | 2306080.00 | 1958400.00 | Instapower Ltd
5.00 | Supply, Installation, testing and commissioning of 12W 3000K LED inground luminaire with System Lumen Output of Minimum 900 Lumen (±10%), CRI > 70, CCT ≥ 3000, driver efficiency ≥ 80%, L70 > 35000 hrs. Min Inground Light die cast aluminium housing integrated with MC PCB populated with LED and optical lens beam angle Symmetrical 15 Deg. / 30 Deg. Fixture shall be made up of Die cast Aluminium Housing for better heat dissipation having IP66 Dust and Water Protection for Outdoor usage mounted on aluminium Die cast Heat Sink. SS ring shall be fixed with a min. 8mm Toughened clear glass with silicon gasket to die cast Heat sink to achieve IP67 ingress protection and meet IK10 protection. Luminaire is powder coated with Polyester TGIC for Heat Sink. The luminaire should have loop in loop out provision for power and DMX Signal. Luminaire should be capable of operating at 24VDC, with External IP66 24Vdc Driver etc., complete as required. (make: wipro LI20-111-30-30-G2 or its equivalent similar to the image provided & meeting the Technical specifications.) Light fixture shall be including of: 1) 06nos. of 120W LED Driver shall be Isolated type, Constant Voltage topology driver in metal enclosure with IP 66 Protection. Output voltage 24Vdc Driver efficiency should be 80% & proper heat sink for heat dissipation suitable to operate in input voltage range of 140V to 270V (nominal rated voltage – 240V) with 4 KV internal surge protection. LED driver shall have out put short circuit & over voltage protection inbuilt. 2) 06nos. of IP 67 Plug-in socket connector (It is 2 core Straight connector used for 3000K luminaires). 3) 41nos. of IP 67 Plug-in socket connector (It is 2 core T connector used for 3000K luminaires). Note: The scope of work covers providing and fixing of suitable loop-in & loop-out polycarbonate junction box having IP-65 including suitable metallic/PVC gland for cable entry & required end terminations complete with all accessories like connectors suitable for connecting the cables,civil works, foundation works for fixing the light fixtures, Driver, JB with suitable supports etc., as required inline with tender specifications. | 47.00 | Nos |  | 13005.00 | 611235.00 | 20776.00 | 976472.00 | 611235.00 | Instapower Ltd
6.00 | Supply, Installation, testing and commissioning of 18W Underwater Surface Mounted Device, IP 68, LED underwater light with chrome plated SS powder coated for better heat dissipation. Product comprising LEDs of 3000K CCT. Fixtures should have high purity lenses with glass with 60° Beam, IK10. The LED shall be compliant with useful L70 life of >35000 Hrs. LED Driver shall be Isolated type, with IP 68 Protection. Driver efficiency should be 80% & proper heat sink for heat dissipation suitable to operate in input voltage range of 100V to 300V nominal, power factor > 0.9, with 3 KV internal surge protection etc., complete as required. (make: wipro LU03-211-030-30-XX or its equivalent similar to the image provided & meeting the Technical specifications.) Light fixture shall be including of: 1) 07nos. of 120 W LED Driver shall be Constant Voltage topology driver in metal enclosure with IP 66 Protection. Output voltage 24Vdc LED driver shall have output short circuit & over voltage protection inbuilt. 2) 07nos. of IP 67 Plug-in socket connector (It is 2 core Straight connector used for 3000K luminaires.) 3) 25nos. of IP 67 Plug-in socket connector (It is 2 core T connector used for 3000K luminaires.) Note: The scope of work covers providing and fixing of suitable loop-in & loop-out polycarbonate junction box having IP-65 including suitable metallic/PVC gland for cable entry & required end terminations complete with all accessories like connectors suitable for connecting the cables,civil works, foundation works for fixing the light fixtures, Driver, JB with suitable supports etc., as required inline with tender specifications. | 20.00 | Nos |  | 18360.00 | 367200.00 | 41340.00 | 826800.00 | 367200.00 | Instapower Ltd
7.00 | Supply, Installation, testing and commissioning of 18W RGB LED Underwater Surface Mounted Device, IP 68, LED underwater light with chrome plated SS powder coated for better heat dissipation. Product comprising LEDs of RGB CCT. Fixtures should have high purity lenses with glass with 60° Beam, IK10. The LED shall be compliant with useful L70 life of >35000 Hrs. LED Driver shall be Isolated type, with IP 68 Protection. Driver efficiency should be 80% & proper heat sink for heat dissipation suitable to operate in input voltage range of 100V to 300V nominal, power factor > 0.9, with 3 KV internal surge protection etc., complete as required. (make: wipro LU03-211-030-CC-XX or its equivalent similar to the image provided & meeting the Technical specifications.) Light fixture shall be including of: 1) 04nos. of 120 W LED Driver shall be, Constant Voltage topology driver in metal enclosure with IP 66 Protection. Output voltage 24Vdc LED driver shall have output short circuit & over voltage protection inbuilt. 2) 04nos. of IP 67 Plug-in socket connector (It is 2 core Straight connector used for 3000K luminaires.) 3) 08nos. of IP 67 Plug-in socket connector (It is 2 core T connector used for 3000K luminaires.) Note: The scope of work covers providing and fixing of suitable loop-in & loop-out polycarbonate junction box having IP-65 including suitable metallic/PVC gland for cable entry & required end terminations complete with all accessories like connectors suitable for connecting the cables,civil works, foundation works for fixing the light fixtures, Driver, JB with suitable supports etc., as required inline with tender specifications . | 12.00 | Nos |  | 26775.00 | 321300.00 | 41340.00 | 496080.00 | 321300.00 | Instapower Ltd
8.00 | Supply, installation, testing and commissioning of 6W to 7.5W LED Step luminaire (with integral driver) Extruded Aluminium Housing IP-66 , IK-07, driver efficiency ≥ 75%, CRI ≥ 70, PF > 0.9, etc., complete as required. (make: wipro LT51-750-XXX-30-XX or its equivalent similar to the image provided & meeting the Technical specifications.) Note: The scope of work covers providing and fixing of suitable loop-in & loop-out polycarbonate junction box having IP-65 including suitable metallic/PVC gland for cable entry & required end terminations complete with all accessories like connectors suitable for connecting the cables, civil works, foundation works for fixing the light fixtures, Driver, JB with suitable supports etc., as required inline with tender specifications. | 140.00 | Nos |  | 11475.00 | 1606500.00 | 3710.00 | 519400.00 | 519400.00 | BUDHIRAJA ELECTRICALS
9.00 | Providing, laying, fixing, connecting and testing of following sizes of GI strip/GI wire from earth electrode to equipment loop and earthing system, in trenches, on surfaces, along pole or along M.S. support, etc. including excavation where required for laying the copper strip/ GI strip and filling back complete, conforming to relevant IS and all as specified. GI wire 8 SWG | 100.00 | Mtr |  | 76.00 | 7600.00 | 42.00 | 4200.00 | 4200.00 | BUDHIRAJA ELECTRICALS
10.00 | Providing, laying, fixing, connecting and testing of following sizes of GI strip/GI wire from earth electrode to equipment loop and earthing system, in trenches, on surfaces, along pole or along M.S. support, etc. including excavation where required for laying the copper strip/ GI strip and filling back complete, conforming to relevant IS and all as specified. Hot dip GI strip 25mmx 5mm on surface or in recess | 100.00 | Mtr |  | 268.00 | 26800.00 | 220.00 | 22000.00 | 22000.00 | BUDHIRAJA ELECTRICALS
11.00 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 16205 complete with fitting and cutting, jointing etc. direct in ground (75 cm below ground level) including excavation and refilling earthwork, and protective covering etc., complete as required. 63 mm dia. (OD-63 mm & ID-51 mm nominal) | 3594.00 | Mtr |  | 352.00 | 1265088.00 | 280.00 | 1006320.00 | 1006320.00 | BUDHIRAJA ELECTRICALS
12.00 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 16205 Part II complete with fitting and cutting, jointing etc. direct in ground (75 cm below ground level) including excavation and refilling earthwork, and protective covering etc., complete as required. 90 mm dia. (OD-90 mm & ID-76 mm nominal) | 168.00 | Mtr |  | 688.00 | 115584.00 | 350.00 | 58800.00 | 58800.00 | BUDHIRAJA ELECTRICALS
13.00 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 16205 Part II complete with fitting and cutting, jointing etc. direct in ground (75 cm below ground level) including excavation and refilling earthwork, and protective covering etc., complete as required. 120 mm dia. (OD-120 mm & ID-103 mm nominal) | 1344.00 | Mtr |  | 903.00 | 1213632.00 | 450.00 | 604800.00 | 604800.00 | BUDHIRAJA ELECTRICALS
14.00 | LT CABLES & CABLE LAYING Supply of following size of 1.1 KV grade FRLS multicore aluminium conductor XLPE insulated and PVC extruded sheathed armoured cable as per IS: 7098:1988 (Part-I) with upto date amendments etc., as required. 3½ core X 120 Sq.mm Al. | 650.00 | Mtr |  | 842.00 | 547300.00 | 1100.00 | 715000.00 | 547300.00 | Instapower Ltd
15.00 | Supply of following size of 1.1 KV grade FRLS multicore aluminium conductor XLPE insulated and PVC sheathed extruded armoured cable as per IS: 7098:1988 (Part-I) with upto date amendments etc., as required. 4 core X 25 Sq.mm Al. | 500.00 | Mtr |  | 283.00 | 141500.00 | 380.00 | 190000.00 | 141500.00 | Instapower Ltd
16.00 | Supply of following size of 1.1 KV grade FRLS multicore copper conductor XLPE insulated and PVC sheathed extruded armoured cable as per IS: 7098:1988 (Part-I) with upto date amendments etc., as required. 4 core X 4 Sq.mm Cu. | 1470.00 | Mtr |  | 336.00 | 493920.00 | 450.00 | 661500.00 | 493920.00 | Instapower Ltd
17.00 | Supply of following size of 1.1 KV grade FRLS multicore copper conductor XLPE insulated and PVC sheathed extruded armoured cable as per IS: 7098:1988 (Part-I) with upto date amendments etc., as required. 4 core X 6 Sq.mm Cu. | 3300.00 | Mtr |  | 477.00 | 1574100.00 | 580.00 | 1914000.00 | 1574100.00 | Instapower Ltd
18.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on existing cable tray as required. Tagging on both the ends will be done with aluminium tags etc. complete as required. (Cable in cable tray shall be clamped with 1mm thick saddle) Upto 35 sq. mm | 500.00 | Mtr |  | 100.00 | 50000.00 | 100.00 | 50000.00 | 50000.00 | Instapower Ltd, BUDHIRAJA ELECTRICALS
19.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on existing cable tray as required. Tagging on both the ends will be done with aluminium tags etc. complete as required. (Cable in cable tray shall be clamped with 1mm thick saddle) Above 95 sq. mm and upto 185 sq. mm | 630.00 | Mtr |  | 230.00 | 144900.00 | 180.00 | 113400.00 | 113400.00 | BUDHIRAJA ELECTRICALS
20.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ STONEWARE/ METAL/ DWC HDPE pipe etc. complete as required. Upto 35 sq. mm | 4770.00 | Mtr |  | 76.00 | 362520.00 | 65.00 | 310050.00 | 310050.00 | BUDHIRAJA ELECTRICALS
21.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ STONEWARE/ METAL/ DWC HDPE pipe etc. complete as required. Above 95 sq. mm and upto 185 sq. mm | 20.00 | Mtr |  | 153.00 | 3060.00 | 100.00 | 2000.00 | 2000.00 | BUDHIRAJA ELECTRICALS
22.00 | Supplying and making indoor end termination with brass single compression gland (Heavy duty type) and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor armoured cable of 1.1 KV grade as required. 3½ core X 120 Sq.mm Al. | 4.00 | Nos |  | 1147.00 | 4588.00 | 800.00 | 3200.00 | 3200.00 | BUDHIRAJA ELECTRICALS
23.00 | Supplying and making indoor end termination with brass single compression gland (Heavy duty type) and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor armoured cable of 1.1 KV grade as required. 4 core X 25 Sq.mm Al. | 32.00 | Nos |  | 688.00 | 22016.00 | 450.00 | 14400.00 | 14400.00 | BUDHIRAJA ELECTRICALS
24.00 | Supplying and making indoor end termination with brass single compression gland (Heavy duty type) and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor armoured cable of 1.1 KV grade as required. 4core X 4 Sq.mm Cu. | 490.00 | Nos |  | 306.00 | 149940.00 | 250.00 | 122500.00 | 122500.00 | BUDHIRAJA ELECTRICALS
25.00 | Supplying and making indoor end termination with brass single compression gland (Heavy duty type) and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor armoured cable of 1.1 KV grade as required. 4 core X 6 Sq.mm Cu. | 558.00 | Nos |  | 336.00 | 187488.00 | 300.00 | 167400.00 | 167400.00 | BUDHIRAJA ELECTRICALS
26.00 | Supplying and fixing 32 A, 415 V, TPN Industrial type socket outlet (IP-65), with 3 pole and earth, plug top along with 63 A, 10 kA MCB in IP-65, IK-08 Polycarbonate enclosure with cover for the socket outlet and complete with connections, testing and commissioning etc. including 1.25 Mtr. MS 'C' class stand post of suitable dia. (minimum 50 mm) including civil foundation work (PCC) complete in all respect etc., as required. | 4.00 | Nos |  | 7650.00 | 30600.00 | 6000.00 | 24000.00 | 24000.00 | BUDHIRAJA ELECTRICALS
27.00 | Constructing brick masonry manhole in cement mortar 1:4 (1 cement : 4 coarse sand) with R.C.C. top slab with 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size), foundation concrete 1:4:8 mix (1 cement : 4 coarse sand : 8 graded stone aggregate 40 mm nominal size), inside plastering 12 mm thick with cement mortar 1:3 (1 cement : 3 coarse sand) finished with floating coat of neat cement and making channels in cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) finished with a floating coat of neat cement complete as per standard design: Inside size 100 x 100 cm and 100 cm deep including RCC cover with frame (heavy duty). With common burnt clay F.P.S. (non modular) bricks of class designation 7.5 | 14.00 | Nos |  | 68850.00 | 963900.00 | 18000.00 | 252000.00 | 252000.00 | BUDHIRAJA ELECTRICALS
28.00 | External Lighting Feeder pillars Supply, installation, testing & commissioning of LT weather proof dust and vermin proof, outdoor feeder pillar, fabricated out of modular Polycarbonate thermoplastic enclosure/FRP enclosure for environment friendly, recyclable, UV resistant, halogen & silicon free, anti acid & anti corrosive. The gasket material shall be Polyurethane; while the gasket shall be internally embedded. Panel shall be openable with locking arrangement/ front operated, if panel board type. Panel shall be IP-65 or higher rated and enclosure shall be type tested as per IS -61439 etc. The feeder pillars shall be complete with 3 phase and neutral bus bars of capacities as described below and moulded case circuit breakers (MCCBs) with adjustable overload relay, copper FRLS control wiring with 1.5 sq.mm, duly painted complete with earth bus, aluminium bus bar, numbering & sign writing, interconnection etc. as per technical specification & CPRI test reports for short circuit, dielectric strength mechanical protection IK-08 and temperature rise test reports. Incomer: i) 1 No. 100 Amps. 4P MCCB '25ka, Icu=Ics at 433 volts with thermal based release with operating handle, spreader links, ON indicating lamp with 2A backup MCB having O/L, S/C, earth fault protection equipped with the following: Bus bar: 160 Amp 4P, 16kA busbars of high conductivity electrolytic quality aluminium alloy. Outgoing: 4 sets of 63 Amps, 4P, MCB, 10kA with 63 Amps, 4P Contractor. 2 Nos. 0-24 hour timer auto/manual by pass selector switches 1 No. 63 Amp, 4P MCB, 10kA 3 Nos. 63 Amp DP RCCB's of 300 mA leakage current. 3 Nos. 63 Amps DP contractor. 24 Nos. 6 to 25 Amps SP MCB, 10kA. | 2.00 | Nos |  | 153000.00 | 306000.00 | 220000.00 | 440000.00 | 306000.00 | Instapower Ltd
29.00 | Supply and fixing of 17.2 mm Copper bonded BIS certified rod of 3 Mtr length complete environment friendly, RoHS certified, low resistivity Ground enhancement material in 22.6 Kg pack, including pit cover, clamping arrangements to fill the bore area around the rod complete in all respect etc., as required as per technical specifications. | 4.00 | Nos |  | 13525.20 | 54100.80 | 15000.00 | 60000.00 | 54100.80 | Instapower Ltd
30.00 | Providing, laying and fixing of following dia. R.C.C. pipe NP3 class complete with R.C.C. collars, jointing with cement mortar 1:2 (1 cement : 2 fine sand) for road crossings including excavation and refilling etc. complete as required. 150 mm | 410.00 | Mtr |  | 2295.00 | 940950.00 | 600.00 | 246000.00 | 246000.00 | BUDHIRAJA ELECTRICALS
31.00 | Making Horizontal boring by suitable mechanical arrangment, Sensor operated, Min 2.5 mts depth, horizontal borewell suitable for inserting 01no 160mm dia HDPE pipe, job including inserting of HDPE pipe in bore well hole, but welding etc., complete as per site requirment. | 120.00 | Mtr |  | 1836.00 | 220320.00 | 6000.00 | 720000.00 | 220320.00 | Instapower Ltd
32.00 | Supply of 160mm dia size HDPE pipe, ISI marked along with all accessories like socket, couplers etc. conforming to IS 4984-1995, NP6 grade, PE63 etc., complete as required. | 132.00 | Mtr |  | 842.00 | 111144.00 | 530.00 | 69960.00 | 69960.00 | BUDHIRAJA ELECTRICALS
33.00 | Providing and fixing flow solar studs of size 125 x 125 x 20 mm made of heavy duty body of moulded Aluminium Alloy and High Impact Polystyrene/Polycarbonate having electronically welded micro-prismatic lens with abrasion resistant coating as approved by Engineer in Charge. The glow stud shall support a load of 13635 kg tested in accordance with ASTM D4280. The slope of retro reflective surface shall be 35 (+/-5) degree to base. The illuminated panels on both sides with at least 12 cm of illuminating area up each side. It shall be tested as described in ASTM I: 809 as recommended in BS: 873 part 4:1973. The studs shall be fixed to the road surface using the adhesive confirming to IS, as per procedure recommended by the manufacturer complete and as per direction of Engineering In Charge. | 550.00 | Nos |  | 2754.00 | 1514700.00 | 2000.00 | 1100000.00 | 1100000.00 | BUDHIRAJA ELECTRICALS
| Total in Figures |  |  |  |  | 17251835.80 |  | 29254002.00
Lowest Amount Quoted BY: Instapower Ltd(17251835.80)

## BOQ Summary
BOQ Summary Details Tender Title: Up-gradation of Passenger Terminal Building and Airside Facilities at Trichy International Airport. S.H. Provision of Landscape Lighting for NITB at Trichy Airport Tender ID: 2023_AAI_155489_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Instapower Ltd | 17251835.80 | L1
| 2 | BUDHIRAJA ELECTRICALS | 29254002.00 | L2