## BoQ1
Government eProcurement System Created By: VETRISELVI JAGADEESAN Created Date/Time: 10-Jul-2023 05:59 PM Tender Title: Provision of Additional Pumps in the existing Fire Fighting system in Utility building at Chennai Airport Tender ID: 2023_AAI_155604_1
Tender Inviting Authority: AGM (Engg-Elect)-V, Airports Authority of India, Chennai Airport, Chennai-600016.
Name of Work: Provision of Additional Pumps for Fire Fighting System in Utility Building at Chennai Airport.
Contract No: AAI/CHE/AMED-V/2023-24/01
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | CENTRE TAP ENGINEERING(GSTN-24AGPPP8172K1ZP) |  | DElite System Engineering (India) Pvt. Ltd.(GSTN-NA) |  | J.K.DEFENCE FIRE ENGG. SERVICES(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply, installation, testing and commissioning of Electric driven main fire pump suitable for automatic operation and consisting of following: complete in all respect as required as per enclosed specifications. Horizontal type, multistage, centrifugal, split casing pump of cast iron body and bronze impeller with stainless steel shaft, mechanical seal to ensure a minimum pressure of 3.5 kg/sq.cm.at highest and farthest outlet at specified flow of 2850 lpm at minimum 110 M head conforming to IS 1520. 100 HP squirrel cage induction motor, TEFC, IE3,speed 1500 RPM, suitable for operation on 415 volts, 3 phase 50 Hz. AC with IP 55 protection for enclosure, horizontal foot mounted type with Class-'F' insulation, conforming to IS- 325. M.S. fabricated Common base Frame onsisiting of 100 x 50 x6 mm C channel, coupling with guard, foundation bolts etc. duly painted as required. Suitable cement concrete foundation duly plastered with anti vibration pads etc complete as required. | 2.00 | Job |  | 500000.00 | 1000000.00 | 1000000.00 | 2000000.00 | 850000.00 | 1700000.00 | 1000000.00 | CENTRE TAP ENGINEERING
2.00 | Supply, Installation, testing and commissioning of electric driven pressurisation(Jockey) pump suitable for automatic operation and consisting o following: complete in all respect as required as per specifications. Horizontal type, multistage, centrifugal pump of cast iron body and bronze impeller with stainless steel shaft, mechanical seal and flow of 180 lpm at minimum 110 m head conforming to IS : 1520. 10 HP Squirrel cage induction motor TEFC type, IE3 suitable for operation on 415 volts, 3 phase 50 Hz. AC with IP 55 protection for enclosure, horizontal foot mounted type with Class-'F' insulation, conforming to IS : 325. M.S. fabricated Common base Frame consisiting of 100 x 50 x6 mm C channel, coupling with guard, foundation bolts etc. duly painted as required. Suitable cement concrete foundation duly plastered with anti vibration pads etc complete as required. | 2.00 | Job |  | 150000.00 | 300000.00 | 400000.00 | 800000.00 | 210000.00 | 420000.00 | 300000.00 | CENTRE TAP ENGINEERING
3.00 | Supplying, installation, testing, & commissioning of pressure switches for Electric driven Main and Jockey Pumps, including Control valve, necessary wiring upto control panel & other materials etc complete as required as per specifications | 4.00 | Job |  | 3000.00 | 12000.00 | 5500.00 | 22000.00 | 3500.00 | 14000.00 | 12000.00 | CENTRE TAP ENGINEERING
4.00 | Supply & fixing dial type (100 mm) pressure gauge with isolation ball valve suitable for working pressure of 250 PSI, short pieces, nipples, elbows, stainless steel 'U' tube & ball valve, etc complete as required as per specifications. | 6.00 | Job |  | 1500.00 | 9000.00 | 5000.00 | 30000.00 | 4000.00 | 24000.00 | 9000.00 | CENTRE TAP ENGINEERING
5.00 | Supply, laying, testing and comissioning of 'C' Class heavy duty MS Pipe conforming to IS:1239 / 3589 including fittings like tees, elbows, flanges, tapers, compressed asbestos gaskets, nuts and bolts, etc. Fixing the pipe on wall / ceiling with suitable clamps and painting with two or more coats of synthetic enamel paint of required shade etc complete as required.
5.01 | 25 mm dia | 10.00 | Mtrs. |  | 800.00 | 8000.00 | 900.00 | 9000.00 | 300.00 | 3000.00 | 3000.00 | J.K.DEFENCE FIRE ENGG. SERVICES
5.02 | 50 mm dia | 30.00 | Mtrs. |  | 1200.00 | 36000.00 | 900.00 | 27000.00 | 600.00 | 18000.00 | 18000.00 | J.K.DEFENCE FIRE ENGG. SERVICES
5.03 | 65 mm dia | 20.00 | Mtrs. |  | 1400.00 | 28000.00 | 1300.00 | 26000.00 | 700.00 | 14000.00 | 14000.00 | J.K.DEFENCE FIRE ENGG. SERVICES
5.04 | 150 mm dia(6.35mm thick) | 30.00 | Mtrs. |  | 3500.00 | 105000.00 | 3200.00 | 96000.00 | 1900.00 | 57000.00 | 57000.00 | J.K.DEFENCE FIRE ENGG. SERVICES
5.05 | 200 mm dia (6.35mm thick ) | 20.00 | Mtrs. |  | 4500.00 | 90000.00 | 4000.00 | 80000.00 | 3000.00 | 60000.00 | 60000.00 | J.K.DEFENCE FIRE ENGG. SERVICES
5.06 | 300mm nominal dia (6.35mm thick ) | 30.00 | Mtrs. |  | 5500.00 | 165000.00 | 5000.00 | 150000.00 | 4000.00 | 120000.00 | 120000.00 | J.K.DEFENCE FIRE ENGG. SERVICES
6.00 | Supply, installation, testing & commissioning of Y type CI strainer fabricated out of 1.6 mm thick stainless steel sheet with 3 mm dia holes with stainless steel flange etc complete as required.
6.01 | 200mm dia | 2.00 | Nos. |  | 50000.00 | 100000.00 | 39000.00 | 78000.00 | 30000.00 | 60000.00 | 60000.00 | J.K.DEFENCE FIRE ENGG. SERVICES
6.02 | 65mm dia | 2.00 | Nos. |  | 30000.00 | 60000.00 | 5500.00 | 11000.00 | 5000.00 | 10000.00 | 10000.00 | J.K.DEFENCE FIRE ENGG. SERVICES
7.00 | Supply, installation, testing & commissioning of Butterfly Valve, Wafer Type with Micro Switch & Position indicator, 300 PSI Rating, UL Listed & FM Approved, complete with matching flanges, gaskets, galvanised fasteners. Valves shall be fitted with lockable steel strapping (pad lock) arrangement.
7.01 | 150 mm dia | 5.00 | Nos. |  | 10000.00 | 50000.00 | 4000.00 | 20000.00 | 7000.00 | 35000.00 | 20000.00 | DElite System Engineering (India) Pvt. Ltd.
7.02 | 200 mm dia | 1.00 | Nos. |  | 15000.00 | 15000.00 | 7200.00 | 7200.00 | 15000.00 | 15000.00 | 7200.00 | DElite System Engineering (India) Pvt. Ltd.
8.00 | Supply, installation, testing & commissioning of Swing Check Valve, Ductile iron body, 300PSI, Flanged ends ANSI, UL Listed and FM Approved with required matching flanges, rubber seated, nuts, bolts & gaskets etc complete as required as per technical specification.
8.01 | 200 mm nominal dia | 1.00 | Nos. |  | 20000.00 | 20000.00 | 19000.00 | 19000.00 | 18000.00 | 18000.00 | 18000.00 | J.K.DEFENCE FIRE ENGG. SERVICES
8.02 | 150 mm nominal dia | 2.00 | Nos. |  | 15000.00 | 30000.00 | 9000.00 | 18000.00 | 9000.00 | 18000.00 | 18000.00 | DElite System Engineering (India) Pvt. Ltd., J.K.DEFENCE FIRE ENGG. SERVICES
8.03 | 50 mm nominal dia | 2.00 | Nos. |  | 80000.00 | 160000.00 | 3700.00 | 7400.00 | 6000.00 | 12000.00 | 7400.00 | DElite System Engineering (India) Pvt. Ltd.
9.00 | Supply, installation, testing & commissioning of Ductile iron Gate Valve, Rising Spindle OS & Y Type, Flanged BS5163,300 PSI,UL Listed & FM Approved etc complete as required.
9.01 | 300 mm dia | 1.00 | No. |  | 80000.00 | 80000.00 | 82000.00 | 82000.00 | 40000.00 | 40000.00 | 40000.00 | J.K.DEFENCE FIRE ENGG. SERVICES
9.02 | 200mm nominal dia | 2.00 | Nos. |  | 45000.00 | 90000.00 | 44000.00 | 88000.00 | 30000.00 | 60000.00 | 60000.00 | J.K.DEFENCE FIRE ENGG. SERVICES
9.03 | 150mm dia | 2.00 | Nos. |  | 35000.00 | 70000.00 | 27000.00 | 54000.00 | 18000.00 | 36000.00 | 36000.00 | J.K.DEFENCE FIRE ENGG. SERVICES
9.04 | 65mm dia | 2.00 | Nos. |  | 15000.00 | 30000.00 | 12000.00 | 24000.00 | 10000.00 | 20000.00 | 20000.00 | J.K.DEFENCE FIRE ENGG. SERVICES
9.05 | 50 mm dia | 2.00 | Nos. |  | 10000.00 | 20000.00 | 9000.00 | 18000.00 | 6000.00 | 12000.00 | 12000.00 | J.K.DEFENCE FIRE ENGG. SERVICES
10.00 | Supply installation testing and commissioning of Expansion bellows (suitable size and thick suitable for system test pressure) at pump delivery side with high tensile nylon/polyester cord body, high tensile nylon flanges with positive sealing, NEOPRENE rubber outer Cover & with Leak proof Abrasion resistant seamless lining of Rubber, Metal Retaining Rings embedded in body including all necessary accessories like nuts, bolts etc. complete of approved make as required as per site requirement.
10.01 | 200mm nominal dia | 2.00 | Nos. |  | 20000.00 | 40000.00 | 10000.00 | 20000.00 | 15000.00 | 30000.00 | 20000.00 | DElite System Engineering (India) Pvt. Ltd.
10.02 | 150mm dia | 2.00 | Nos |  | 15000.00 | 30000.00 | 9000.00 | 18000.00 | 10000.00 | 20000.00 | 18000.00 | DElite System Engineering (India) Pvt. Ltd.
10.03 | 65mm dia | 2.00 | Nos |  | 13000.00 | 26000.00 | 4000.00 | 8000.00 | 8000.00 | 16000.00 | 8000.00 | DElite System Engineering (India) Pvt. Ltd.
10.04 | 50mm nominal dia | 2.00 | Nos |  | 10000.00 | 20000.00 | 3500.00 | 7000.00 | 6500.00 | 13000.00 | 7000.00 | DElite System Engineering (India) Pvt. Ltd.
11.00 | Supply and fixing of Air vessel tank of 250mm dia, 8mm thick MS sheet, 1200mm in height with air release valve on top and flanged connection to riser, drain arrangement with 25mm dia gun metal wheel valve with required accessories like pressure gauge etc. i/c painting with synthetic enamel paint of approved shade etc complete as required as per specifications. | 2.00 | Set |  | 80000.00 | 160000.00 | 25000.00 | 50000.00 | 35000.00 | 70000.00 | 50000.00 | DElite System Engineering (India) Pvt. Ltd.
12.00 | Supply and fixing of spring loaded release valve suitable for pressure of 16 Kg / sqcm including flanges nuts, bolt and washer etc complete as required as per site requirement. 25 mm dia | 2.00 | Set |  | 3000.00 | 6000.00 | 5000.00 | 10000.00 | 3500.00 | 7000.00 | 6000.00 | CENTRE TAP ENGINEERING
13.00 | Supply, Installation, Testing and Commissioning of cubicle type Main Distribution Panel, IP55, suitable for 415V+/-10%, 3 Phase, 4 wire, 50 Hz AC supply system fabricated in compartmentalized modular design from CRCA sheet steel of 2 mm thick for frame work and covers, 3 mm thick for gland, plates i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having TPN Aluminium alloy bus bars for high conductivity, DMC/SMC bus bar supports with short circuit withstand capacity of 25 KA for 1 sec, bottom base channel of MS section not less than 100 mm x 50 mm x 5 mm thick, fabrication shall be done in transportable sections, entire panel shall have a common copper earth bar of size 25 mm x 5 mm at the rear with 2 Nos. earth stud, solid / flexible connections from main bus bar to switchgears and from switchgear output to cable termination in cable alley with required size of Aluminium conductors / bus bars and control wiring with 2.5 sqmm PVC insulated copper conductor cable (FRLS), cable alleys, cable gland plates in two half, i/c providing following switchgears / accessories as per specifications. INCOMER 2 Nos.400 Amps,four pole MCCB,(Ics = Icu = 25 KA), microprocessor release with adjustable setting for O/C, S/C & E/F protection as per specification and with following accessories. digital meter to read V,A, Hz etc with communication facility (RS485 port) and LED display with required Nos CTs, 400/5,5VA class 1.0 and control circuit wiring with 2 Amp MCB for controling BUSCOUPLER 1 No. 400 Amp ,four pole Moulded Case Circuit Breaker (Ics = Icu = 25 KA) microprocessor release unit with adjustable setting with O/L, S/C and inbuilt E/F protection as per specification BUSBARS TPN aluminium bus bars of minimum 800 Amps capacity with heat shrinkable coloured sleeves and i/c, SMC bus bars supports at required intervals complete for cross section, size supports & their spacing etc. for withstanding fault level of 25 KA for 1 sec.
13.01 | OUTGOING 250 Amps MCCB,TP,(Ics = Icu = 25 KA), microprocessor release with adjustable setting for O/C, S/C & E/F protection, 100 HP pump with Star Delta starter for Hydrant, Sprinkler & 0-250 Amps Ammeter with 3 nos. 250/5A CTs, Class I accuracy and 5 VA burden with RS 485 communication port, current sensing type single phase preventor complete with all accessories and internal wiring required for automatic operation, Auto/Manual selector switch and indication lamp with 2 Amps MCBs for ON/OFF status of motor -2 sets. 40 Amps MCCB ,TP,(Ics = Icu = 25 KA), with built in thermal magnetic release with fixed setting for O/C & S/C protection, 10 HP pump with DOL starter for Jockey pumps motor, 0-40 Amps Ammeter with 3 nos. 40/5A CTs, Class I accuracy and 5 VA burden with RS 485 communication port, current sensing type single phase preventor complete with all accessories and internal wiring required for automatic operation, Auto/Manual selector switch and indication lamp with 2 Amps MCBs for ON/OFF status of motor - 2 sets. 40 Amps MCCB ,TP,(Ics = Icu = 25 KA), with built in thermal magnetic release with fixed setting for O/C & S/C protection, 10 HP pump with DOL starter for Jockey pumps motor, 0-40 Amps Ammeter with 3 nos. 40/5A CTs, Class I accuracy and 5 VA burden with RS 485 communication port, current sensing type single phase preventor complete with all accessories and internal wiring required for automatic operation, Auto/Manual selector switch and indication lamp with 2 Amps MCBs for ON/OFF status of motor - 2 sets.
13.02 | System Controller Designing, supplying, installation, testing and commissioning of System controller to control operation of main electric fire pump, pressurisation pump in sequence as per specification consisting of relays, timers, sensors, annunciation window for fault indication, complete as per specification. Note: All incomer & buscoupler MCCB shall be mechanical interlocked with suitable accessories. Separate neutral link shall be provided in all 3 Pole feeders. All breakers breaking capacities shall be Icu=Ics | 1.00 | Set |  | 500000.00 | 500000.00 | 400000.00 | 400000.00 | 525000.00 | 525000.00 | 400000.00 | DElite System Engineering (India) Pvt. Ltd.
14.00 | Supply and Installing following size of perforated Hot dip G.I cable tray including horizontal and vertical bends, reducers, tees, cross members and other accessories as required and duly suspended from the ceiling with MS suspenders and including paintingetc complete as required as per technical specification.
14.01 | 300 mm width x 60mm depth x 1.6 mm thickness. | 30.00 | Mtrs. |  | 5000.00 | 150000.00 | 1100.00 | 33000.00 | 750.00 | 22500.00 | 22500.00 | J.K.DEFENCE FIRE ENGG. SERVICES
14.02 | 150 mm width x 60mm depth x 1.6 mm thickness. | 30.00 | Mtrs. |  | 2500.00 | 75000.00 | 900.00 | 27000.00 | 500.00 | 15000.00 | 15000.00 | J.K.DEFENCE FIRE ENGG. SERVICES
15.00 | Supply, Laying, Fixing, Testing and Commissioning of following sizes of XLPE insulated PVC sheathed armoured Copper / aluminium conductor cable of 1.1 KV grade on existing cable tray / surface as required.
15.01 | 2C x 1.5 Sq mm copper conductor armoured control cable. | 60.00 | Mtrs. |  | 100.00 | 6000.00 | 400.00 | 24000.00 | 90.00 | 5400.00 | 5400.00 | J.K.DEFENCE FIRE ENGG. SERVICES
15.02 | 3 x 10 Sq.mm. Aluminium Armoured | 50.00 | Mtrs. |  | 200.00 | 10000.00 | 300.00 | 15000.00 | 250.00 | 12500.00 | 10000.00 | CENTRE TAP ENGINEERING
15.03 | 3 x 120 Sq.mm. Aluminium Armoured | 100.00 | Mtrs. |  | 500.00 | 50000.00 | 490.00 | 49000.00 | 1000.00 | 100000.00 | 49000.00 | DElite System Engineering (India) Pvt. Ltd.
15.04 | 3 1/2 x 300 Sq.mm. Aluminium Armoured | 50.00 | Mtrs. |  | 1000.00 | 50000.00 | 900.00 | 45000.00 | 1900.00 | 95000.00 | 45000.00 | DElite System Engineering (India) Pvt. Ltd.
16.00 | Supply and making end termination with brass compression gland and copper/ aluminium lugs for following size of XLPE insulated and PVC sheathed aluminium conductor cable of 1.1 KV grade as required.
16.01 | 2core x 1.5 Sq mm copper conductor armoured control cable. | 8.00 | Nos. |  | 200.00 | 1600.00 | 500.00 | 4000.00 | 250.00 | 2000.00 | 1600.00 | CENTRE TAP ENGINEERING
16.02 | 3 x 10 Sq.mm. Aluminium Armoured | 4.00 | Nos. |  | 300.00 | 1200.00 | 700.00 | 2800.00 | 750.00 | 3000.00 | 1200.00 | CENTRE TAP ENGINEERING
16.03 | 3 x 120 Sq.mm. Aluminium Armoured | 8.00 | Nos. |  | 500.00 | 4000.00 | 999.00 | 7992.00 | 1000.00 | 8000.00 | 4000.00 | CENTRE TAP ENGINEERING
16.04 | 3.5 core x 300 Sq.mm. Aluminium Armoured | 4.00 | Nos. |  | 1000.00 | 4000.00 | 1200.00 | 4800.00 | 1800.00 | 7200.00 | 4000.00 | CENTRE TAP ENGINEERING
17.00 | Supply and fixing of following size of GI strips/ GI wire etc. on surface or in recess for connections, including GI clamps etc. as required.
17.01 | 25 mm x 5 mm GI strip | 30.00 | Mtrs. |  | 1000.00 | 30000.00 | 400.00 | 12000.00 | 600.00 | 18000.00 | 12000.00 | DElite System Engineering (India) Pvt. Ltd.
17.02 | 6 SWG dia G.I. wire | 30.00 | Mtrs. |  | 200.00 | 6000.00 | 50.00 | 1500.00 | 350.00 | 10500.00 | 1500.00 | DElite System Engineering (India) Pvt. Ltd.
18.00 | Supply and fixing of Shock treatment chart both in Regional, Hindi & English and framed with 5mm thick glass as required. | 2.00 | Nos. |  | 1000.00 | 2000.00 | 900.00 | 1800.00 | 4000.00 | 8000.00 | 1800.00 | DElite System Engineering (India) Pvt. Ltd.
19.00 | Supply & fixing LT danger notice plate of 250 mm x 200mm, made of mild steel sheet of at least 2mm thick & vitreous enamelled white on both sides and with inscription in signal red colour on front side as required. | 2.00 | Nos. |  | 500.00 | 1000.00 | 900.00 | 1800.00 | 3500.00 | 7000.00 | 1000.00 | CENTRE TAP ENGINEERING
20.00 | Supply of synthetic Insulation mat of 1 meter wide & 2.0mm thick to withstand 2.5kV dielectric strength as per IS 15652- 2006 | 4.00 | Mtrs. |  | 2000.00 | 8000.00 | 1200.00 | 4800.00 | 3000.00 | 12000.00 | 4800.00 | DElite System Engineering (India) Pvt. Ltd.
21.00 | Supply of Single Line Diagram pasted on 5mm thick Aluminium sheet in A1 Size, duly laminated. | 2.00 | Nos. |  | 5000.00 | 10000.00 | 3000.00 | 6000.00 | 4500.00 | 9000.00 | 6000.00 | DElite System Engineering (India) Pvt. Ltd.
22.00 | Supplying and making straight through joint of size 3.5 X 300 sq mm with heat Shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required | 2.00 | Nos. |  | 5000.00 | 10000.00 | 9000.00 | 18000.00 | 10000.00 | 20000.00 | 10000.00 | CENTRE TAP ENGINEERING
23.00 | Supply, Installation, Testing and Commissioning of loop in /loop out cubicle type Main Distribution Panel, IP55, suitable for 415V+/-10%, 3 Phase, 4 wire 50 Hz AC supply system fabricated in modular design from CRCA sheet steel of 2 mm thick for frame work and covers, 3 mm thick for gland, plates i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having TPN Aluminium alloy bus bars for high conductivity, DMC/SMC bus bar supports,with short circuit withstand capacity of 25 KA for 1 sec, fabrication shall be done in transportable sections, entire panel shall have a common copper earth bar of suitable size at the rear with 2 Nos. earth stud, solid / flexible connections from main bus bar of 630 Amps capacity to outgoing busbars. Panel shall have provision to accomodate single incomer cable & outgoing cable of 02 Nos of 3.5 C X 300 Sqmm Al armoured cable etc. complete as required. | 2.00 | Nos. |  | 100000.00 | 200000.00 | 79000.00 | 158000.00 | 95000.00 | 190000.00 | 158000.00 | DElite System Engineering (India) Pvt. Ltd.
| Total in Figures |  |  |  |  | 3878800.00 |  | 4596092.00 |  | 3992100.00
Lowest Amount Quoted BY: CENTRE TAP ENGINEERING(3878800.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of Additional Pumps in the existing Fire Fighting system in Utility building at Chennai Airport Tender ID: 2023_AAI_155604_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | CENTRE TAP ENGINEERING | 3878800.00 | L1
| 2 | J.K.DEFENCE FIRE ENGG. SERVICES | 3992100.00 | L2
| 3 | DElite System Engineering (India) Pvt. Ltd. | 4596092.00 | L3