## BoQ1
Government eProcurement System Created By: Rajesh Tamrakar Created Date/Time: 14-Jul-2023 04:51 PM Tender Title: Precision Air-conditioning works for the installation of New Automation System and ASMGCS at ATS Complex and Sky Tower, Mumbai -Phase-I and II Tender ID: 2023_AAI_156153_1
Tender Inviting Authority: Asstt.Gen.Manager (Engg.-Elect.),ATS Complex, Mumbai.
Name of Work: "Precision Air-conditioning works for the installation of New Automation System and ASMGCS at ATS Complex and Sky Tower, Mumbai - Phase-I & II”
Contract No: MUM/ATS/ENGG-E/eNIT-01/2023-24
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Network Techlab India Pvt Ltd(GSTN-NA)
[5 empty] | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SH-A :Supply of PAC Units
2.00 | Supply of following capacity Floor Mounted, Bottom discharge and top return Air Cooled type Precision Air Condtioners . The Indoor units shall comprise of stepless variable capacity Digital/Inverter scroll compressor, Min. Two Sided Double skin side panels, with Class "O" Glasswool insulation, Bottom discharge type complete with dynamically balanced composite material fan driven by Electronically Commutated (EC) motor, hydrophilic coated slant/flat cooling coil. The unit shall be equipped with high efficiency filters(G4), micro processor based programmable logic controller, Liquid receiver, Expansion Valve, Driers, suction and discharge piping, Internal power & control wiring, Water leak detector sensor, SS drain tray with nitrile rubber insulation, Stainless steel strip Heater, Infrared steam humidifier, Power and Control contactors and Other Electrical accessories. Provision to communicate with the BMS monitoring system through RS 485 communications protocol. The Outdoor Condenser units shall comprise of Condenser fans & motor, Condenser cooling coil (Copper coil with aluminium fins), Fan speed controller, Isolater switch The outdoor unit shall be selected at min. 38 Deg C of ambient temperatures with R-410A Refrigerant Gas. The units shall be suitable for operation on 415 Volts, 50 Hz, 3 Phase, 4 Wire AC supply. Each unit should be having individual display panel, which shall display date, time, actual & set values, operating conditions, signal faults, collective faults, limiting values and unit wellness alarm / service alarm to reduce the down time and unit memory shall hold the 400 most recent events with ID number, time and date stamp for each event. Operational & Control Features - Supply Air Set points & Operational Capabilities: 20 Deg.C +/- 2 Deg.C, 40% to 70% RH - Return Air Set points & Operational Capabilities: 22 Deg.C to 38 Deg C, 20% to 60% RH - P / PI / PID - All three Control logics for temperature control - Relative / Compensated / Predictive method for humidity control - Temperature & Humidity graphs for the system (Avg. value of all the connected units) & for each single unit - Record of Peak & Low temperature/humidity of the current day - Display shows SET / ACTUAL / SET+ACTUAL Values - Records total run hours for all main components - Team Mode operation for synchronising all machines in room without any external controller - Sequencing & Stand-by rotation - Cascading, Lead-Lag functions - Min. 16 days record of controlled parameters - Unit memory shall hold min. 200 recent alarms with date and time for each alarm - Status report of last 400 event logs - 3 types of access; User, Service & Advanced to protect all settings - Auto restart after a power failure - Graphical display of status of operation of all major components like Compressor, Fan, Heater & Humidifier on screen in an idle mode
3.00 | Operational & Control Features - Supply Air Set points & Operational Capabilities: 20 Deg.C +/- 2 Deg.C, 40% to 70% RH - Return Air Set points & Operational Capabilities: 22 Deg.C to 38 Deg C, 20% to 60% RH - P / PI / PID - All three Control logics for temperature control - Relative / Compensated / Predictive method for humidity control - Temperature & Humidity graphs for the system (Avg. value of all the connected units) & for each single unit - Record of Peak & Low temperature/humidity of the current day - Display shows SET / ACTUAL / SET+ACTUAL Values - Records total run hours for all main components - Team Mode operation for synchronising all machines in room without any external controller - Sequencing & Stand-by rotation - Cascading, Lead-Lag functions - Min. 16 days record of controlled parameters - Unit memory shall hold min. 200 recent alarms with date and time for each alarm - Status report of last 400 event logs - 3 types of access; User, Service & Advanced to protect all settings - Auto restart after a power failure - Graphical display of status of operation of all major components like Compressor, Fan, Heater & Humidifier on screen in an idle mode
4.00 | 15.0 TR Total cooling capacity with minimum airflow of 16000 CMH, at minimum 20 Pa ESP, Return Air as temperature at 28 +/-2 Deg C DB & 45% +/-5 RH (Non Condensing). (For Location ATS Complex First Floor- DPDS Server Room(1W+1S), Second Floor- ACC Room(2W+2S), Third Floor- APP SIM Room(2W+2S)) | 10.00 | Each |  | 1432495.00 | 14324950.00 | 14324950.00 | Network Techlab India Pvt Ltd
5.00 | 12.5 TR Total cooling capacity with minimum airflow of 11500 CMH, at minimum 20 Pa ESP, Return Air to be considerd as temperature at 28 +/-2 Deg C DB & 45% +/-5 RH (Non Condensing). (For Location ATS Complex Third Floor- OCC Room(1W+1S)) | 2.00 | Each |  | 970064.00 | 1940128.00 | 1940128.00 | Network Techlab India Pvt Ltd
6.00 | 9.5 TR Total cooling capacity with minimum airflow of 8000 CMH, at minimum 20 Pa ESP, Return Air to be considerd as temperature at 28 +/-2 Deg C DB & 45% +/-5 RH (Non Condensing). (For Location ATC Complex Second Floor- HFRT Room(1W+1S), SKY Tower Third Floor- ITWP Server Room(1W+1S)) | 4.00 | Each |  | 858307.00 | 3433228.00 | 3433228.00 | Network Techlab India Pvt Ltd
7.00 | 5.5 TR Total cooling capacity with minimum airflow of 5750 CMH, at minimum 20 Pa ESP, Return Air to be considerd as temperature at 28 +/-2 Deg C DB & 45% +/-5 RH (Non Condensing). (For Location SKY Tower Fourth Floor- ASMGCS Server Room(1W+1S)) | 2.00 | Each |  | 777700.00 | 1555400.00 | 1555400.00 | Network Techlab India Pvt Ltd
8.00 | Supply, of following capacity Wall Mounted, Front discharge Air Cooled type Precision Air Condtioners -3.0 TR Nominal Cooling capacity @ minimum 2800 CMH. The Indoor unit shall comprise of variable Scroll Compressor, fan section complete with EC fan, Evaporator, Copper Cooling coil, Microprocessor controllers, Thermal Expansion valves, G4 Filter, Internal power and control wiring, HP/LP Cutouts, Power & Control Contactors and other electrical accessories. The Outdoor Condenser unit shall comprise of Condenser fan & motor, Condenser cooling coil (Copper coil with Aluminium fins), Isolator Switch. The protection level of the outdoor unit will be IP54. Items included the following :- Indoor unit with Metalic Body with Anti Corrosive Coating, Feature for PAC units controller for synchronising the multiple no. of units to work as single system for above units, Load sharing mode feature, Cascading Effect, Sequencing of above units.
9.00 | Wall mounted high sensible cooling unit - 3TR Supply Air Set points & Operational Capabilities:- 20 Deg.C +/- 2 Deg.C, 40% to 70% RH (For Location - First Floor ATS - UPS Room 1 (2W+2S), UPS Room 2 (2W+2S), First Floor ATS Battery Bank Room 1 (1W+1S), Battery Bank 2 (1W+1S) | 12.00 | Each |  | 369434.00 | 4433208.00 | 4433208.00 | Network Techlab India Pvt Ltd
10.00 | SH-B : Installation, Testing & Commissioning of PAC System
11.00 | Installation, testing, and commissioning of following capacity Floor Mounted, Bottom discharge and top return type Air Cooled type Precision Air Condtioners including supply & fixing suitable adjutable GI/MS stands with rubber pad for each outdoor unit to dimension as specified / recommendation of OEM (for Indoor and Outdoor units) including wiring, connection & interconnection making suitable for operation complete as required.
12.00 | 15.0 TR Total cooling capacity with minimum airflow of 16000 CMH, at minimum 20 Pa ESP, Return Air as temperature at 28 +/-2 Deg C DB & 45% +/-5 RH (Non Condensing). (For Location ATS Complex First Floor- DPDS Server Room(1W+1S), Second Floor- ACC Room(2W+2S), Third Floor- APP SIM Room(2W+2S)) | 10.00 | Each |  | 49700.00 | 497000.00 | 497000.00 | Network Techlab India Pvt Ltd
13.00 | 12.5 TR Total cooling capacity with minimum airflow of 11500 CMH, at minimum 20 Pa ESP, Return Air to be considerd as temperature at 28 +/-2 Deg C DB & 45% +/-5 RH (Non Condensing). (For Location ATS Complex Third Floor- OCC Room(1W+1S)) | 2.00 | Each |  | 51925.00 | 103850.00 | 103850.00 | Network Techlab India Pvt Ltd
14.00 | 9.5 TR Total cooling capacity with minimum airflow of 8000 CMH, at minimum 20 Pa ESP, Return Air to be considerd as temperature at 28 +/-2 Deg C DB & 45% +/-5 RH (Non Condensing). (For Location ATC Complex Second Floor- HFRT Room(1W+1S), SKY Tower Third Floor- ITWP Server Room(1W+1S)) | 4.00 | Each |  | 37700.00 | 150800.00 | 150800.00 | Network Techlab India Pvt Ltd
15.00 | 5.5 TR Total cooling capacity with minimum airflow of 5750 CMH, at minimum 20 Pa ESP, Return Air to be considerd as temperature at 28 +/-2 Deg C DB & 45% +/-5 RH (Non Condensing). (For Location SKY Tower Fourth Floor- ASMGCS Server Room(1W+1S)) | 2.00 | Each |  | 41180.00 | 82360.00 | 82360.00 | Network Techlab India Pvt Ltd
16.00 | Supply, installation, testing of 18 SWG hard drawn copper refrigerant piping of sizes as per OEM standard with insulation for precision units with proper "U" traps in piping for required length. All refrigerant piping along within conditioned space shall be provided with 9mm Class '0' Nitril Rubber insulation while rest pipework shall be provided with Nitrile Rubber Insulation & Anticorrosive coating and supports, between indoor and outdoor units. Each running meter of one circuit includes one meter of copper pipe (inlet & outlet), necessary supports, fittings, insulation, Thermogaurd coating etc. and should connect the indoor to the outdoor as per locations. (Including extension kit if required) | 1620.00 | Meter |  | 3003.00 | 4864860.00 | 4864860.00 | Network Techlab India Pvt Ltd
17.00 | Supply and fixing Perforated GI trays (With maximum 50% perforation) with necessary support and covertop for Refrigerant Pipes of of following Size in (mm)
18.00 | Width 300 x Height 75 x thickness 1.2 | 200.00 | Meter |  | 1557.30 | 311460.00 | 311460.00 | Network Techlab India Pvt Ltd
19.00 | Width 150 x Height 50 x thickness 1.2 | 160.00 | Meter |  | 132.00 | 21120.00 | 21120.00 | Network Techlab India Pvt Ltd
20.00 | Supply & Installation of following size GI Class "B" Drain Pipe with 9 mm thickness Nitrile rubber insulation with including all accessories complete as required.
21.00 | 50mm diameter | 100.00 | Meter |  | 1462.50 | 146250.00 | 146250.00 | Network Techlab India Pvt Ltd
22.00 | 32mm diameter | 60.00 | Meter |  | 1292.00 | 77520.00 | 77520.00 | Network Techlab India Pvt Ltd
23.00 | 25mm diameter | 20.00 | Meter |  | 912.00 | 18240.00 | 18240.00 | Network Techlab India Pvt Ltd
24.00 | Supply & Installation of 25mm dia GI B class pipe for humidifier connection with including all accessories complete as required. | 200.00 | Meter |  | 912.00 | 182400.00 | 182400.00 | Network Techlab India Pvt Ltd
25.00 | Charging of Refrigerant Gas R-410a with Oil
26.00 | Supply & charging of Refrigerant Gas (R-410A) for the compressor for the 100 % rating and equivalent copper pipe length between Indoor & Outdoor Unit along with required oil for commisioning. | 720.00 | Kg |  | 1292.00 | 930240.00 | 930240.00 | Network Techlab India Pvt Ltd
27.00 | Supply & Installation of Motorized Damper with Actuator (of sufficient torque) & necessary control cablings for ON/OFF operation by interfacing with indoor unit operation and to be installed on indoor machines on Return Air path. | 18.00 | Each |  | 29450.00 | 530100.00 | 530100.00 | Network Techlab India Pvt Ltd
28.00 | Supply and laying of 3 C x 2.5 Sqmm Cu. Flexible cable (Indoor to outdoor unit) on existing cable tray or surface as directed by EIC. | 1000.00 | Meter |  | 262.20 | 262200.00 | 262200.00 | Network Techlab India Pvt Ltd
29.00 | Supply and laying of Size 4C x 16Sqmm. armoured Copper cable from Incoming Isolator Panel to Indoor Unit on existing cable tray or surface as directed by EIC. | 200.00 | Meter |  | 1168.50 | 233700.00 | 233700.00 | Network Techlab India Pvt Ltd
30.00 | Sequencing & logic control necessary timers and logic control for automatic start-stop of the unit.with necessary timers and logic control for automatic start-stop of the unit.Logic should include orderly restart after power failure. | 18.00 | Lot |  | 9500.00 | 171000.00 | 171000.00 | Network Techlab India Pvt Ltd
31.00 | WALL MOUNTED UNITS
32.00 | Installation , testing, and commissioning of following capacity Wall Mounted, Front discharge type Air Cooled type Precision Air Condtioners -3.0 TR Nominal Cooling capacity @ minimum 2800 CMH including supply & fixing suitable GI/MS stands for outdoor units and required plate for indoor unit including wiring, connection & interconnection making suitable for operation complete as required.
33.00 | Wall mounted high sensible cooling unit - 3TR (For Location - First Floor ATS - UPS Room 1 (2W+2S), UPS Room 2 (2W+2S), First Floor ATS Battery Bank Room 1 (1W+1S), Battery Bank Room 2 (1W+1S) | 12.00 | Each |  | 29452.00 | 353424.00 | 353424.00 | Network Techlab India Pvt Ltd
34.00 | Supply & fixing of suitable size (as per OEM recommendation) Copper piping for Interconnecting between indoor & outdoor unit with suitable with Nitrile Rubber insullation. HOT gas line with insulation | 200.00 | Meter |  | 1721.85 | 344370.00 | 344370.00 | Network Techlab India Pvt Ltd
35.00 | Supply & fixing of suitable size (as per OEM recommendation) Copper piping for Interconnecting between indoor & outdoor unit with suitable Nitrile Rubber insullation. Liquid gas line Insulation | 200.00 | Meter |  | 1349.50 | 269900.00 | 269900.00 | Network Techlab India Pvt Ltd
36.00 | Supply and laying of following size copper conductor cable for Interconnection between indoor & outdoor unit in existing cable tray or surface complete as required. 5C X 2.5Sq.mm | 220.00 | Meter |  | 335.40 | 73788.00 | 73788.00 | Network Techlab India Pvt Ltd
37.00 | Supply and laying following size copper conductor control cable for Interconnecting between indoor & outdoor unit in existing cable tray or surface complete as required. 1.5 sqmm x 4C Copper cable | 220.00 | Meter |  | 253.50 | 55770.00 | 55770.00 | Network Techlab India Pvt Ltd
38.00 | Supplying and fixing Condensate drain piping 25 mm UPVC with 9mm nitrile rubber Insulation | 80.00 | Meter |  | 643.50 | 51480.00 | 51480.00 | Network Techlab India Pvt Ltd
39.00 | Supply and fixing Perforated GI trays with necessary support and covertop for Refrigerant Pipes of of following Size in (mm) Width 100x Height 50x thickness 1.2 in mm | 80.00 | Meter |  | 1503.00 | 120240.00 | 120240.00 | Network Techlab India Pvt Ltd
40.00 | Supply & charging of Refrigerant Gas (R407C) and oil required for the compressor for the 100 % rating and equivalent copper pipe length between Indoor & Outdoor Unit. | 96.00 | Kg |  | 1326.00 | 127296.00 | 127296.00 | Network Techlab India Pvt Ltd
41.00 | SH-C: Supply and Fixing of G.I. duct i/c insulation and New Diffusers/ Grills.
42.00 | Supply, installation, balancing and commissioning of fabricated at site GSS sheet metal rectangular/round ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required.
43.00 | Thickness 0.63 mm sheet (24 Gauge) | 80.00 | Sq.Mtr. |  | 1368.00 | 109440.00 | 109440.00 | Network Techlab India Pvt Ltd
44.00 | Thickness 0.8 mm sheet (22 Gauge) | 40.00 | Sq.Mtr. |  | 1509.30 | 60372.00 | 60372.00 | Network Techlab India Pvt Ltd
45.00 | Supplying & fixing of powder coated extruded aluminium Air Grills with louvers but without volume control dampers complete as required. | 50.00 | Sq.Mtr. |  | 7686.00 | 384300.00 | 384300.00 | Network Techlab India Pvt Ltd
46.00 | Supplying and fixing of following thickness duly laminated aluminum foil of mat finish closed cell Nitrile rubber (Class “O”) insulation on existing duct after applying suitable adhesive for Nitrile rubber. The joints shall be sealed with 50 mm wide and 3 mm thick self adhesive nitrile rubber tape insulation complete as per specifications and as required.
47.00 | Thickness- 19 mm | 120.00 | Sq.Mtr. |  | 1145.00 | 137400.00 | 137400.00 | Network Techlab India Pvt Ltd
48.00 | SH-D : Annual Comprehensive Maintenance Contract of PAC
49.00 | Annual Comprehensive Maintenance Contract of above Floor mounted PAC i.e 18 Nos. and wall monted SRC i.e. 12 Nos. or Total Nos. of installed units under above work after completion of defect liability period of one year. The scope of work during CMC Period shall be as per technical specifications. For First Year | 12.00 | Months |  | 208053.31 | 2496639.72 | 2496639.72 | Network Techlab India Pvt Ltd
50.00 | Annual Comprehensive Maintenance Contract of above Floor mounted PAC i.e 18 Nos. and wall monted SRC i.e. 12 Nos. or Total Nos. of installed units under above work after completion of defect liability period of one year. The scope of work during CMC Period shall be as per technical specifications. For Second Year | 12.00 | Months |  | 218455.98 | 2621471.76 | 2621471.76 | Network Techlab India Pvt Ltd
51.00 | Annual Comprehensive Maintenance Contract of above Floor mounted PAC i.e 18 Nos. and wall monted SRC i.e. 12 Nos. or Total Nos. of installed units under above work after completion of defect liability period of one year. The scope of work during CMC Period shall be as per technical specifications. For Third Year | 12.00 | Months |  | 229378.78 | 2752545.36 | 2752545.36 | Network Techlab India Pvt Ltd
52.00 | Annual Comprehensive Maintenance Contract of above Floor mounted PAC i.e 18 Nos. and wall monted SRC i.e. 12 Nos. or Total Nos. of installed units under above work after completion of defect liability period of one year. The scope of work during CMC Period shall be as per technical specifications. For Fourth Year | 12.00 | Months |  | 240847.72 | 2890172.64 | 2890172.64 | Network Techlab India Pvt Ltd
53.00 | Annual Comprehensive Maintenance Contract of above Floor mounted PAC i.e 18 Nos. and wall monted SRC i.e. 12 Nos. or Total Nos. of installed units under above work after completion of defect liability period of one year. The scope of work during CMC Period shall be as per technical specifications. For FifthYear | 12.00 | Months |  | 252890.11 | 3034681.32 | 3034681.32 | Network Techlab India Pvt Ltd
| Total in Figures |  |  |  |  | 50153304.80
Lowest Amount Quoted BY: Network Techlab India Pvt Ltd(50153304.80)

## BOQ Summary
BOQ Summary Details Tender Title: Precision Air-conditioning works for the installation of New Automation System and ASMGCS at ATS Complex and Sky Tower, Mumbai -Phase-I and II Tender ID: 2023_AAI_156153_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Network Techlab India Pvt Ltd | 50153304.80 | L1